## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1706-9_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1706-9_0_5_node_102 | 0.4 | n |  | TRUE
2 | bus_LV_1706-9_0_5_node_103 | 0.4 | n |  | TRUE
3 | bus_LV_1706-9_0_5_node_1 | 0.4 | n |  | TRUE
4 | bus_LV_1706-9_0_5_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_1706-9_0_5_node_3 | 0.4 | n |  | TRUE
6 | bus_LV_1706-9_0_5_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1706-9_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1706-9_0_5_node_134 | 0.4 | n |  | TRUE
9 | bus_LV_1706-9_0_5_node_135 | 0.4 | n |  | TRUE
10 | bus_LV_1706-9_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1706-9_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1706-9_0_5_node_130 | 0.4 | n |  | TRUE
13 | bus_LV_1706-9_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1706-9_0_5_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_1706-9_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1706-9_0_5_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_1706-9_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_1706-9_0_5_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1706-9_0_5_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1706-9_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_1706-9_0_5_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1706-9_0_5_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1706-9_0_5_node_117 | 0.4 | n |  | TRUE
24 | bus_LV_1706-9_0_5_node_72 | 0.4 | n |  | TRUE
25 | bus_LV_1706-9_0_5_node_97 | 0.4 | n |  | TRUE
26 | bus_LV_1706-9_0_5_node_73 | 0.4 | n |  | TRUE
27 | bus_LV_1706-9_0_5_node_59 | 0.4 | n |  | TRUE
28 | bus_LV_1706-9_0_5_node_65 | 0.4 | n |  | TRUE
29 | bus_LV_1706-9_0_5_node_57 | 0.4 | n |  | TRUE
30 | bus_LV_1706-9_0_5_node_19 | 0.4 | n |  | TRUE
31 | bus_LV_1706-9_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1706-9_0_5_node_104 | 0.4 | n |  | TRUE
33 | bus_LV_1706-9_0_5_node_88 | 0.4 | n |  | TRUE
34 | bus_LV_1706-9_0_5_node_115 | 0.4 | n |  | TRUE
35 | bus_LV_1706-9_0_5_node_21 | 0.4 | n |  | TRUE
36 | bus_LV_1706-9_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_1706-9_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_1706-9_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_1706-9_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_1706-9_0_5_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1706-9_0_5_node_54 | 0.4 | n |  | TRUE
42 | bus_LV_1706-9_0_5_node_51 | 0.4 | n |  | TRUE
43 | bus_LV_1706-9_0_5_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_1706-9_0_5_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_1706-9_0_5_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_1706-9_0_5_node_52 | 0.4 | n |  | TRUE
47 | bus_LV_1706-9_0_5_node_26 | 0.4 | n |  | TRUE
48 | bus_LV_1706-9_0_5_node_27 | 0.4 | n |  | TRUE
49 | bus_LV_1706-9_0_5_node_28 | 0.4 | n |  | TRUE
50 | bus_LV_1706-9_0_5_node_29 | 0.4 | n |  | TRUE
51 | bus_LV_1706-9_0_5_node_30 | 0.4 | n |  | TRUE
52 | bus_LV_1706-9_0_5_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_1706-9_0_5_node_66 | 0.4 | n |  | TRUE
54 | bus_LV_1706-9_0_5_node_34 | 0.4 | n |  | TRUE
55 | bus_LV_1706-9_0_5_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_1706-9_0_5_node_36 | 0.4 | n |  | TRUE
57 | bus_LV_1706-9_0_5_node_131 | 0.4 | n |  | TRUE
58 | bus_LV_1706-9_0_5_node_132 | 0.4 | n |  | TRUE
59 | bus_LV_1706-9_0_5_node_129 | 0.4 | n |  | TRUE
60 | bus_LV_1706-9_0_5_node_137 | 0.4 | n |  | TRUE
61 | bus_LV_1706-9_0_5_node_31 | 0.4 | n |  | TRUE
62 | bus_LV_1706-9_0_5_node_32 | 0.4 | n |  | TRUE
63 | bus_LV_1706-9_0_5_node_33 | 0.4 | n |  | TRUE
64 | bus_LV_1706-9_0_5_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_1706-9_0_5_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_1706-9_0_5_node_64 | 0.4 | n |  | TRUE
67 | bus_LV_1706-9_0_5_node_62 | 0.4 | n |  | TRUE
68 | bus_LV_1706-9_0_5_node_43 | 0.4 | n |  | TRUE
69 | bus_LV_1706-9_0_5_node_38 | 0.4 | n |  | TRUE
70 | bus_LV_1706-9_0_5_node_39 | 0.4 | n |  | TRUE
71 | bus_LV_1706-9_0_5_node_40 | 0.4 | n |  | TRUE
72 | bus_LV_1706-9_0_5_node_46 | 0.4 | n |  | TRUE
73 | bus_LV_1706-9_0_5_node_53 | 0.4 | n |  | TRUE
74 | bus_LV_1706-9_0_5_node_44 | 0.4 | n |  | TRUE
75 | bus_LV_1706-9_0_5_node_60 | 0.4 | n |  | TRUE
76 | bus_LV_1706-9_0_5_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_1706-9_0_5_node_45 | 0.4 | n |  | TRUE
78 | bus_LV_1706-9_0_5_node_138 | 0.4 | n |  | TRUE
79 | bus_LV_1706-9_0_5_node_133 | 0.4 | n |  | TRUE
80 | bus_LV_1706-9_0_5_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_1706-9_0_5_node_58 | 0.4 | n |  | TRUE
82 | bus_LV_1706-9_0_5_node_128 | 0.4 | n |  | TRUE
83 | bus_LV_1706-9_0_5_node_127 | 0.4 | n |  | TRUE
84 | bus_LV_1706-9_0_5_node_67 | 0.4 | n |  | TRUE
85 | bus_LV_1706-9_0_5_node_68 | 0.4 | n |  | TRUE
86 | bus_LV_1706-9_0_5_node_69 | 0.4 | n |  | TRUE
87 | bus_LV_1706-9_0_5_node_70 | 0.4 | n |  | TRUE
88 | bus_LV_1706-9_0_5_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_1706-9_0_5_node_89 | 0.4 | n |  | TRUE
90 | bus_LV_1706-9_0_5_node_105 | 0.4 | n |  | TRUE
91 | bus_LV_1706-9_0_5_node_90 | 0.4 | n |  | TRUE
92 | bus_LV_1706-9_0_5_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_1706-9_0_5_node_74 | 0.4 | n |  | TRUE
94 | bus_LV_1706-9_0_5_node_75 | 0.4 | n |  | TRUE
95 | bus_LV_1706-9_0_5_node_76 | 0.4 | n |  | TRUE
96 | bus_LV_1706-9_0_5_node_77 | 0.4 | n |  | TRUE
97 | bus_LV_1706-9_0_5_node_78 | 0.4 | n |  | TRUE
98 | bus_LV_1706-9_0_5_node_94 | 0.4 | n |  | TRUE
99 | bus_LV_1706-9_0_5_node_100 | 0.4 | n |  | TRUE
100 | bus_LV_1706-9_0_5_node_136 | 0.4 | n |  | TRUE
101 | bus_LV_1706-9_0_5_node_96 | 0.4 | n |  | TRUE
102 | bus_LV_1706-9_0_5_node_93 | 0.4 | n |  | TRUE
103 | bus_LV_1706-9_0_5_node_98 | 0.4 | n |  | TRUE
104 | bus_LV_1706-9_0_5_node_79 | 0.4 | n |  | TRUE
105 | bus_LV_1706-9_0_5_node_80 | 0.4 | n |  | TRUE
106 | bus_LV_1706-9_0_5_node_81 | 0.4 | n |  | TRUE
107 | bus_LV_1706-9_0_5_node_82 | 0.4 | n |  | TRUE
108 | bus_LV_1706-9_0_5_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_1706-9_0_5_node_106 | 0.4 | n |  | TRUE
110 | bus_LV_1706-9_0_5_node_107 | 0.4 | n |  | TRUE
111 | bus_LV_1706-9_0_5_node_125 | 0.4 | n |  | TRUE
112 | bus_LV_1706-9_0_5_node_84 | 0.4 | n |  | TRUE
113 | bus_LV_1706-9_0_5_node_85 | 0.4 | n |  | TRUE
114 | bus_LV_1706-9_0_5_node_86 | 0.4 | n |  | TRUE
115 | bus_LV_1706-9_0_5_node_87 | 0.4 | n |  | TRUE
116 | bus_LV_1706-9_0_5_node_91 | 0.4 | n |  | TRUE
117 | bus_LV_1706-9_0_5_node_92 | 0.4 | n |  | TRUE
118 | bus_LV_1706-9_0_5_node_99 | 0.4 | n |  | TRUE
119 | bus_LV_1706-9_0_5_node_95 | 0.4 | n |  | TRUE
120 | bus_LV_1706-9_0_5_node_116 | 0.4 | n |  | TRUE
121 | bus_LV_1706-9_0_5_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_1706-9_0_5_node_126 | 0.4 | n |  | TRUE
123 | bus_LV_1706-9_0_5_node_111 | 0.4 | n |  | TRUE
124 | bus_LV_1706-9_0_5_node_108 | 0.4 | n |  | TRUE
125 | bus_LV_1706-9_0_5_node_109 | 0.4 | n |  | TRUE
126 | bus_LV_1706-9_0_5_node_110 | 0.4 | n |  | TRUE
127 | bus_LV_1706-9_0_5_node_112 | 0.4 | n |  | TRUE
128 | bus_LV_1706-9_0_5_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_1706-9_0_5_node_118 | 0.4 | n |  | TRUE
130 | bus_LV_1706-9_0_5_node_119 | 0.4 | n |  | TRUE
131 | bus_LV_1706-9_0_5_node_120 | 0.4 | n |  | TRUE
132 | bus_LV_1706-9_0_5_node_124 | 0.4 | n |  | TRUE
133 | bus_LV_1706-9_0_5_node_123 | 0.4 | n |  | TRUE
134 | bus_LV_1706-9_0_5_node_121 | 0.4 | n |  | TRUE
135 | bus_LV_1706-9_0_5_node_122 | 0.4 | n |  | TRUE
136 | bus_MV_22_0_node_147 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1706-9_0_5_load_0 | 0 | 0.0022452 | 0.00056269 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1706-9_0_5_load_102 | 1 | 0.0015462 | 0.00038752 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1706-9_0_5_load_103 | 2 | 0.0014847 | 0.0003721 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1706-9_0_5_load_1 | 3 | 0.00026289 | 6.5886e-05 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1706-9_0_5_load_2 | 4 | 0.00046292 | 0.00011602 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1706-9_0_5_load_4 | 6 | 0.00068502 | 0.00017168 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1706-9_0_5_load_134 | 8 | 0.0015412 | 0.00038627 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1706-9_0_5_load_135 | 9 | 0.0018962 | 0.00047522 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1706-9_0_5_load_5 | 10 | 0.0010932 | 0.00027397 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1706-9_0_5_load_7 | 11 | 0.0022796 | 0.00057133 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1706-9_0_5_load_130 | 12 | 0.00035252 | 8.8349e-05 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1706-9_0_5_load_9 | 13 | 0.0020657 | 0.00051771 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1706-9_0_5_load_10 | 14 | 0.0012185 | 0.0003054 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1706-9_0_5_load_12 | 16 | 0.00036013 | 9.0257e-05 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1706-9_0_5_load_13 | 17 | 0.0039519 | 0.00099043 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1706-9_0_5_load_18 | 18 | 0.00030728 | 7.7012e-05 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1706-9_0_5_load_14 | 19 | 0.00016183 | 4.0558e-05 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1706-9_0_5_load_17 | 20 | 0.00013756 | 3.4475e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1706-9_0_5_load_15 | 21 | 0.00029832 | 7.4766e-05 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1706-9_0_5_load_16 | 22 | 0.00020169 | 5.0548e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1706-9_0_5_load_117 | 23 | 0.0001965 | 4.9248e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1706-9_0_5_load_72 | 24 | 0.00030627 | 7.6759e-05 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1706-9_0_5_load_97 | 25 | 0.0010814 | 0.00027102 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1706-9_0_5_load_73 | 26 | 0.0001698 | 4.2555e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1706-9_0_5_load_59 | 27 | 0.0007113 | 0.00017827 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1706-9_0_5_load_65 | 28 | 0.00094415 | 0.00023663 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1706-9_0_5_load_57 | 29 | 0.00033358 | 8.3602e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1706-9_0_5_load_19 | 30 | 0.00077725 | 0.0001948 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1706-9_0_5_load_88 | 33 | 0.00082626 | 0.00020708 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1706-9_0_5_load_21 | 35 | 0.005019 | 0.0012579 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1706-9_0_5_load_22 | 36 | 0.00087686 | 0.00021976 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1706-9_0_5_load_23 | 37 | 0.0014374 | 0.00036026 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1706-9_0_5_load_24 | 38 | 0.0010013 | 0.00025095 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1706-9_0_5_load_54 | 41 | 0.0010506 | 0.0002633 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1706-9_0_5_load_51 | 42 | 0.00077986 | 0.00019545 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1706-9_0_5_load_42 | 44 | 0.000553 | 0.0001386 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1706-9_0_5_load_55 | 45 | 0.00065426 | 0.00016397 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1706-9_0_5_load_52 | 46 | 0.00092204 | 0.00023109 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1706-9_0_5_load_26 | 47 | 0.00028349 | 7.1049e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1706-9_0_5_load_29 | 50 | 0.00097296 | 0.00024385 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1706-9_0_5_load_30 | 51 | 0.0014999 | 0.00037591 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1706-9_0_5_load_66 | 53 | 0.00039615 | 9.9285e-05 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1706-9_0_5_load_34 | 54 | 0.00070581 | 0.00017689 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1706-9_0_5_load_35 | 55 | 0.00012084 | 3.0285e-05 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1706-9_0_5_load_36 | 56 | 0.00030294 | 7.5923e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1706-9_0_5_load_131 | 57 | 0.00034465 | 8.6377e-05 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1706-9_0_5_load_132 | 58 | 0.00031081 | 7.7897e-05 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1706-9_0_5_load_137 | 60 | 0.00080798 | 0.0002025 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1706-9_0_5_load_31 | 61 | 0.00050125 | 0.00012563 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1706-9_0_5_load_33 | 63 | 0.00041238 | 0.00010335 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1706-9_0_5_load_64 | 66 | 0.00044649 | 0.0001119 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1706-9_0_5_load_62 | 67 | 0.00026569 | 6.6589e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1706-9_0_5_load_43 | 68 | 0.00048141 | 0.00012065 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1706-9_0_5_load_38 | 69 | 0.00086397 | 0.00021653 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1706-9_0_5_load_53 | 73 | 0.0015076 | 0.00037784 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1706-9_0_5_load_44 | 74 | 0.00042455 | 0.0001064 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1706-9_0_5_load_60 | 75 | 0.0030636 | 0.00076782 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1706-9_0_5_load_63 | 76 | 0.00045133 | 0.00011311 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1706-9_0_5_load_45 | 77 | 0.00034049 | 8.5336e-05 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1706-9_0_5_load_138 | 78 | 0.0002834 | 7.1026e-05 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1706-9_0_5_load_133 | 79 | 0.0017501 | 0.00043861 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1706-9_0_5_load_56 | 80 | 0.00039178 | 9.819e-05 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1706-9_0_5_load_58 | 81 | 0.00034816 | 8.7258e-05 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1706-9_0_5_load_127 | 83 | 0.00035208 | 8.8239e-05 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1706-9_0_5_load_67 | 84 | 0.00097804 | 0.00024512 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1706-9_0_5_load_68 | 85 | 0.0018211 | 0.00045641 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1706-9_0_5_load_69 | 86 | 0.00085427 | 0.0002141 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1706-9_0_5_load_70 | 87 | 0.0010229 | 0.00025636 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1706-9_0_5_load_71 | 88 | 0.0012743 | 0.00031938 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1706-9_0_5_load_89 | 89 | 0.0013942 | 0.00034941 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1706-9_0_5_load_105 | 90 | 0.0020587 | 0.00051595 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1706-9_0_5_load_90 | 91 | 0.0012642 | 0.00031684 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1706-9_0_5_load_74 | 93 | 0.0020337 | 0.00050969 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1706-9_0_5_load_75 | 94 | 0.001323 | 0.00033158 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1706-9_0_5_load_76 | 95 | 0.0016585 | 0.00041565 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1706-9_0_5_load_78 | 97 | 0.0015684 | 0.00039307 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1706-9_0_5_load_100 | 99 | 0.0015206 | 0.00038109 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1706-9_0_5_load_136 | 100 | 0.00086965 | 0.00021795 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1706-9_0_5_load_96 | 101 | 0.0013029 | 0.00032653 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1706-9_0_5_load_93 | 102 | 0.0016152 | 0.00040481 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1706-9_0_5_load_98 | 103 | 0.0012048 | 0.00030196 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1706-9_0_5_load_79 | 104 | 0.00078369 | 0.00019641 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1706-9_0_5_load_80 | 105 | 0.0011798 | 0.00029569 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1706-9_0_5_load_81 | 106 | 0.0031489 | 0.00078918 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1706-9_0_5_load_82 | 107 | 0.001884 | 0.00047216 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1706-9_0_5_load_101 | 108 | 0.0010683 | 0.00026774 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1706-9_0_5_load_106 | 109 | 0.0033787 | 0.00084679 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1706-9_0_5_load_107 | 110 | 0.00066201 | 0.00016592 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1706-9_0_5_load_125 | 111 | 0.0012989 | 0.00032553 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1706-9_0_5_load_84 | 112 | 0.0039742 | 0.00099602 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1706-9_0_5_load_85 | 113 | 0.0022771 | 0.00057071 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1706-9_0_5_load_86 | 114 | 0.0034382 | 0.0008617 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1706-9_0_5_load_87 | 115 | 0.0035235 | 0.00088306 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1706-9_0_5_load_91 | 116 | 0.0029997 | 0.00075179 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1706-9_0_5_load_92 | 117 | 0.0016636 | 0.00041693 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1706-9_0_5_load_99 | 118 | 0.001702 | 0.00042656 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1706-9_0_5_load_95 | 119 | 0.0013023 | 0.0003264 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1706-9_0_5_load_116 | 120 | 0.0016906 | 0.0004237 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1706-9_0_5_load_114 | 121 | 0.0012302 | 0.00030832 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1706-9_0_5_load_126 | 122 | 0.003832 | 0.00096038 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1706-9_0_5_load_111 | 123 | 0.0032146 | 0.00080565 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1706-9_0_5_load_108 | 124 | 0.0016545 | 0.00041466 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1706-9_0_5_load_109 | 125 | 0.0015793 | 0.0003958 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1706-9_0_5_load_112 | 127 | 0.001083 | 0.00027142 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1706-9_0_5_load_113 | 128 | 0.0011604 | 0.00029083 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1706-9_0_5_load_118 | 129 | 0.004024 | 0.0010085 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1706-9_0_5_load_120 | 131 | 0.004305 | 0.0010789 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1706-9_0_5_load_123 | 133 | 0.00081564 | 0.00020442 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1706-9_0_5_load_121 | 134 | 0.0032269 | 0.00080873 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1706-9_0_5_load_122 | 135 | 0.003196 | 0.000801 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 85 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1706-9_0_5_line_0 |  | 0 | 1 | 0.41304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1706-9_0_5_line_1 |  | 1 | 2 | 0.083337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1706-9_0_5_line_2 |  | 2 | 32 | 0.023755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1706-9_0_5_line_3 |  | 3 | 4 | 0.020452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1706-9_0_5_line_4 |  | 3 | 5 | 0.02097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1706-9_0_5_line_5 |  | 4 | 6 | 0.031505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1706-9_0_5_line_6 |  | 5 | 7 | 0.36662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1706-9_0_5_line_7 |  | 6 | 8 | 0.30082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1706-9_0_5_line_8 |  | 7 | 10 | 0.030986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1706-9_0_5_line_9 |  | 8 | 9 | 0.012337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1706-9_0_5_line_10 |  | 9 | 21 | 0.14282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1706-9_0_5_line_11 |  | 10 | 11 | 0.032367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1706-9_0_5_line_12 |  | 11 | 12 | 0.32955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1706-9_0_5_line_13 |  | 13 | 14 | 0.033243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1706-9_0_5_line_14 |  | 13 | 15 | 0.025824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1706-9_0_5_line_15 |  | 14 | 16 | 0.022831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1706-9_0_5_line_16 |  | 15 | 17 | 0.0028592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1706-9_0_5_line_17 |  | 16 | 18 | 0.20929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1706-9_0_5_line_18 |  | 17 | 19 | 0.052093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1706-9_0_5_line_19 |  | 18 | 20 | 0.090519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1706-9_0_5_line_20 |  | 19 | 21 | 0.039097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1706-9_0_5_line_21 |  | 20 | 24 | 0.09128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1706-9_0_5_line_22 |  | 20 | 22 | 0.043277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1706-9_0_5_line_23 |  | 22 | 23 | 0.15575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
24 | LV_1706-9_0_5_line_24 |  | 23 | 25 | 0.13673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1706-9_0_5_line_25 |  | 24 | 26 | 0.030304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1706-9_0_5_line_26 |  | 24 | 27 | 0.12436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1706-9_0_5_line_27 |  | 25 | 103 | 0.04867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1706-9_0_5_line_28 |  | 25 | 118 | 0.018867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1706-9_0_5_line_29 |  | 27 | 28 | 0.034949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1706-9_0_5_line_30 |  | 27 | 29 | 0.09733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1706-9_0_5_line_31 |  | 28 | 33 | 0.092329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1706-9_0_5_line_32 |  | 29 | 80 | 0.018872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_1706-9_0_5_line_33 |  | 30 | 31 | 0.034503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1706-9_0_5_line_34 |  | 31 | 32 | 0.008693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1706-9_0_5_line_35 |  | 31 | 33 | 0.0070996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1706-9_0_5_line_36 |  | 32 | 34 | 0.049376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1706-9_0_5_line_37 |  | 34 | 121 | 0.018447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1706-9_0_5_line_38 |  | 35 | 36 | 0.05052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_1706-9_0_5_line_39 |  | 35 | 37 | 0.0032663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1706-9_0_5_line_40 |  | 36 | 38 | 0.022125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_1706-9_0_5_line_41 |  | 37 | 39 | 0.019785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1706-9_0_5_line_42 |  | 38 | 40 | 0.051463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_1706-9_0_5_line_43 |  | 39 | 41 | 0.014285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1706-9_0_5_line_44 |  | 39 | 42 | 0.066557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1706-9_0_5_line_45 |  | 40 | 43 | 0.005966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1706-9_0_5_line_46 |  | 40 | 44 | 0.085136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1706-9_0_5_line_47 |  | 41 | 45 | 0.018916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1706-9_0_5_line_48 |  | 42 | 46 | 0.094776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1706-9_0_5_line_49 |  | 43 | 66 | 0.029361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1706-9_0_5_line_50 |  | 43 | 67 | 0.040737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1706-9_0_5_line_51 |  | 44 | 68 | 0.0057613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1706-9_0_5_line_52 |  | 45 | 69 | 0.047493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1706-9_0_5_line_53 |  | 46 | 73 | 0.059707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1706-9_0_5_line_54 |  | 46 | 70 | 0.13118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1706-9_0_5_line_55 |  | 47 | 48 | 0.013334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1706-9_0_5_line_56 |  | 47 | 49 | 0.0064013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1706-9_0_5_line_57 |  | 48 | 50 | 0.090808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1706-9_0_5_line_58 |  | 49 | 51 | 0.020408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1706-9_0_5_line_59 |  | 50 | 55 | 0.019022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1706-9_0_5_line_60 |  | 51 | 53 | 0.011908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1706-9_0_5_line_61 |  | 52 | 53 | 0.16992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_1706-9_0_5_line_62 |  | 52 | 54 | 0.01238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_1706-9_0_5_line_63 |  | 53 | 60 | 0.17014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_1706-9_0_5_line_64 |  | 54 | 62 | 0.025079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_1706-9_0_5_line_65 |  | 55 | 56 | 0.013774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1706-9_0_5_line_66 |  | 57 | 58 | 0.0096152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1706-9_0_5_line_67 |  | 57 | 59 | 0.086057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1706-9_0_5_line_68 |  | 58 | 79 | 0.0165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1706-9_0_5_line_69 |  | 59 | 82 | 0.010218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1706-9_0_5_line_70 |  | 60 | 83 | 0.18794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1706-9_0_5_line_71 |  | 61 | 62 | 0.031258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1706-9_0_5_line_72 |  | 62 | 63 | 0.0081843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_1706-9_0_5_line_73 |  | 63 | 64 | 0.02337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1706-9_0_5_line_74 |  | 64 | 65 | 0.11989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1706-9_0_5_line_75 |  | 65 | 72 | 0.050306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1706-9_0_5_line_76 |  | 66 | 75 | 0.0087634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1706-9_0_5_line_77 |  | 67 | 76 | 0.14422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1706-9_0_5_line_78 |  | 70 | 71 | 0.1045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_1706-9_0_5_line_79 |  | 71 | 72 | 0.039815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_1706-9_0_5_line_80 |  | 72 | 74 | 0.062152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1706-9_0_5_line_81 |  | 74 | 77 | 0.035968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1706-9_0_5_line_82 |  | 75 | 81 | 0.01383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1706-9_0_5_line_83 |  | 77 | 78 | 0.17671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1706-9_0_5_line_84 |  | 80 | 81 | 0.036597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1706-9_0_5_line_85 |  | 82 | 83 | 0.1518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1706-9_0_5_line_86 |  | 83 | 135 | 0.34525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1706-9_0_5_line_87 |  | 84 | 85 | 0.0084196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1706-9_0_5_line_88 |  | 84 | 86 | 0.019335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1706-9_0_5_line_89 |  | 85 | 87 | 0.042056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_1706-9_0_5_line_90 |  | 86 | 88 | 0.00067451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1706-9_0_5_line_91 |  | 87 | 89 | 0.001432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1706-9_0_5_line_92 |  | 88 | 90 | 0.037115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1706-9_0_5_line_93 |  | 89 | 91 | 0.02509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1706-9_0_5_line_94 |  | 90 | 92 | 0.016065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1706-9_0_5_line_95 |  | 91 | 116 | 0.023841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
96 | LV_1706-9_0_5_line_96 |  | 92 | 109 | 0.12254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1706-9_0_5_line_97 |  | 92 | 106 | 0.044643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1706-9_0_5_line_98 |  | 93 | 94 | 0.03346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1706-9_0_5_line_99 |  | 93 | 95 | 0.025577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1706-9_0_5_line_100 |  | 94 | 96 | 0.011604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1706-9_0_5_line_101 |  | 95 | 97 | 0.024667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1706-9_0_5_line_102 |  | 96 | 98 | 0.015174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1706-9_0_5_line_103 |  | 96 | 99 | 0.026761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1706-9_0_5_line_104 |  | 97 | 100 | 0.01003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1706-9_0_5_line_105 |  | 98 | 101 | 0.0056721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1706-9_0_5_line_106 |  | 98 | 102 | 0.039555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1706-9_0_5_line_107 |  | 99 | 103 | 0.0201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1706-9_0_5_line_108 |  | 101 | 115 | 0.032072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1706-9_0_5_line_109 |  | 102 | 119 | 0.021231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1706-9_0_5_line_110 |  | 104 | 105 | 0.03456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1706-9_0_5_line_111 |  | 104 | 106 | 0.019632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1706-9_0_5_line_112 |  | 105 | 107 | 0.025837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1706-9_0_5_line_113 |  | 107 | 108 | 0.032854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1706-9_0_5_line_114 |  | 108 | 110 | 0.019437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1706-9_0_5_line_115 |  | 109 | 111 | 0.009497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1706-9_0_5_line_116 |  | 110 | 120 | 0.0058721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1706-9_0_5_line_117 |  | 111 | 122 | 0.032741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1706-9_0_5_line_118 |  | 112 | 113 | 0.015651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1706-9_0_5_line_119 |  | 112 | 114 | 0.017185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1706-9_0_5_line_120 |  | 113 | 115 | 0.018456 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1706-9_0_5_line_121 |  | 116 | 117 | 0.0090784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
122 | LV_1706-9_0_5_line_122 |  | 117 | 118 | 0.02094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_1706-9_0_5_line_123 |  | 120 | 123 | 0.0047186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1706-9_0_5_line_124 |  | 121 | 128 | 0.022162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1706-9_0_5_line_125 |  | 123 | 125 | 0.025222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1706-9_0_5_line_126 |  | 124 | 125 | 0.012137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1706-9_0_5_line_127 |  | 124 | 126 | 0.019699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_1706-9_0_5_line_128 |  | 126 | 127 | 0.030842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_1706-9_0_5_line_129 |  | 129 | 130 | 0.042704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_1706-9_0_5_line_130 |  | 130 | 131 | 0.05461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
131 | LV_1706-9_0_5_line_131 |  | 130 | 132 | 0.50377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_1706-9_0_5_line_132 |  | 131 | 134 | 0.097092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
133 | LV_1706-9_0_5_line_133 |  | 132 | 133 | 0.15187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
134 | LV_1706-9_0_5_line_134 |  | 133 | 135 | 0.0090362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1706-9_0_5_trafo_68 | 0.63 MVA 20/0.4 kV | 136 | 85 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2691278.3927 | 1220054.5387 | 2690941.6991 | 1219815.2932
1 | 2691278.3927 | 1220054.5387 | 2691289.2689 | 1220044.5944 | 2691296.0409 | 1220039.9617 | 2691300.3214 | 1220039.9383 | 2691298.1738 | 1220058.7406 | 2691294.5046 | 1220067.4015 | 2691278.7075 | 1220089.9861 | 2691278.5864 | 1220090.1728
2 | 2691268.1885 | 1220111.3396 | 2691272.0387 | 1220100.2688 | 2691278.5864 | 1220090.1728
3 | 2691539.2543 | 1220731.2044 | 2691539.0341 | 1220728.9439 | 2691532.9521 | 1220713.4175 | 2691532.4058 | 1220712.0146
4 | 2691541.6863 | 1220751.8783 | 2691540.0191 | 1220746.8047 | 2691539.8009 | 1220736.8167 | 2691539.2543 | 1220731.2044
5 | 2691520.9732 | 1220682.6566 | 2691532.4058 | 1220712.0146
6 | 2691541.6863 | 1220751.8783 | 2691721.9809 | 1221071.106
7 | 2691786.3257 | 1220540.9525 | 2691520.9732 | 1220682.6566
8 | 2691721.9809 | 1221071.106 | 2691748.8141 | 1221086.6025
9 | 2691786.3257 | 1220540.9525 | 2691786.3257 | 1220540.9525 | 2691785.6801 | 1220528.6321
10 | 2691762.0239 | 1220390.8404 | 2691784.9748 | 1220452.3816 | 2691789.0641 | 1220466.2097 | 2691790.2829 | 1220478.2146 | 2691789.564 | 1220494.815 | 2691785.6749 | 1220528.5339 | 2691785.6801 | 1220528.6321
11 | 2691773.29 | 1221105.8982 | 2691770.5036 | 1221099.1284 | 2691748.8141 | 1221086.6025
12 | 2691773.29 | 1221105.8982 | 2692052.897 | 1221280.3158
13 | 2691722.2884 | 1220277.7606 | 2691717.1072 | 1220262.6052 | 2691710.9434 | 1220246.5198
14 | 2691730.6422 | 1220302.1965 | 2691722.2884 | 1220277.7606
15 | 2691710.9434 | 1220246.5198 | 2691706.281 | 1220234.3523 | 2691701.3356 | 1220225.8908
16 | 2691730.6422 | 1220302.1965 | 2691731.5497 | 1220304.9078
17 | 2691701.3356 | 1220225.8908 | 2691492.8465 | 1220207.542
18 | 2691748.3626 | 1220354.2083 | 2691745.3253 | 1220346.064 | 2691731.5497 | 1220304.9078
19 | 2691522.3251 | 1220121.9576 | 2691492.8465 | 1220207.542
20 | 2691762.0239 | 1220390.8404 | 2691748.3626 | 1220354.2083
21 | 2691522.3251 | 1220121.9576 | 2691515.8516 | 1220121.8907 | 2691506.9332 | 1220120.5195 | 2691499.4086 | 1220116.3455 | 2691495.2837 | 1220110.2001 | 2691491.4579 | 1220101.3797 | 2691488.089 | 1220082.0924 | 2691488.338 | 1220070.8218 | 2691491.9692 | 1220060.7039 | 2691496.8704 | 1220053.6865
22 | 2691522.3251 | 1220121.9576 | 2691537.9009 | 1220122.1185 | 2691553.8558 | 1220124.3653 | 2691564.6602 | 1220128.5537
23 | 2691703.7487 | 1220058.4583 | 2691564.6602 | 1220128.5537
24 | 2691820.3479 | 1219987.0504 | 2691703.7487 | 1220058.4583
25 | 2691496.8704 | 1220053.6865 | 2691497.4319 | 1220052.8824 | 2691515.6869 | 1220029.9345
26 | 2691377.2041 | 1220019.854 | 2691496.8704 | 1220053.6865
27 | 2691820.3479 | 1219987.0504 | 2691817.549 | 1219988.5631 | 2691813.4199 | 1219991.0679 | 2691810.4387 | 1219993.9462 | 2691809.0822 | 1219996.7717 | 2691808.9388 | 1219999.6715 | 2691809.5224 | 1220002.1822 | 2691810.8819 | 1220004.0822 | 2691813.8182 | 1220005.5952 | 2691818.1484 | 1220006.2846 | 2691835.9757 | 1220007.5987
28 | 2691820.3479 | 1219987.0504 | 2691836.946 | 1219978.0796
29 | 2691353.6932 | 1220045.311 | 2691367.8573 | 1220033.3136 | 2691377.2041 | 1220019.854
30 | 2691405.8546 | 1219927.1035 | 2691380.1498 | 1220015.6122 | 2691377.2041 | 1220019.854
31 | 2691353.6932 | 1220045.311 | 2691313.3058 | 1220079.5202 | 2691281.1092 | 1220102.2308
32 | 2691411.1179 | 1219908.9804 | 2691411.1179 | 1219908.9804 | 2691405.8546 | 1219927.1035
33 | 2691275.3077 | 1220106.323 | 2691272.7763 | 1220117.9923 | 2691268.751 | 1220131.5733 | 2691269.1216 | 1220139.9622
34 | 2691275.3077 | 1220106.323 | 2691268.1885 | 1220111.3396
35 | 2691275.3077 | 1220106.323 | 2691281.1092 | 1220102.2308
36 | 2691268.1885 | 1220111.3396 | 2691262.0588 | 1220115.6598 | 2691250.7762 | 1220124.949 | 2691239.4374 | 1220149.7924
37 | 2691239.4374 | 1220149.7924 | 2691235.3318 | 1220131.808
38 | 2691601.6029 | 1219808.7027 | 2691562.6527 | 1219827.2177 | 2691555.3856 | 1219828.5774
39 | 2691601.6029 | 1219808.7027 | 2691604.5529 | 1219807.3004
40 | 2691555.3856 | 1219828.5774 | 2691533.6375 | 1219832.6466
41 | 2691623.3561 | 1219801.7001 | 2691611.9326 | 1219803.7925 | 2691604.5529 | 1219807.3004
42 | 2691487.6314 | 1219854.0837 | 2691500.577 | 1219844.7873 | 2691520.2595 | 1219835.1496 | 2691533.6375 | 1219832.6466
43 | 2691623.3561 | 1219801.7001 | 2691633.1961 | 1219791.3452
44 | 2691623.3561 | 1219801.7001 | 2691635.9675 | 1219800.8268 | 2691652.756 | 1219802.2193 | 2691670.2688 | 1219800.9323 | 2691679.1326 | 1219792.574 | 2691685.6012 | 1219789.134
45 | 2691487.6314 | 1219854.0837 | 2691482.774 | 1219857.5671
46 | 2691487.6314 | 1219854.0837 | 2691490.3383 | 1219839.9155 | 2691505.5221 | 1219818.3227 | 2691529.0018 | 1219800.6157 | 2691540.7416 | 1219791.4296
47 | 2691633.1961 | 1219791.3452 | 2691634.2175 | 1219790.2703 | 2691645.7305 | 1219780.8854 | 2691647.495 | 1219779.0032
48 | 2691685.6012 | 1219789.134 | 2691691.2225 | 1219786.1446 | 2691738.4751 | 1219795.8342 | 2691752.2527 | 1219792.6664 | 2691757.0158 | 1219789.4042 | 2691766.8778 | 1219773.9009 | 2691768.4566 | 1219772.864
49 | 2691482.774 | 1219857.5671 | 2691458.3322 | 1219873.8351
50 | 2691482.774 | 1219857.5671 | 2691466.8577 | 1219848.8056 | 2691449.9761 | 1219844.0987 | 2691446.9466 | 1219840.0671
51 | 2691545.279 | 1219787.8792 | 2691540.7416 | 1219791.4296
52 | 2691647.495 | 1219779.0032 | 2691625.8051 | 1219736.7527
53 | 2691768.4566 | 1219772.864 | 2691776.4383 | 1219767.6217 | 2691822.1859 | 1219747.0559
54 | 2691768.4566 | 1219772.864 | 2691727.3457 | 1219648.2944
55 | 2692143.8491 | 1219296.6788 | 2692136.4977 | 1219307.8036
56 | 2692132.9686 | 1219313.1442 | 2692136.4977 | 1219307.8036
57 | 2692143.8491 | 1219296.6788 | 2692137.6447 | 1219283.6628 | 2692133.5789 | 1219262.9078 | 2692133.5449 | 1219227.3383 | 2692135.5537 | 1219207.7708
58 | 2692132.9686 | 1219313.1442 | 2692123.217 | 1219331.0715
59 | 2692135.5537 | 1219207.7708 | 2692137.4963 | 1219188.8481
60 | 2692116.3771 | 1219340.6288 | 2692119.6179 | 1219337.688 | 2692123.217 | 1219331.0715
61 | 2691951.8368 | 1219383.0387 | 2692116.3771 | 1219340.6288
62 | 2691951.8368 | 1219383.0387 | 2691949.1673 | 1219381.9189 | 2691941.1883 | 1219387.0479
63 | 2692116.3771 | 1219340.6288 | 2692244.3179 | 1219452.7856
64 | 2691921.5507 | 1219401.4396 | 2691924.8862 | 1219395.7982 | 2691936.6338 | 1219389.9755 | 2691941.1883 | 1219387.0479
65 | 2692137.4963 | 1219188.8481 | 2692138.9029 | 1219175.1458
66 | 2692379.8597 | 1219182.8962 | 2692381.2096 | 1219173.3762
67 | 2692419.2033 | 1219247.0649 | 2692417.3332 | 1219244.3229 | 2692388.3919 | 1219230.2087 | 2692379.2414 | 1219217.3024 | 2692377.2337 | 1219201.4159 | 2692379.8597 | 1219182.8962
68 | 2692381.2096 | 1219173.3762 | 2692382.1341 | 1219166.8569 | 2692380.7495 | 1219157.0385
69 | 2692419.2033 | 1219247.0649 | 2692425.7147 | 1219249.5565 | 2692428.7704 | 1219250.7269
70 | 2692425.3478 | 1219402.2813 | 2692244.3179 | 1219452.7856
71 | 2691921.5507 | 1219401.4396 | 2691918.4627 | 1219375.3184 | 2691918.1915 | 1219370.3712
72 | 2691921.5507 | 1219401.4396 | 2691917.3842 | 1219408.484
73 | 2691910.3793 | 1219430.4094 | 2691912.916 | 1219416.0386 | 2691917.3842 | 1219408.484
74 | 2691910.3793 | 1219430.4094 | 2691899.431 | 1219440.0138 | 2691835.7224 | 1219484.8846 | 2691823.3356 | 1219494.7672 | 2691814.2569 | 1219502.2547
75 | 2691814.2569 | 1219502.2547 | 2691811.1745 | 1219508.7228 | 2691804.2321 | 1219516.4656 | 2691778.9702 | 1219537.4019
76 | 2691458.3322 | 1219873.8351 | 2691451.037 | 1219878.6906
77 | 2691375.9651 | 1219725.5704 | 2691379.6915 | 1219723.5928 | 2691391.8558 | 1219728.6162 | 2691402.7993 | 1219745.9293 | 2691420.8137 | 1219768.3212 | 2691424.4289 | 1219773.5803 | 2691425.9327 | 1219783.3879 | 2691434.1073 | 1219798.635 | 2691441.0424 | 1219820.4675 | 2691442.7324 | 1219834.4587 | 2691446.9466 | 1219840.0671
78 | 2691727.3457 | 1219648.2944 | 2691750.8919 | 1219636.2153 | 2691775.2317 | 1219615.487 | 2691780.6408 | 1219604.7963 | 2691781.9559 | 1219602.1926 | 2691769.6121 | 1219582.7223 | 2691767.5092 | 1219574.8845
79 | 2691778.9702 | 1219537.4019 | 2691774.3725 | 1219543.2129 | 2691771.5969 | 1219554.8893 | 2691767.5092 | 1219574.8845
80 | 2691778.9702 | 1219537.4019 | 2691764.5579 | 1219507.8484 | 2691762.5791 | 1219490.973 | 2691759.7904 | 1219481.8349 | 2691757.1857 | 1219481.0285
81 | 2691757.1857 | 1219481.0285 | 2691749.9255 | 1219478.7808 | 2691747.7346 | 1219466.3052 | 2691748.6303 | 1219457.4351 | 2691751.6882 | 1219451.3772
82 | 2691439.524 | 1219886.3534 | 2691451.037 | 1219878.6906
83 | 2691751.6882 | 1219451.3772 | 2691579.3672 | 1219490.5093
84 | 2691411.1179 | 1219908.9804 | 2691418.8967 | 1219900.0825 | 2691439.524 | 1219886.3534
85 | 2692428.7704 | 1219250.7269 | 2692426.5139 | 1219267.0143 | 2692424.4865 | 1219397.6175 | 2692425.3478 | 1219402.2813
86 | 2692425.3478 | 1219402.2813 | 2692726.0243 | 1219571.9555
87 | 2691959.7197 | 1219939.2132 | 2691951.3508 | 1219938.2909
88 | 2691959.7197 | 1219939.2132 | 2691978.938 | 1219941.331
89 | 2691910.3774 | 1219945.6064 | 2691921.3119 | 1219941.3973 | 2691946.1998 | 1219937.7233 | 2691951.3508 | 1219938.2909
90 | 2691978.938 | 1219941.331 | 2691979.6084 | 1219941.4049
91 | 2691910.3774 | 1219945.6064 | 2691909.041 | 1219946.1208
92 | 2692015.6452 | 1219950.0818 | 2691984.8075 | 1219941.9778 | 2691979.6084 | 1219941.4049
93 | 2691909.041 | 1219946.1208 | 2691885.626 | 1219955.1341
94 | 2692025.1096 | 1219938.7313 | 2692023.0295 | 1219946.1376 | 2692015.6452 | 1219950.0818 | 2692015.6452 | 1219950.0818
95 | 2691885.626 | 1219955.1341 | 2691880.766 | 1219957.0049 | 2691863.7872 | 1219964.6807
96 | 2692025.1096 | 1219938.7313 | 2692037.3089 | 1219936.029 | 2692049.1146 | 1219933.265 | 2692069.3139 | 1219930.9756 | 2692081.9992 | 1219931.6943 | 2692135.7185 | 1219943.1773 | 2692145.5426 | 1219944.7803
97 | 2692025.1096 | 1219938.7313 | 2692018.0335 | 1219938.444 | 2692007.3094 | 1219936.0434 | 2691996.5635 | 1219931.6188 | 2691983.5409 | 1219924.2751
98 | 2691925.5359 | 1220004.579 | 2691893.1891 | 1220013.1398
99 | 2691950.3476 | 1219998.4517 | 2691946.5965 | 1219999.0051 | 2691925.5359 | 1220004.579
100 | 2691881.9711 | 1220016.1087 | 2691893.1891 | 1220013.1398
101 | 2691950.3476 | 1219998.4517 | 2691953.4193 | 1219997.9986 | 2691960.0789 | 1219997.7345 | 2691966.9168 | 1219998.2071 | 2691974.8798 | 1219999.3381
102 | 2691896.5345 | 1220020.5142 | 2691881.9711 | 1220016.1087
103 | 2691881.9711 | 1220016.1087 | 2691855.8911 | 1220010.1094
104 | 2691984.5966 | 1220001.7936 | 2691976.1398 | 1219999.517 | 2691974.8798 | 1219999.3381
105 | 2691896.5345 | 1220020.5142 | 2691901.9464 | 1220022.2123
106 | 2691896.5345 | 1220020.5142 | 2691886.4642 | 1220022.9605 | 2691874.7751 | 1220027.0386 | 2691859.1938 | 1220033.353
107 | 2691835.9757 | 1220007.5987 | 2691844.6642 | 1220008.2391 | 2691853.3715 | 1220009.5298 | 2691855.8911 | 1220010.1094
108 | 2691901.9464 | 1220022.2123 | 2691913.6781 | 1220025.8935 | 2691921.5946 | 1220029.2513 | 2691929.9469 | 1220033.383 | 2691931.6326 | 1220034.1652
109 | 2691839.5169 | 1220041.3271 | 2691859.1938 | 1220033.353
110 | 2691966.4409 | 1219914.632 | 2691957.5393 | 1219909.6122 | 2691940.2409 | 1219902.4403 | 2691934.9615 | 1219900.5295
111 | 2691966.4409 | 1219914.632 | 2691983.5409 | 1219924.2751
112 | 2691934.9615 | 1219900.5295 | 2691924.7095 | 1219896.819 | 2691912.0336 | 1219894.4996 | 2691909.9861 | 1219894.5405
113 | 2691909.9861 | 1219894.5405 | 2691877.1386 | 1219895.1967
114 | 2691877.1386 | 1219895.1967 | 2691859.9113 | 1219895.5408 | 2691857.7496 | 1219895.9831
115 | 2692145.5426 | 1219944.7803 | 2692154.9156 | 1219946.3097 | 2692154.9156 | 1219946.3097
116 | 2691857.7496 | 1219895.9831 | 2691851.9967 | 1219897.16
117 | 2692154.9156 | 1219946.3097 | 2692183.0812 | 1219950.048 | 2692187.4019 | 1219950.3092
118 | 2691961.6508 | 1220050.1862 | 2691950.2985 | 1220042.8258 | 2691948.3741 | 1220041.933
119 | 2691976.0701 | 1220059.5352 | 2691961.6508 | 1220050.1862
120 | 2691948.3741 | 1220041.933 | 2691931.6326 | 1220034.1652
121 | 2691863.7872 | 1219964.6807 | 2691855.5149 | 1219968.4205
122 | 2691836.946 | 1219978.0796 | 2691851.2516 | 1219970.3479 | 2691855.5149 | 1219968.4205
123 | 2691851.9967 | 1219897.16 | 2691847.3738 | 1219898.1058
124 | 2691233.3261 | 1220109.8379 | 2691233.663 | 1220124.4976 | 2691235.3318 | 1220131.808
125 | 2691824.1439 | 1219907.7915 | 2691833.0077 | 1219903.4427 | 2691845.6596 | 1219898.4565 | 2691847.3738 | 1219898.1058
126 | 2691813.2476 | 1219913.1375 | 2691824.1439 | 1219907.7915
127 | 2691795.3113 | 1219921.274 | 2691808.7289 | 1219915.3545 | 2691813.2476 | 1219913.1375
128 | 2691795.3113 | 1219921.274 | 2691802.1628 | 1219907.092 | 2691803.9415 | 1219892.1054
129 | 2693189.8982 | 1219879.2295 | 2693214.0534 | 1219881.7091 | 2693231.6253 | 1219876.1776
130 | 2693189.8982 | 1219879.2295 | 2693191.7439 | 1219883.0054 | 2693197.0967 | 1219891.5729 | 2693208.2612 | 1219898.2967 | 2693228.5615 | 1219908.0211 | 2693231.8104 | 1219911.504
131 | 2692865.1881 | 1219494.0702 | 2693189.8982 | 1219879.2295
132 | 2693274.8309 | 1219996.974 | 2693249.4227 | 1219930.3853 | 2693231.8104 | 1219911.504
133 | 2692865.1881 | 1219494.0702 | 2692861.6904 | 1219500.8093 | 2692813.96 | 1219527.0726 | 2692737.9894 | 1219564.0596 | 2692733.6307 | 1219567.0877
134 | 2692726.0243 | 1219571.9555 | 2692730.2095 | 1219569.4645 | 2692733.6307 | 1219567.0877

## bus_geodata
| x | y | coords
0 | 2690941.6991 | 1219815.2932
1 | 2691278.3927 | 1220054.5387
2 | 2691278.5864 | 1220090.1728
3 | 2691539.2543 | 1220731.2044
4 | 2691532.4058 | 1220712.0146
5 | 2691541.6863 | 1220751.8783
6 | 2691520.9732 | 1220682.6566
7 | 2691721.9809 | 1221071.106
8 | 2691786.3257 | 1220540.9525
9 | 2691785.6801 | 1220528.6321
10 | 2691748.8141 | 1221086.6025
11 | 2691773.29 | 1221105.8982
12 | 2692052.897 | 1221280.3158
13 | 2691722.2884 | 1220277.7606
14 | 2691710.9434 | 1220246.5198
15 | 2691730.6422 | 1220302.1965
16 | 2691701.3356 | 1220225.8908
17 | 2691731.5497 | 1220304.9078
18 | 2691492.8465 | 1220207.542
19 | 2691748.3626 | 1220354.2083
20 | 2691522.3251 | 1220121.9576
21 | 2691762.0239 | 1220390.8404
22 | 2691564.6602 | 1220128.5537
23 | 2691703.7487 | 1220058.4583
24 | 2691496.8704 | 1220053.6865
25 | 2691820.3479 | 1219987.0504
26 | 2691515.6869 | 1220029.9345
27 | 2691377.2041 | 1220019.854
28 | 2691353.6932 | 1220045.311
29 | 2691405.8546 | 1219927.1035
30 | 2691269.1216 | 1220139.9622
31 | 2691275.3077 | 1220106.323
32 | 2691268.1885 | 1220111.3396
33 | 2691281.1092 | 1220102.2308
34 | 2691239.4374 | 1220149.7924
35 | 2691601.6029 | 1219808.7027
36 | 2691555.3856 | 1219828.5774
37 | 2691604.5529 | 1219807.3004
38 | 2691533.6375 | 1219832.6466
39 | 2691623.3561 | 1219801.7001
40 | 2691487.6314 | 1219854.0837
41 | 2691633.1961 | 1219791.3452
42 | 2691685.6012 | 1219789.134
43 | 2691482.774 | 1219857.5671
44 | 2691540.7416 | 1219791.4296
45 | 2691647.495 | 1219779.0032
46 | 2691768.4566 | 1219772.864
47 | 2692136.4977 | 1219307.8036
48 | 2692143.8491 | 1219296.6788
49 | 2692132.9686 | 1219313.1442
50 | 2692135.5537 | 1219207.7708
51 | 2692123.217 | 1219331.0715
52 | 2691951.8368 | 1219383.0387
53 | 2692116.3771 | 1219340.6288
54 | 2691941.1883 | 1219387.0479
55 | 2692137.4963 | 1219188.8481
56 | 2692138.9029 | 1219175.1458
57 | 2692379.8597 | 1219182.8962
58 | 2692381.2096 | 1219173.3762
59 | 2692419.2033 | 1219247.0649
60 | 2692244.3179 | 1219452.7856
61 | 2691918.1915 | 1219370.3712
62 | 2691921.5507 | 1219401.4396
63 | 2691917.3842 | 1219408.484
64 | 2691910.3793 | 1219430.4094
65 | 2691814.2569 | 1219502.2547
66 | 2691458.3322 | 1219873.8351
67 | 2691446.9466 | 1219840.0671
68 | 2691545.279 | 1219787.8792
69 | 2691625.8051 | 1219736.7527
70 | 2691727.3457 | 1219648.2944
71 | 2691767.5092 | 1219574.8845
72 | 2691778.9702 | 1219537.4019
73 | 2691822.1859 | 1219747.0559
74 | 2691757.1857 | 1219481.0285
75 | 2691451.037 | 1219878.6906
76 | 2691375.9651 | 1219725.5704
77 | 2691751.6882 | 1219451.3772
78 | 2691579.3672 | 1219490.5093
79 | 2692380.7495 | 1219157.0385
80 | 2691411.1179 | 1219908.9804
81 | 2691439.524 | 1219886.3534
82 | 2692428.7704 | 1219250.7269
83 | 2692425.3478 | 1219402.2813
84 | 2691959.7197 | 1219939.2132
85 | 2691951.3508 | 1219938.2909
86 | 2691978.938 | 1219941.331
87 | 2691910.3774 | 1219945.6064
88 | 2691979.6084 | 1219941.4049
89 | 2691909.041 | 1219946.1208
90 | 2692015.6452 | 1219950.0818
91 | 2691885.626 | 1219955.1341
92 | 2692025.1096 | 1219938.7313
93 | 2691925.5359 | 1220004.579
94 | 2691893.1891 | 1220013.1398
95 | 2691950.3476 | 1219998.4517
96 | 2691881.9711 | 1220016.1087
97 | 2691974.8798 | 1219999.3381
98 | 2691896.5345 | 1220020.5142
99 | 2691855.8911 | 1220010.1094
100 | 2691984.5966 | 1220001.7936
101 | 2691901.9464 | 1220022.2123
102 | 2691859.1938 | 1220033.353
103 | 2691835.9757 | 1220007.5987
104 | 2691966.4409 | 1219914.632
105 | 2691934.9615 | 1219900.5295
106 | 2691983.5409 | 1219924.2751
107 | 2691909.9861 | 1219894.5405
108 | 2691877.1386 | 1219895.1967
109 | 2692145.5426 | 1219944.7803
110 | 2691857.7496 | 1219895.9831
111 | 2692154.9157 | 1219946.3097
112 | 2691961.6508 | 1220050.1862
113 | 2691948.3741 | 1220041.9329
114 | 2691976.0701 | 1220059.5352
115 | 2691931.6326 | 1220034.1652
116 | 2691863.7872 | 1219964.6807
117 | 2691855.5149 | 1219968.4205
118 | 2691836.946 | 1219978.0796
119 | 2691839.5169 | 1220041.3271
120 | 2691851.9967 | 1219897.16
121 | 2691235.3318 | 1220131.808
122 | 2692187.4019 | 1219950.3092
123 | 2691847.3738 | 1219898.1058
124 | 2691813.2476 | 1219913.1375
125 | 2691824.1439 | 1219907.7915
126 | 2691795.3113 | 1219921.274
127 | 2691803.9415 | 1219892.1054
128 | 2691233.3261 | 1220109.8379
129 | 2693231.6253 | 1219876.1776
130 | 2693189.8982 | 1219879.2295
131 | 2693231.8104 | 1219911.504
132 | 2692865.1881 | 1219494.0702
133 | 2692733.6307 | 1219567.0877
134 | 2693274.8309 | 1219996.974
135 | 2692726.0243 | 1219571.9555
136 | 2692025.1096 | 1219938.7313

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98535 | -0.28292 | 0.0022452 | 0.00056269
1 | 0.9862 | -0.26624 | 0.0015462 | 0.00038752
2 | 0.98649 | -0.26056 | 0.0014847 | 0.0003721
3 | 0.98131 | -0.36189 | 0.00026289 | 6.5886e-05
4 | 0.98138 | -0.3604 | 0.00046292 | 0.00011602
5 | 0.98123 | -0.36331 | 0 | 0
6 | 0.98151 | -0.35785 | 0.00068502 | 0.00017168
7 | 0.97997 | -0.38819 | 0 | 0
8 | 0.98294 | -0.32977 | 0.0015412 | 0.00038627
9 | 0.98302 | -0.32827 | 0.0018962 | 0.00047522
10 | 0.97987 | -0.3903 | 0.0010932 | 0.00027397
11 | 0.97979 | -0.39185 | 0.0022796 | 0.00057133
12 | 0.97968 | -0.39399 | 0.00035252 | 8.8349e-05
13 | 0.98524 | -0.28463 | 0.0020657 | 0.00051771
14 | 0.98571 | -0.27562 | 0.0012185 | 0.0003054
15 | 0.98493 | -0.29067 | 0 | 0
16 | 0.98605 | -0.26894 | 0.00036013 | 9.0257e-05
17 | 0.9849 | -0.29134 | 0.0039519 | 0.00099043
18 | 0.98926 | -0.20656 | 0.00030728 | 7.7012e-05
19 | 0.98447 | -0.29984 | 0.00016183 | 4.0558e-05
20 | 0.99067 | -0.1792 | 0.00013756 | 3.4475e-05
21 | 0.98415 | -0.30611 | 0.00029832 | 7.4766e-05
22 | 0.99141 | -0.16484 | 0.00020169 | 5.0548e-05
23 | 0.99409 | -0.11318 | 0.0001965 | 4.9248e-05
24 | 0.98946 | -0.2026 | 0.00030627 | 7.6759e-05
25 | 0.99645 | -0.067931 | 0.0010814 | 0.00027102
26 | 0.98946 | -0.20269 | 0.0001698 | 4.2555e-05
27 | 0.98784 | -0.23429 | 0.0007113 | 0.00017827
28 | 0.98751 | -0.24069 | 0.00094415 | 0.00023663
29 | 0.98681 | -0.25439 | 0.00033358 | 8.3602e-05
30 | 0.98664 | -0.25759 | 0.00077725 | 0.0001948
31 | 0.98667 | -0.25711 | 0 | 0
32 | 0.98661 | -0.25831 | 0 | 0
33 | 0.98672 | -0.25603 | 0.00082626 | 0.00020708
34 | 0.9865 | -0.26042 | 0 | 0
35 | 0.98456 | -0.29841 | 0.005019 | 0.0012579
36 | 0.985 | -0.28979 | 0.00087686 | 0.00021976
37 | 0.98453 | -0.29889 | 0.0014374 | 0.00036026
38 | 0.98519 | -0.28593 | 0.0010013 | 0.00025095
39 | 0.98439 | -0.30169 | 0 | 0
40 | 0.98566 | -0.27674 | 0 | 0
41 | 0.98436 | -0.30235 | 0.0010506 | 0.0002633
42 | 0.98395 | -0.31035 | 0.00077986 | 0.00019545
43 | 0.98572 | -0.27564 | 0 | 0
44 | 0.98558 | -0.27832 | 0.000553 | 0.0001386
45 | 0.98433 | -0.30287 | 0.00065426 | 0.00016397
46 | 0.98334 | -0.32235 | 0.00092204 | 0.00023109
47 | 0.97941 | -0.39985 | 0.00028349 | 7.1049e-05
48 | 0.97939 | -0.40019 | 0 | 0
49 | 0.97942 | -0.39965 | 0 | 0
50 | 0.97928 | -0.4025 | 0.00097296 | 0.00024385
51 | 0.97945 | -0.39903 | 0.0014999 | 0.00037591
52 | 0.98038 | -0.38066 | 0 | 0
53 | 0.97949 | -0.39834 | 0.00039615 | 9.9285e-05
54 | 0.98045 | -0.37937 | 0.00070581 | 0.00017689
55 | 0.97927 | -0.40264 | 0.00012084 | 3.0285e-05
56 | 0.97927 | -0.40272 | 0.00030294 | 7.5923e-05
57 | 0.97738 | -0.44 | 0.00034465 | 8.6377e-05
58 | 0.97736 | -0.44037 | 0.00031081 | 7.7897e-05
59 | 0.97757 | -0.43622 | 0 | 0
60 | 0.97873 | -0.41328 | 0.00080798 | 0.0002025
61 | 0.98057 | -0.37697 | 0.00050125 | 0.00012563
62 | 0.98058 | -0.37669 | 0 | 0
63 | 0.98063 | -0.37579 | 0.00041238 | 0.00010335
64 | 0.98076 | -0.37319 | 0 | 0
65 | 0.98144 | -0.35985 | 0 | 0
66 | 0.986 | -0.27017 | 0.00044649 | 0.0001119
67 | 0.98569 | -0.27617 | 0.00026569 | 6.6589e-05
68 | 0.98558 | -0.27837 | 0.00048141 | 0.00012065
69 | 0.98429 | -0.30361 | 0.00086397 | 0.00021653
70 | 0.98257 | -0.33754 | 0 | 0
71 | 0.98195 | -0.34964 | 0 | 0
72 | 0.98172 | -0.35426 | 0 | 0
73 | 0.98326 | -0.32397 | 0.0015076 | 0.00037784
74 | 0.98166 | -0.35545 | 0.00042455 | 0.0001064
75 | 0.98608 | -0.26851 | 0.0030636 | 0.00076782
76 | 0.98563 | -0.27734 | 0.00045133 | 0.00011311
77 | 0.98164 | -0.35586 | 0.00034049 | 8.5336e-05
78 | 0.98159 | -0.35677 | 0.0002834 | 7.1026e-05
79 | 0.97734 | -0.44089 | 0.0017501 | 0.00043861
80 | 0.98661 | -0.25827 | 0.00039178 | 9.819e-05
81 | 0.98623 | -0.26572 | 0.00034816 | 8.7258e-05
82 | 0.9776 | -0.43577 | 0 | 0
83 | 0.97793 | -0.4291 | 0.00035208 | 8.8239e-05
84 | 0.99976 | -0.0046444 | 0.00097804 | 0.00024512
85 | 1 | 0 | -0.14824 | -0.037106
86 | 0.99922 | -0.014988 | 0.00085427 | 0.0002141
87 | 0.9989 | -0.020916 | 0.0010229 | 0.00025636
88 | 0.9992 | -0.015339 | 0.0012743 | 0.00031938
89 | 0.99887 | -0.021623 | 0.0013942 | 0.00034941
90 | 0.99824 | -0.033844 | 0.0020587 | 0.00051595
91 | 0.99823 | -0.033858 | 0.0012642 | 0.00031684
92 | 0.99785 | -0.041285 | 0 | 0
93 | 0.99386 | -0.1178 | 0.0020337 | 0.00050969
94 | 0.99405 | -0.11418 | 0.001323 | 0.00033158
95 | 0.99377 | -0.11965 | 0.0016585 | 0.00041565
96 | 0.99413 | -0.11265 | 0 | 0
97 | 0.99371 | -0.12071 | 0.0015684 | 0.00039307
98 | 0.99389 | -0.11732 | 0 | 0
99 | 0.99474 | -0.10091 | 0.0015206 | 0.00038109
100 | 0.9937 | -0.12086 | 0.00086965 | 0.00021795
101 | 0.99381 | -0.11877 | 0.0013029 | 0.00032653
102 | 0.99378 | -0.11936 | 0.0016152 | 0.00040481
103 | 0.99522 | -0.09156 | 0.0012048 | 0.00030196
104 | 0.99686 | -0.060425 | 0.00078369 | 0.00019641
105 | 0.99642 | -0.068929 | 0.0011798 | 0.00029569
106 | 0.99712 | -0.055328 | 0.0031489 | 0.00078918
107 | 0.99611 | -0.074755 | 0.001884 | 0.00047216
108 | 0.99579 | -0.081081 | 0.0010683 | 0.00026774
109 | 0.9969 | -0.059564 | 0.0033787 | 0.00084679
110 | 0.99561 | -0.084459 | 0.00066201 | 0.00016592
111 | 0.99686 | -0.060418 | 0.0012989 | 0.00032553
112 | 0.99316 | -0.13146 | 0.0039742 | 0.00099602
113 | 0.99326 | -0.12941 | 0.0022771 | 0.00057071
114 | 0.9931 | -0.13251 | 0.0034382 | 0.0008617
115 | 0.99342 | -0.12625 | 0.0035235 | 0.00088306
116 | 0.99762 | -0.045366 | 0.0029997 | 0.00075179
117 | 0.9974 | -0.049632 | 0.0016636 | 0.00041693
118 | 0.9969 | -0.059328 | 0.001702 | 0.00042656
119 | 0.99376 | -0.11984 | 0.0013023 | 0.0003264
120 | 0.99556 | -0.085412 | 0.0016906 | 0.0004237
121 | 0.98646 | -0.26121 | 0.0012302 | 0.00030832
122 | 0.99674 | -0.062619 | 0.003832 | 0.00096038
123 | 0.99553 | -0.086037 | 0.0032146 | 0.00080565
124 | 0.9954 | -0.088538 | 0.0016545 | 0.00041466
125 | 0.99543 | -0.087953 | 0.0015793 | 0.0003958
126 | 0.99538 | -0.088914 | 0 | 0
127 | 0.99535 | -0.089502 | 0.001083 | 0.00027142
128 | 0.98643 | -0.26167 | 0.0011604 | 0.00029083
129 | 0.97474 | -0.49232 | 0.004024 | 0.0010085
130 | 0.9749 | -0.48917 | 0 | 0
131 | 0.97481 | -0.49106 | 0.004305 | 0.0010789
132 | 0.97625 | -0.46241 | 0 | 0
133 | 0.97666 | -0.45433 | 0.00081564 | 0.00020442
134 | 0.97466 | -0.49393 | 0.0032269 | 0.00080873
135 | 0.97669 | -0.45381 | 0.003196 | 0.000801
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0022452 | -0.00056269 | 0.0022469 | 0.00055856 | 1.7796e-06 | -4.1268e-06 | 0.0033905 | 0.0033887 | 0.0033905 | 0.98535 | -0.28292 | 0.9862 | -0.26624 | 0.93146
1 | -0.0037932 | -0.00094609 | 0.0037942 | 0.00094568 | 1.023e-06 | -4.0893e-07 | 0.0057217 | 0.0057213 | 0.0057217 | 0.9862 | -0.26624 | 0.98649 | -0.26056 | 1.5719
2 | -0.0052789 | -0.0013178 | 0.0052795 | 0.0013178 | 5.6453e-07 | 5.7985e-08 | 0.0079608 | 0.0079607 | 0.0079608 | 0.98649 | -0.26056 | 0.98661 | -0.25831 | 2.187
3 | -0.0039934 | -0.00099306 | 0.0039937 | 0.00099298 | 2.8097e-07 | -7.8576e-08 | 0.0060527 | 0.0060526 | 0.0060527 | 0.98131 | -0.36189 | 0.98138 | -0.3604 | 1.6628
4 | 0.0037306 | 0.00092717 | -0.0037303 | -0.00092727 | 2.514e-07 | -1.0401e-07 | 0.0056541 | 0.0056542 | 0.0056542 | 0.98131 | -0.36189 | 0.98123 | -0.36331 | 1.5533
5 | -0.0044566 | -0.001109 | 0.0044572 | 0.0011089 | 5.3901e-07 | -5.3168e-08 | 0.0067545 | 0.0067544 | 0.0067545 | 0.98138 | -0.3604 | 0.98151 | -0.35785 | 1.8556
6 | 0.0037303 | 0.00092727 | -0.0037259 | -0.00092909 | 4.3966e-06 | -1.8112e-06 | 0.0056542 | 0.0056558 | 0.0056558 | 0.98123 | -0.36331 | 0.97997 | -0.38819 | 1.5538
7 | -0.0051422 | -0.0012806 | 0.005149 | 0.0012812 | 6.8495e-06 | 5.762e-07 | 0.0077929 | 0.0077915 | 0.0077929 | 0.98151 | -0.35785 | 0.98294 | -0.32977 | 2.1409
8 | 0.0037259 | 0.00092909 | -0.0037255 | -0.00092924 | 3.7171e-07 | -1.5246e-07 | 0.0056558 | 0.005656 | 0.005656 | 0.97997 | -0.38819 | 0.97987 | -0.3903 | 1.5538
9 | -0.0066903 | -0.0016675 | 0.0066908 | 0.0016676 | 4.7426e-07 | 1.4713e-07 | 0.010125 | 0.010125 | 0.010125 | 0.98294 | -0.32977 | 0.98302 | -0.32827 | 2.7815
10 | -0.0085869 | -0.0021428 | 0.008596 | 0.0021468 | 9.0441e-06 | 3.9755e-06 | 0.012995 | 0.012994 | 0.012995 | 0.98302 | -0.32827 | 0.98415 | -0.30611 | 3.57
11 | 0.0026324 | 0.00065527 | -0.0026322 | -0.00065555 | 1.9381e-07 | -2.8364e-07 | 0.0039959 | 0.0039961 | 0.0039961 | 0.97987 | -0.3903 | 0.97979 | -0.39185 | 1.0978
12 | 0.00035255 | 8.4222e-05 | -0.00035252 | -8.8349e-05 | 3.5331e-08 | -4.1273e-06 | 0.00053398 | 0.00053543 | 0.00053543 | 0.97979 | -0.39185 | 0.97968 | -0.39399 | 0.1471
13 | -0.015084 | -0.0037755 | 0.015091 | 0.0037792 | 6.4688e-06 | 3.7165e-06 | 0.02278 | 0.02278 | 0.02278 | 0.98524 | -0.28463 | 0.98571 | -0.27562 | 6.2582
14 | 0.013018 | 0.0032577 | -0.013015 | -0.0032557 | 3.7431e-06 | 2.0668e-06 | 0.01966 | 0.01966 | 0.01966 | 0.98524 | -0.28463 | 0.98493 | -0.29067 | 5.4011
15 | -0.016309 | -0.0040846 | 0.016314 | 0.0040876 | 5.1892e-06 | 3.03e-06 | 0.024619 | 0.024619 | 0.024619 | 0.98571 | -0.27562 | 0.98605 | -0.26894 | 6.7635
16 | 0.013015 | 0.0032557 | -0.013014 | -0.0032555 | 4.1442e-07 | 2.2884e-07 | 0.01966 | 0.01966 | 0.01966 | 0.98493 | -0.29067 | 0.9849 | -0.29134 | 5.4011
17 | -0.016674 | -0.0041779 | 0.016724 | 0.004207 | 4.9692e-05 | 2.9124e-05 | 0.025163 | 0.025162 | 0.025163 | 0.98605 | -0.26894 | 0.98926 | -0.20656 | 6.9128
18 | 0.0090624 | 0.002265 | -0.0090588 | -0.0022633 | 3.661e-06 | 1.6804e-06 | 0.01369 | 0.01369 | 0.01369 | 0.9849 | -0.29134 | 0.98447 | -0.29984 | 3.7609
19 | -0.017031 | -0.004284 | 0.017054 | 0.0042971 | 2.2287e-05 | 1.31e-05 | 0.025624 | 0.025623 | 0.025624 | 0.98926 | -0.20656 | 0.99067 | -0.1792 | 7.0395
20 | 0.0088969 | 0.0022228 | -0.0088943 | -0.0022216 | 2.6504e-06 | 1.1993e-06 | 0.013445 | 0.013445 | 0.013445 | 0.98447 | -0.29984 | 0.98415 | -0.30611 | 3.6938
21 | 0.057712 | 0.014481 | -0.057648 | -0.014445 | 6.4314e-05 | 3.6465e-05 | 0.086691 | 0.086693 | 0.086693 | 0.99067 | -0.1792 | 0.98946 | -0.2026 | 5.9542
22 | -0.074903 | -0.018813 | 0.074955 | 0.018843 | 5.1368e-05 | 3.0645e-05 | 0.11252 | 0.11252 | 0.11252 | 0.99067 | -0.1792 | 0.99141 | -0.16484 | 7.7281
23 | -0.075156 | -0.018894 | 0.075342 | 0.019005 | 0.00018586 | 0.0001109 | 0.11282 | 0.11282 | 0.11282 | 0.99141 | -0.16484 | 0.99409 | -0.11318 | 7.7488
24 | -0.075539 | -0.019054 | 0.075703 | 0.019152 | 0.000164 | 9.7855e-05 | 0.11311 | 0.11311 | 0.11311 | 0.99409 | -0.11318 | 0.99645 | -0.067931 | 7.7688
25 | 0.0001698 | 4.2166e-05 | -0.0001698 | -4.2555e-05 | 7.4058e-10 | -3.8876e-07 | 0.00025521 | 0.00025535 | 0.00025535 | 0.98946 | -0.2026 | 0.98946 | -0.20269 | 0.070151
26 | 0.057172 | 0.014326 | -0.057085 | -0.014277 | 8.6182e-05 | 4.8778e-05 | 0.085977 | 0.085979 | 0.085979 | 0.98946 | -0.2026 | 0.98784 | -0.23429 | 5.9052
27 | 0.027683 | 0.0069611 | -0.027652 | -0.0069418 | 3.1204e-05 | 1.9337e-05 | 0.041348 | 0.041348 | 0.041348 | 0.99645 | -0.067931 | 0.99522 | -0.09156 | 11.3595
28 | -0.10447 | -0.026384 | 0.10451 | 0.026411 | 4.3087e-05 | 2.6592e-05 | 0.15607 | 0.15607 | 0.15607 | 0.99645 | -0.067931 | 0.9969 | -0.059328 | 10.7194
29 | 0.010229 | 0.0025592 | -0.010226 | -0.0025577 | 3.1109e-06 | 1.5437e-06 | 0.015407 | 0.015407 | 0.015407 | 0.98784 | -0.23429 | 0.98751 | -0.24069 | 4.2326
30 | 0.046145 | 0.01154 | -0.046101 | -0.011516 | 4.4077e-05 | 2.3231e-05 | 0.069501 | 0.069503 | 0.069503 | 0.98784 | -0.23429 | 0.98681 | -0.25439 | 4.7736
31 | 0.0092816 | 0.002321 | -0.0092749 | -0.0023179 | 6.771e-06 | 3.1531e-06 | 0.013984 | 0.013985 | 0.013985 | 0.98751 | -0.24069 | 0.98672 | -0.25603 | 3.8419
32 | 0.045768 | 0.011433 | -0.045759 | -0.011428 | 8.4234e-06 | 4.4268e-06 | 0.069 | 0.069 | 0.069 | 0.98681 | -0.25439 | 0.98661 | -0.25827 | 4.739
33 | -0.00077725 | -0.0001948 | 0.00077727 | 0.00019437 | 1.7776e-08 | -4.2927e-07 | 0.0011722 | 0.0011721 | 0.0011722 | 0.98664 | -0.25759 | 0.98667 | -0.25711 | 0.32204
34 | 0.0076709 | 0.0019162 | -0.0076705 | -0.0019161 | 4.3612e-07 | 1.681e-07 | 0.011566 | 0.011567 | 0.011567 | 0.98667 | -0.25711 | 0.98661 | -0.25831 | 3.1776
35 | -0.0084482 | -0.0021106 | 0.0084486 | 0.0021108 | 4.3202e-07 | 1.8581e-07 | 0.012739 | 0.012739 | 0.012739 | 0.98667 | -0.25711 | 0.98672 | -0.25603 | 3.4996
36 | 0.002391 | 0.00059823 | -0.0023908 | -0.00059871 | 2.4076e-07 | -4.7639e-07 | 0.0036058 | 0.003606 | 0.003606 | 0.98661 | -0.25831 | 0.9865 | -0.26042 | 0.99067
37 | 0.0023908 | 0.00059871 | -0.0023907 | -0.00059889 | 8.9955e-08 | -1.7794e-07 | 0.003606 | 0.0036061 | 0.0036061 | 0.9865 | -0.26042 | 0.98646 | -0.26121 | 0.99069
38 | -0.037801 | -0.0094181 | 0.037817 | 0.0094254 | 1.5448e-05 | 7.3157e-06 | 0.057111 | 0.05711 | 0.057111 | 0.98456 | -0.29841 | 0.985 | -0.28979 | 3.9225
39 | 0.032782 | 0.0081602 | -0.032781 | -0.0081599 | 7.5109e-07 | 3.1455e-07 | 0.049526 | 0.049526 | 0.049526 | 0.98456 | -0.29841 | 0.98453 | -0.29889 | 3.4015
40 | -0.038694 | -0.0096452 | 0.038701 | 0.0096486 | 7.0828e-06 | 3.4063e-06 | 0.058435 | 0.058435 | 0.058435 | 0.985 | -0.28979 | 0.98519 | -0.28593 | 4.0134
41 | 0.031344 | 0.0077996 | -0.03134 | -0.007798 | 4.1591e-06 | 1.6556e-06 | 0.047353 | 0.047354 | 0.047354 | 0.98453 | -0.29889 | 0.98439 | -0.30169 | 3.2523
42 | -0.039702 | -0.0098995 | 0.039719 | 0.009908 | 1.7338e-05 | 8.4737e-06 | 0.059947 | 0.059946 | 0.059947 | 0.98519 | -0.28593 | 0.98566 | -0.27674 | 4.1172
43 | 0.002569 | 0.00064287 | -0.0025689 | -0.000643 | 8.0765e-08 | -1.299e-07 | 0.0038829 | 0.003883 | 0.003883 | 0.98439 | -0.30169 | 0.98436 | -0.30235 | 1.0668
44 | 0.028771 | 0.0071551 | -0.028759 | -0.0071509 | 1.1792e-05 | 4.1636e-06 | 0.043471 | 0.043472 | 0.043472 | 0.98439 | -0.30169 | 0.98395 | -0.31035 | 2.9857
45 | -0.040754 | -0.010166 | 0.040756 | 0.010167 | 2.116e-06 | 1.05e-06 | 0.061507 | 0.061507 | 0.061507 | 0.98566 | -0.27674 | 0.98572 | -0.27564 | 4.2244
46 | 0.0010345 | 0.00025814 | -0.0010344 | -0.00025918 | 7.7847e-08 | -1.0352e-06 | 0.0015613 | 0.0015617 | 0.0015617 | 0.98566 | -0.27674 | 0.98558 | -0.27832 | 0.42904
47 | 0.0015183 | 0.0003797 | -0.0015183 | -0.00037992 | 3.7359e-08 | -2.1655e-07 | 0.0022949 | 0.002295 | 0.002295 | 0.98436 | -0.30235 | 0.98433 | -0.30287 | 0.63048
48 | 0.027979 | 0.0069555 | -0.027963 | -0.0069501 | 1.5893e-05 | 5.3595e-06 | 0.042293 | 0.042294 | 0.042294 | 0.98395 | -0.31035 | 0.98334 | -0.32235 | 2.9048
49 | -0.041473 | -0.010345 | 0.041484 | 0.01035 | 1.0783e-05 | 5.4034e-06 | 0.062589 | 0.062588 | 0.062589 | 0.98572 | -0.27564 | 0.986 | -0.27017 | 4.2987
50 | 0.00071707 | 0.00017737 | -0.00071705 | -0.00017788 | 1.7875e-08 | -5.0783e-07 | 0.0010816 | 0.0010818 | 0.0010818 | 0.98572 | -0.27564 | 0.98569 | -0.27617 | 0.2972
51 | 0.00048141 | 0.00012058 | -0.00048141 | -0.00012065 | 1.1413e-09 | -7.269e-08 | 0.0007268 | 0.00072683 | 0.00072683 | 0.98558 | -0.27832 | 0.98558 | -0.27837 | 0.19968
52 | 0.00086401 | 0.00021595 | -0.00086397 | -0.00021653 | 3.0378e-08 | -5.8423e-07 | 0.0013059 | 0.0013061 | 0.0013061 | 0.98433 | -0.30287 | 0.98429 | -0.30361 | 0.35883
53 | 0.0015077 | 0.00037716 | -0.0015076 | -0.00037784 | 1.1654e-07 | -6.8278e-07 | 0.0022813 | 0.0022816 | 0.0022816 | 0.98334 | -0.32235 | 0.98326 | -0.32397 | 0.6268
54 | 0.025534 | 0.0063419 | -0.025515 | -0.0063368 | 1.8341e-05 | 5.0873e-06 | 0.038618 | 0.03862 | 0.03862 | 0.98334 | -0.32235 | 0.98257 | -0.33754 | 2.6525
55 | 0.0013969 | 0.00034845 | -0.0013969 | -0.0003486 | 2.2511e-08 | -1.534e-07 | 0.0021217 | 0.0021218 | 0.0021218 | 0.97941 | -0.39985 | 0.97939 | -0.40019 | 0.58291
56 | -0.0016804 | -0.0004195 | 0.0016804 | 0.00041943 | 1.5639e-08 | -7.055e-08 | 0.0025524 | 0.0025524 | 0.0025524 | 0.97941 | -0.39985 | 0.97942 | -0.39965 | 0.70122
57 | 0.0013969 | 0.0003486 | -0.0013967 | -0.00034965 | 1.5334e-07 | -1.0445e-06 | 0.0021218 | 0.0021222 | 0.0021222 | 0.97939 | -0.40019 | 0.97928 | -0.4025 | 0.58302
58 | -0.0016804 | -0.00041943 | 0.0016805 | 0.0004192 | 4.9856e-08 | -2.2493e-07 | 0.0025524 | 0.0025523 | 0.0025524 | 0.97942 | -0.39965 | 0.97945 | -0.39903 | 0.70121
59 | 0.00042378 | 0.0001058 | -0.00042378 | -0.00010604 | 2.9569e-09 | -2.3743e-07 | 0.00064379 | 0.00064388 | 0.00064388 | 0.97928 | -0.4025 | 0.97927 | -0.40264 | 0.17689
60 | -0.0031804 | -0.00079511 | 0.0031805 | 0.00079503 | 1.0422e-07 | -8.3178e-08 | 0.004831 | 0.004831 | 0.004831 | 0.97945 | -0.39903 | 0.97949 | -0.39834 | 1.3272
61 | 0.022797 | 0.0056591 | -0.022778 | -0.0056554 | 1.9052e-05 | 3.6306e-06 | 0.034581 | 0.034585 | 0.034585 | 0.98038 | -0.38066 | 0.97949 | -0.39834 | 2.3753
62 | -0.022797 | -0.0056591 | 0.022798 | 0.0056593 | 1.388e-06 | 2.6383e-07 | 0.034581 | 0.034581 | 0.034581 | 0.98038 | -0.38066 | 0.98045 | -0.37937 | 2.3751
63 | 0.019201 | 0.0047611 | -0.019188 | -0.004761 | 1.3557e-05 | 1.1689e-07 | 0.029152 | 0.029155 | 0.029155 | 0.97949 | -0.39834 | 0.97873 | -0.41328 | 2.0024
64 | -0.023504 | -0.0058362 | 0.023507 | 0.0058369 | 2.9886e-06 | 6.4736e-07 | 0.035652 | 0.035652 | 0.035652 | 0.98045 | -0.37937 | 0.98058 | -0.37669 | 2.4487
65 | 0.00030294 | 7.575e-05 | -0.00030294 | -7.5923e-05 | 1.0944e-09 | -1.7259e-07 | 0.00046026 | 0.00046032 | 0.00046032 | 0.97927 | -0.40264 | 0.97927 | -0.40272 | 0.12646
66 | 0.002061 | 0.00051624 | -0.0020609 | -0.00051633 | 3.5498e-08 | -9.7782e-08 | 0.0031376 | 0.0031377 | 0.0031377 | 0.97738 | -0.44 | 0.97736 | -0.44037 | 0.862
67 | -0.0024056 | -0.00060261 | 0.0024061 | 0.00060181 | 4.3281e-07 | -8.0173e-07 | 0.0036624 | 0.003662 | 0.0036624 | 0.97738 | -0.44 | 0.97757 | -0.43622 | 1.0061
68 | 0.0017501 | 0.00043844 | -0.0017501 | -0.00043861 | 4.3929e-08 | -1.7866e-07 | 0.0026645 | 0.0026646 | 0.0026646 | 0.97736 | -0.44037 | 0.97734 | -0.44089 | 0.73202
69 | -0.0024061 | -0.00060181 | 0.0024061 | 0.00060172 | 5.1383e-08 | -9.5225e-08 | 0.003662 | 0.0036619 | 0.003662 | 0.97757 | -0.43622 | 0.9776 | -0.43577 | 1.006
70 | 0.01838 | 0.0045585 | -0.018366 | -0.0045591 | 1.3743e-05 | -6.4454e-07 | 0.027926 | 0.02793 | 0.02793 | 0.97873 | -0.41328 | 0.97793 | -0.4291 | 1.9182
71 | -0.00050125 | -0.00012563 | 0.00050126 | 0.00012524 | 6.7808e-09 | -3.8996e-07 | 0.00076065 | 0.00076051 | 0.00076065 | 0.98057 | -0.37697 | 0.98058 | -0.37669 | 0.20897
72 | -0.024008 | -0.0059621 | 0.024009 | 0.0059623 | 1.0173e-06 | 2.3809e-07 | 0.036413 | 0.036412 | 0.036413 | 0.98058 | -0.37669 | 0.98063 | -0.37579 | 2.5009
73 | -0.024422 | -0.0060657 | 0.024425 | 0.0060664 | 3.0055e-06 | 7.4405e-07 | 0.037038 | 0.037038 | 0.037038 | 0.98063 | -0.37579 | 0.98076 | -0.37319 | 2.5438
74 | -0.024425 | -0.0060664 | 0.02444 | 0.0060702 | 1.5418e-05 | 3.8114e-06 | 0.037038 | 0.037036 | 0.037038 | 0.98076 | -0.37319 | 0.98144 | -0.35985 | 2.5438
75 | -0.02444 | -0.0060702 | 0.024447 | 0.0060718 | 6.4687e-06 | 1.5964e-06 | 0.037036 | 0.037035 | 0.037036 | 0.98144 | -0.35985 | 0.98172 | -0.35426 | 2.5436
76 | -0.04193 | -0.010462 | 0.041934 | 0.010464 | 3.288e-06 | 1.6572e-06 | 0.063262 | 0.063262 | 0.063262 | 0.986 | -0.27017 | 0.98608 | -0.26851 | 4.3449
77 | 0.00045135 | 0.00011129 | -0.00045133 | -0.00011311 | 2.5085e-08 | -1.8221e-06 | 0.00068073 | 0.00068137 | 0.00068137 | 0.98569 | -0.27617 | 0.98563 | -0.27734 | 0.18719
78 | 0.025515 | 0.0063368 | -0.025501 | -0.0063327 | 1.4613e-05 | 4.0612e-06 | 0.03862 | 0.038622 | 0.038622 | 0.98257 | -0.33754 | 0.98195 | -0.34964 | 2.6526
79 | 0.025501 | 0.0063327 | -0.025495 | -0.0063312 | 5.5679e-06 | 1.5493e-06 | 0.038622 | 0.038623 | 0.038623 | 0.98195 | -0.34964 | 0.98172 | -0.35426 | 2.6527
80 | 0.0010485 | 0.00025934 | -0.0010485 | -0.00026009 | 5.8789e-08 | -7.4818e-07 | 0.001588 | 0.0015883 | 0.0015883 | 0.98172 | -0.35426 | 0.98166 | -0.35545 | 0.43635
81 | 0.00062392 | 0.00015369 | -0.0006239 | -0.00015414 | 1.2042e-08 | -4.4701e-07 | 0.00094479 | 0.00094495 | 0.00094495 | 0.98166 | -0.35545 | 0.98164 | -0.35586 | 0.2596
82 | -0.044997 | -0.011231 | 0.045003 | 0.011234 | 5.975e-06 | 3.1182e-06 | 0.067885 | 0.067885 | 0.067885 | 0.98608 | -0.26851 | 0.98623 | -0.26572 | 4.6624
83 | 0.00028341 | 6.88e-05 | -0.0002834 | -7.1026e-05 | 1.2208e-08 | -2.226e-06 | 0.00042882 | 0.00042961 | 0.00042961 | 0.98164 | -0.35586 | 0.98159 | -0.35677 | 0.11802
84 | 0.045367 | 0.01133 | -0.045351 | -0.011322 | 1.6057e-05 | 8.4076e-06 | 0.068409 | 0.06841 | 0.06841 | 0.98661 | -0.25827 | 0.98623 | -0.26572 | 4.6985
85 | -0.0024061 | -0.00060172 | 0.0024069 | 0.0006003 | 7.6323e-07 | -1.4155e-06 | 0.0036619 | 0.0036612 | 0.0036619 | 0.9776 | -0.43577 | 0.97793 | -0.4291 | 1.006
86 | 0.015607 | 0.0038706 | -0.015589 | -0.0038762 | 1.8235e-05 | -5.6343e-06 | 0.023733 | 0.023739 | 0.023739 | 0.97793 | -0.4291 | 0.97669 | -0.45381 | 1.6304
87 | -0.031713 | -0.007976 | 0.03172 | 0.0079804 | 7.0372e-06 | 4.3934e-06 | 0.04721 | 0.04721 | 0.04721 | 0.99976 | -0.0046444 | 1 | 0 | 12.9699
88 | 0.030735 | 0.0077309 | -0.03072 | -0.0077215 | 1.5179e-05 | 9.461e-06 | 0.045755 | 0.045755 | 0.045755 | 0.99976 | -0.0046444 | 0.99922 | -0.014988 | 12.57
89 | 0.11487 | 0.029126 | -0.11476 | -0.029054 | 0.00011536 | 7.1629e-05 | 0.17105 | 0.17105 | 0.17105 | 1 | 0 | 0.9989 | -0.020916 | 11.7483
90 | 0.029865 | 0.0075074 | -0.029865 | -0.007507 | 5.0049e-07 | 3.1148e-07 | 0.044483 | 0.044483 | 0.044483 | 0.99922 | -0.014988 | 0.9992 | -0.015339 | 12.2205
91 | 0.11374 | 0.028798 | -0.11373 | -0.028795 | 3.8584e-06 | 2.3944e-06 | 0.16953 | 0.16953 | 0.16953 | 0.9989 | -0.020916 | 0.99887 | -0.021623 | 11.6436
92 | 0.02859 | 0.0071877 | -0.028565 | -0.007172 | 2.524e-05 | 1.5668e-05 | 0.042585 | 0.042585 | 0.042585 | 0.9992 | -0.015339 | 0.99824 | -0.033844 | 11.6992
93 | 0.11234 | 0.028446 | -0.11227 | -0.028405 | 6.5957e-05 | 4.09e-05 | 0.16745 | 0.16745 | 0.16745 | 0.99887 | -0.021623 | 0.99823 | -0.033858 | 11.501
94 | 0.026506 | 0.006656 | -0.026497 | -0.0066502 | 9.407e-06 | 5.8106e-06 | 0.039516 | 0.039516 | 0.039516 | 0.99824 | -0.033844 | 0.99785 | -0.041285 | 10.8561
95 | 0.11101 | 0.028088 | -0.11095 | -0.02805 | 6.1272e-05 | 3.7968e-05 | 0.16557 | 0.16557 | 0.16557 | 0.99823 | -0.033858 | 0.99762 | -0.045366 | 11.3716
96 | 0.0085176 | 0.0021357 | -0.0085102 | -0.0021325 | 7.4144e-06 | 3.146e-06 | 0.012702 | 0.012703 | 0.012703 | 0.99785 | -0.041285 | 0.9969 | -0.059564 | 3.4897
97 | 0.017979 | 0.0045145 | -0.017967 | -0.0045074 | 1.2037e-05 | 7.121e-06 | 0.026814 | 0.026815 | 0.026815 | 0.99785 | -0.041285 | 0.99712 | -0.055328 | 7.3666
98 | -0.0061307 | -0.0015359 | 0.0061317 | 0.0015361 | 1.0571e-06 | 2.4286e-07 | 0.0091787 | 0.0091785 | 0.0091787 | 0.99386 | -0.1178 | 0.99405 | -0.11418 | 2.5216
99 | 0.004097 | 0.0010262 | -0.0040966 | -0.0010263 | 3.6088e-07 | -1.0046e-07 | 0.0061339 | 0.006134 | 0.006134 | 0.99386 | -0.1178 | 0.99377 | -0.11965 | 1.6852
100 | -0.0074547 | -0.0018677 | 0.0074553 | 0.0018679 | 5.4187e-07 | 1.9635e-07 | 0.011159 | 0.011159 | 0.011159 | 0.99405 | -0.11418 | 0.99413 | -0.11265 | 3.0657
101 | 0.0024382 | 0.00061066 | -0.002438 | -0.0006109 | 1.2328e-07 | -2.4067e-07 | 0.0036506 | 0.0036508 | 0.0036508 | 0.99377 | -0.11965 | 0.99371 | -0.12071 | 1.003
102 | 0.017446 | 0.0043749 | -0.017442 | -0.0043727 | 3.8803e-06 | 2.2867e-06 | 0.026114 | 0.026114 | 0.026114 | 0.99413 | -0.11265 | 0.99389 | -0.11732 | 7.1741
103 | -0.024901 | -0.0062429 | 0.024915 | 0.0062514 | 1.3942e-05 | 8.5755e-06 | 0.037273 | 0.037273 | 0.037273 | 0.99413 | -0.11265 | 0.99474 | -0.10091 | 10.2397
104 | 0.00086966 | 0.00021783 | -0.00086965 | -0.00021795 | 6.3787e-09 | -1.2586e-07 | 0.0013022 | 0.0013023 | 0.0013023 | 0.99371 | -0.12071 | 0.9937 | -0.12086 | 0.35776
105 | 0.014524 | 0.003642 | -0.014523 | -0.0036415 | 1.0058e-06 | 5.7022e-07 | 0.021746 | 0.021746 | 0.021746 | 0.99389 | -0.11732 | 0.99381 | -0.11877 | 5.974
106 | 0.0029179 | 0.00073062 | -0.0029176 | -0.00073095 | 2.8306e-07 | -3.314e-07 | 0.0043683 | 0.0043685 | 0.0043685 | 0.99389 | -0.11732 | 0.99378 | -0.11936 | 1.2001
107 | -0.026435 | -0.0066325 | 0.026447 | 0.0066398 | 1.1788e-05 | 7.2835e-06 | 0.039547 | 0.039547 | 0.039547 | 0.99474 | -0.10091 | 0.99522 | -0.09156 | 10.8646
108 | 0.01322 | 0.0033149 | -0.013215 | -0.0033123 | 4.7125e-06 | 2.6006e-06 | 0.019795 | 0.019795 | 0.019795 | 0.99381 | -0.11877 | 0.99342 | -0.12625 | 5.4382
109 | 0.0013024 | 0.00032614 | -0.0013023 | -0.0003264 | 3.0275e-08 | -2.557e-07 | 0.00195 | 0.0019501 | 0.0019501 | 0.99378 | -0.11936 | 0.99376 | -0.11984 | 0.53574
110 | 0.014031 | 0.0035198 | -0.014026 | -0.0035166 | 5.6859e-06 | 3.1886e-06 | 0.020946 | 0.020946 | 0.020946 | 0.99686 | -0.060425 | 0.99642 | -0.068929 | 5.7544
111 | -0.014815 | -0.0037162 | 0.014819 | 0.0037182 | 3.6006e-06 | 2.0484e-06 | 0.022116 | 0.022115 | 0.022116 | 0.99686 | -0.060425 | 0.99712 | -0.055328 | 6.0757
112 | 0.012846 | 0.0032209 | -0.012842 | -0.003219 | 3.5658e-06 | 1.9457e-06 | 0.019184 | 0.019184 | 0.019184 | 0.99642 | -0.068929 | 0.99611 | -0.074755 | 5.2704
113 | 0.010958 | 0.0027468 | -0.010955 | -0.0027451 | 3.3015e-06 | 1.6854e-06 | 0.01637 | 0.01637 | 0.01637 | 0.99611 | -0.074755 | 0.99579 | -0.081081 | 4.4972
114 | 0.0098867 | 0.0024774 | -0.0098851 | -0.0024766 | 1.5909e-06 | 7.6536e-07 | 0.014774 | 0.014774 | 0.014774 | 0.99579 | -0.081081 | 0.99561 | -0.084459 | 4.0587
115 | 0.0051315 | 0.0012858 | -0.0051313 | -0.0012857 | 2.0893e-07 | 9.8989e-09 | 0.0076594 | 0.0076594 | 0.0076594 | 0.9969 | -0.059564 | 0.99686 | -0.060418 | 2.1042
116 | 0.0092231 | 0.0023107 | -0.0092226 | -0.0023105 | 4.184e-07 | 1.9142e-07 | 0.013784 | 0.013784 | 0.013784 | 0.99561 | -0.084459 | 0.99556 | -0.085412 | 3.7869
117 | 0.0038324 | 0.00096022 | -0.003832 | -0.00096038 | 4.018e-07 | -1.6965e-07 | 0.0057205 | 0.0057207 | 0.0057207 | 0.99686 | -0.060418 | 0.99674 | -0.062619 | 1.5716
118 | -0.0074126 | -0.0018576 | 0.0074133 | 0.0018579 | 7.2391e-07 | 2.6075e-07 | 0.011106 | 0.011106 | 0.011106 | 0.99316 | -0.13146 | 0.99326 | -0.12941 | 3.0511
119 | 0.0034384 | 0.00086159 | -0.0034382 | -0.0008617 | 1.7103e-07 | -1.1291e-07 | 0.0051516 | 0.0051517 | 0.0051517 | 0.99316 | -0.13146 | 0.9931 | -0.13251 | 1.4153
120 | -0.0096905 | -0.0024286 | 0.0096919 | 0.0024293 | 1.4586e-06 | 6.9459e-07 | 0.014517 | 0.014517 | 0.014517 | 0.99326 | -0.12941 | 0.99342 | -0.12625 | 3.9883
121 | 0.10795 | 0.027298 | -0.10793 | -0.027285 | 2.2088e-05 | 1.3662e-05 | 0.1611 | 0.1611 | 0.1611 | 0.99762 | -0.045366 | 0.9974 | -0.049632 | 11.0643
122 | 0.10626 | 0.026868 | -0.10621 | -0.026837 | 4.939e-05 | 3.0517e-05 | 0.15861 | 0.15862 | 0.15862 | 0.9974 | -0.049632 | 0.9969 | -0.059328 | 10.8939
123 | 0.0075321 | 0.0018868 | -0.0075318 | -0.0018867 | 2.2425e-07 | 8.2164e-08 | 0.011257 | 0.011257 | 0.011257 | 0.99556 | -0.085412 | 0.99553 | -0.086037 | 3.0927
124 | 0.0011605 | 0.00029057 | -0.0011604 | -0.00029083 | 2.5465e-08 | -2.6662e-07 | 0.0017504 | 0.0017505 | 0.0017505 | 0.98646 | -0.26121 | 0.98643 | -0.26167 | 0.4809
125 | 0.0043173 | 0.0010811 | -0.0043169 | -0.0010811 | 3.9382e-07 | -7.5864e-08 | 0.0064527 | 0.0064528 | 0.0064528 | 0.99553 | -0.086037 | 0.99543 | -0.087953 | 1.7727
126 | -0.0027375 | -0.00068545 | 0.0027376 | 0.00068534 | 7.6213e-08 | -1.09e-07 | 0.0040921 | 0.004092 | 0.0040921 | 0.9954 | -0.088538 | 0.99543 | -0.087953 | 1.1242
127 | 0.001083 | 0.00027079 | -0.001083 | -0.00027103 | 1.9358e-08 | -2.4367e-07 | 0.0016188 | 0.0016189 | 0.0016189 | 0.9954 | -0.088538 | 0.99538 | -0.088914 | 0.44474
128 | 0.001083 | 0.00027103 | -0.001083 | -0.00027142 | 3.0313e-08 | -3.8148e-07 | 0.0016189 | 0.001619 | 0.001619 | 0.99538 | -0.088914 | 0.99535 | -0.089502 | 0.44478
129 | -0.004024 | -0.0010085 | 0.0040246 | 0.0010084 | 6.0428e-07 | -1.4565e-07 | 0.0061429 | 0.0061428 | 0.0061429 | 0.97474 | -0.49232 | 0.9749 | -0.48917 | 1.6876
130 | 0.007533 | 0.0018832 | -0.0075323 | -0.0018855 | 6.7668e-07 | -2.2904e-06 | 0.011496 | 0.011497 | 0.011497 | 0.9749 | -0.48917 | 0.97481 | -0.49106 | 0.78964
131 | -0.011558 | -0.0028916 | 0.011572 | 0.0028758 | 1.4687e-05 | -1.5761e-05 | 0.017639 | 0.01763 | 0.017639 | 0.9749 | -0.48917 | 0.97625 | -0.46241 | 1.2115
132 | 0.0032273 | 0.00080659 | -0.0032269 | -0.00080873 | 4.4175e-07 | -2.1377e-06 | 0.0049256 | 0.0049264 | 0.0049264 | 0.97481 | -0.49106 | 0.97466 | -0.49393 | 0.67671
133 | -0.011572 | -0.0028758 | 0.011577 | 0.0028711 | 4.4248e-06 | -4.7673e-06 | 0.01763 | 0.017627 | 0.01763 | 0.97625 | -0.46241 | 0.97666 | -0.45433 | 1.2108
134 | -0.012392 | -0.0030755 | 0.012393 | 0.0030752 | 3.0164e-07 | -2.5928e-07 | 0.01887 | 0.01887 | 0.01887 | 0.97666 | -0.45433 | 0.97669 | -0.45381 | 1.296

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.15007 | 0.037563

## res_load
| p_mw | q_mvar
0 | 0.0022452 | 0.00056269
1 | 0.0015462 | 0.00038752
2 | 0.0014847 | 0.0003721
3 | 0.00026289 | 6.5886e-05
4 | 0.00046292 | 0.00011602
5 | 0.00068502 | 0.00017168
6 | 0.0015412 | 0.00038627
7 | 0.0018962 | 0.00047522
8 | 0.0010932 | 0.00027397
9 | 0.0022796 | 0.00057133
10 | 0.00035252 | 8.8349e-05
11 | 0.0020657 | 0.00051771
12 | 0.0012185 | 0.0003054
13 | 0.00036013 | 9.0257e-05
14 | 0.0039519 | 0.00099043
15 | 0.00030728 | 7.7012e-05
16 | 0.00016183 | 4.0558e-05
17 | 0.00013756 | 3.4475e-05
18 | 0.00029832 | 7.4766e-05
19 | 0.00020169 | 5.0548e-05
20 | 0.0001965 | 4.9248e-05
21 | 0.00030627 | 7.6759e-05
22 | 0.0010814 | 0.00027102
23 | 0.0001698 | 4.2555e-05
24 | 0.0007113 | 0.00017827
25 | 0.00094415 | 0.00023663
26 | 0.00033358 | 8.3602e-05
27 | 0.00077725 | 0.0001948
28 | 0.00082626 | 0.00020708
29 | 0.005019 | 0.0012579
30 | 0.00087686 | 0.00021976
31 | 0.0014374 | 0.00036026
32 | 0.0010013 | 0.00025095
33 | 0.0010506 | 0.0002633
34 | 0.00077986 | 0.00019545
35 | 0.000553 | 0.0001386
36 | 0.00065426 | 0.00016397
37 | 0.00092204 | 0.00023109
38 | 0.00028349 | 7.1049e-05
39 | 0.00097296 | 0.00024385
40 | 0.0014999 | 0.00037591
41 | 0.00039615 | 9.9285e-05
42 | 0.00070581 | 0.00017689
43 | 0.00012084 | 3.0285e-05
44 | 0.00030294 | 7.5923e-05
45 | 0.00034465 | 8.6377e-05
46 | 0.00031081 | 7.7897e-05
47 | 0.00080798 | 0.0002025
48 | 0.00050125 | 0.00012563
49 | 0.00041238 | 0.00010335
50 | 0.00044649 | 0.0001119
51 | 0.00026569 | 6.6589e-05
52 | 0.00048141 | 0.00012065
53 | 0.00086397 | 0.00021653
54 | 0.0015076 | 0.00037784
55 | 0.00042455 | 0.0001064
56 | 0.0030636 | 0.00076782
57 | 0.00045133 | 0.00011311
58 | 0.00034049 | 8.5336e-05
59 | 0.0002834 | 7.1026e-05
60 | 0.0017501 | 0.00043861
61 | 0.00039178 | 9.819e-05
62 | 0.00034816 | 8.7258e-05
63 | 0.00035208 | 8.8239e-05
64 | 0.00097804 | 0.00024512
65 | 0.0018211 | 0.00045641
66 | 0.00085427 | 0.0002141
67 | 0.0010229 | 0.00025636
68 | 0.0012743 | 0.00031938
69 | 0.0013942 | 0.00034941
70 | 0.0020587 | 0.00051595
71 | 0.0012642 | 0.00031684
72 | 0.0020337 | 0.00050969
73 | 0.001323 | 0.00033158
74 | 0.0016585 | 0.00041565
75 | 0.0015684 | 0.00039307
76 | 0.0015206 | 0.00038109
77 | 0.00086965 | 0.00021795
78 | 0.0013029 | 0.00032653
79 | 0.0016152 | 0.00040481
80 | 0.0012048 | 0.00030196
81 | 0.00078369 | 0.00019641
82 | 0.0011798 | 0.00029569
83 | 0.0031489 | 0.00078918
84 | 0.001884 | 0.00047216
85 | 0.0010683 | 0.00026774
86 | 0.0033787 | 0.00084679
87 | 0.00066201 | 0.00016592
88 | 0.0012989 | 0.00032553
89 | 0.0039742 | 0.00099602
90 | 0.0022771 | 0.00057071
91 | 0.0034382 | 0.0008617
92 | 0.0035235 | 0.00088306
93 | 0.0029997 | 0.00075179
94 | 0.0016636 | 0.00041693
95 | 0.001702 | 0.00042656
96 | 0.0013023 | 0.0003264
97 | 0.0016906 | 0.0004237
98 | 0.0012302 | 0.00030832
99 | 0.003832 | 0.00096038
100 | 0.0032146 | 0.00080565
101 | 0.0016545 | 0.00041466
102 | 0.0015793 | 0.0003958
103 | 0.001083 | 0.00027142
104 | 0.0011604 | 0.00029083
105 | 0.004024 | 0.0010085
106 | 0.004305 | 0.0010789
107 | 0.00081564 | 0.00020442
108 | 0.0032269 | 0.00080873
109 | 0.003196 | 0.000801

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1