## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1709-17_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1709-17_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1709-17_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1709-17_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1709-17_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1709-17_0_5_node_29 | 0.4 | n |  | TRUE
6 | bus_LV_1709-17_0_5_node_10 | 0.4 | n |  | TRUE
7 | bus_LV_1709-17_0_5_node_19 | 0.4 | n |  | TRUE
8 | bus_LV_1709-17_0_5_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_1709-17_0_5_node_25 | 0.4 | n |  | TRUE
10 | bus_LV_1709-17_0_5_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_1709-17_0_5_node_21 | 0.4 | n |  | TRUE
12 | bus_LV_1709-17_0_5_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_1709-17_0_5_node_5 | 0.4 | n |  | TRUE
14 | bus_LV_1709-17_0_5_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1709-17_0_5_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_1709-17_0_5_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_1709-17_0_5_node_20 | 0.4 | n |  | TRUE
18 | bus_LV_1709-17_0_5_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1709-17_0_5_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_1709-17_0_5_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_1709-17_0_5_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_1709-17_0_5_node_9 | 0.4 | n |  | TRUE
23 | bus_LV_1709-17_0_5_node_32 | 0.4 | n |  | TRUE
24 | bus_LV_1709-17_0_5_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_1709-17_0_5_node_27 | 0.4 | n |  | TRUE
26 | bus_LV_1709-17_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_1709-17_0_5_node_26 | 0.4 | n |  | TRUE
28 | bus_LV_1709-17_0_5_node_31 | 0.4 | n |  | TRUE
29 | bus_LV_1709-17_0_5_node_34 | 0.4 | n |  | TRUE
30 | bus_LV_1709-17_0_5_node_12 | 0.4 | n |  | TRUE
31 | bus_LV_1709-17_0_5_node_14 | 0.4 | n |  | TRUE
32 | bus_LV_1709-17_0_5_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_1709-17_0_5_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_1709-17_0_5_node_18 | 0.4 | n |  | TRUE
35 | bus_LV_1709-17_0_5_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_1709-17_0_5_node_37 | 0.4 | n |  | TRUE
37 | bus_MV_25_0_node_53 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1709-17_0_5_load_0 | 0 | 0.028104 | 0.0070435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1709-17_0_5_load_1 | 1 | 0.0046197 | 0.0011578 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1709-17_0_5_load_3 | 3 | 0.0091462 | 0.0022923 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1709-17_0_5_load_29 | 5 | 0.051151 | 0.01282 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1709-17_0_5_load_28 | 8 | 0.0090824 | 0.0022763 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1709-17_0_5_load_25 | 9 | 0.018655 | 0.0046755 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1709-17_0_5_load_35 | 10 | 0.0060207 | 0.0015089 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1709-17_0_5_load_21 | 11 | 0.0065518 | 0.001642 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1709-17_0_5_load_17 | 12 | 0.011128 | 0.002789 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1709-17_0_5_load_5 | 13 | 0.00094178 | 0.00023603 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1709-17_0_5_load_6 | 14 | 0.0022686 | 0.00056858 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1709-17_0_5_load_15 | 15 | 0.024581 | 0.0061606 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1709-17_0_5_load_13 | 16 | 0.092968 | 0.0233 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1709-17_0_5_load_20 | 17 | 0.0404 | 0.010125 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1709-17_0_5_load_22 | 18 | 0.045186 | 0.011325 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1709-17_0_5_load_7 | 19 | 0.0014606 | 0.00036607 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1709-17_0_5_load_32 | 23 | 0.0077907 | 0.0019525 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1709-17_0_5_load_30 | 24 | 0.001733 | 0.00043434 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1709-17_0_5_load_24 | 26 | 0.0037325 | 0.00093544 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1709-17_0_5_load_26 | 27 | 0.096563 | 0.024201 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1709-17_0_5_load_34 | 29 | 0.0075949 | 0.0019035 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1709-17_0_5_load_12 | 30 | 0.05738 | 0.014381 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1709-17_0_5_load_16 | 32 | 0.0058076 | 0.0014555 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1709-17_0_5_load_23 | 33 | 0.031695 | 0.0079435 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1709-17_0_5_load_18 | 34 | 0.0066866 | 0.0016758 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1709-17_0_5_load_37 | 36 | 0.00049031 | 0.00012288 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1709-17_0_5_line_0 |  | 0 | 1 | 0.047938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_1709-17_0_5_line_1 |  | 0 | 2 | 0.03205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_1709-17_0_5_line_2 |  | 1 | 3 | 0.034638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_1709-17_0_5_line_3 |  | 2 | 4 | 0.056376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_1709-17_0_5_line_4 |  | 3 | 5 | 0.010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
5 | LV_1709-17_0_5_line_5 |  | 4 | 6 | 0.099853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_1709-17_0_5_line_6 |  | 4 | 7 | 0.053139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
7 | LV_1709-17_0_5_line_7 |  | 4 | 8 | 0.028462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1709-17_0_5_line_8 |  | 5 | 9 | 0.075183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
9 | LV_1709-17_0_5_line_9 |  | 6 | 10 | 0.034996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_1709-17_0_5_line_10 |  | 7 | 11 | 0.02068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1709-17_0_5_line_11 |  | 7 | 12 | 0.0090441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_1709-17_0_5_line_12 |  | 9 | 15 | 0.091576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_1709-17_0_5_line_13 |  | 10 | 29 | 0.03959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1709-17_0_5_line_14 |  | 12 | 34 | 0.024055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1709-17_0_5_line_15 |  | 13 | 14 | 0.014011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1709-17_0_5_line_16 |  | 14 | 15 | 0.15593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1709-17_0_5_line_17 |  | 15 | 16 | 0.03758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_1709-17_0_5_line_18 |  | 16 | 30 | 0.040433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_1709-17_0_5_line_19 |  | 17 | 18 | 0.05605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_1709-17_0_5_line_20 |  | 18 | 33 | 0.014307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
21 | LV_1709-17_0_5_line_21 |  | 19 | 20 | 0.072397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1709-17_0_5_line_22 |  | 20 | 21 | 0.1175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1709-17_0_5_line_23 |  | 21 | 25 | 0.070453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1709-17_0_5_line_24 |  | 21 | 22 | 0.056562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1709-17_0_5_line_25 |  | 22 | 23 | 0.060387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1709-17_0_5_line_26 |  | 22 | 24 | 0.071869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1709-17_0_5_line_27 |  | 24 | 28 | 0.019121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1709-17_0_5_line_28 |  | 25 | 26 | 0.008859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1709-17_0_5_line_29 |  | 25 | 27 | 0.053758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1709-17_0_5_line_30 |  | 26 | 33 | 0.087768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1709-17_0_5_line_31 |  | 28 | 35 | 0.10014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1709-17_0_5_line_32 |  | 30 | 31 | 0.053418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_1709-17_0_5_line_33 |  | 31 | 32 | 0.064655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_1709-17_0_5_line_34 |  | 32 | 33 | 0.075328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_1709-17_0_5_line_35 |  | 35 | 36 | 0.059615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1709-17_0_5_trafo_20 | 0.63 MVA 20/0.4 kV | 37 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2686195.3887 | 1221087.0948 | 2686200.4243 | 1221052.4174 | 2686200.7132 | 1221039.524
1 | 2686190.783 | 1221118.8118 | 2686195.3887 | 1221087.0948
2 | 2686200.7132 | 1221039.524 | 2686201.0464 | 1221024.652 | 2686196.4477 | 1221005.4326
3 | 2686190.783 | 1221118.8118 | 2686135.5801 | 1221106.6161
4 | 2686194.0279 | 1220995.3194 | 2686196.4477 | 1221005.4326
5 | 2686092.878 | 1221196.9156 | 2686094.1146 | 1221194.2984 | 2686096.9007 | 1221188.4125 | 2686135.5801 | 1221106.6161
6 | 2686135.5801 | 1221106.6161 | 2686134.4975 | 1221053.4978
7 | 2686135.5801 | 1221106.6161 | 2686107.7227 | 1221100.7833
8 | 2686194.0279 | 1220995.3194 | 2686205.4707 | 1220921.0124
9 | 2686092.878 | 1221196.9156 | 2686099.3962 | 1221200.5234 | 2686107.3839 | 1221208.4998 | 2686118.5247 | 1221220.3398
10 | 2686134.4975 | 1221053.4978 | 2686114.1937 | 1221049.5687
11 | 2686134.4975 | 1221053.4978 | 2686134.3096 | 1221044.4556
12 | 2686205.4707 | 1220921.0124 | 2686128.0596 | 1220872.0869
13 | 2686150.9587 | 1221242.9879 | 2686141.8519 | 1221237.3623 | 2686118.8389 | 1221220.6737 | 2686118.5247 | 1221220.3398
14 | 2686134.3096 | 1221044.4556 | 2686126.338 | 1221021.76
15 | 2686234.8265 | 1220747.9335 | 2686238.0546 | 1220761.5681
16 | 2686128.0596 | 1220872.0869 | 2686238.0546 | 1220761.5681
17 | 2686096.1849 | 1220852.1827 | 2686105.6718 | 1220857.9373 | 2686128.0596 | 1220872.0869
18 | 2686096.1849 | 1220852.1827 | 2686061.6142 | 1220831.213
19 | 2686085.051 | 1220939.6178 | 2686080.735 | 1220933.7727 | 2686064.8636 | 1220918.4441 | 2686048.4787 | 1220912.3811 | 2686039.2328 | 1220912.1585
20 | 2686027.3271 | 1220920.0919 | 2686027.3271 | 1220920.0919 | 2686039.2328 | 1220912.1585 | 2686039.2328 | 1220912.1585
21 | 2685948.4888 | 1221182.0759 | 2685961.2343 | 1221187.3968 | 2686018.1857 | 1221201.1353
22 | 2685948.4888 | 1221182.0759 | 2685963.3186 | 1221154.9716 | 2685976.1378 | 1221131.5518 | 2685978.054 | 1221126.5316 | 2685978.0025 | 1221124.3182 | 2685980.6534 | 1221121.4879 | 2685990.8842 | 1221103.4122 | 2686004.0431 | 1221079.0746
23 | 2686004.0431 | 1221079.0746 | 2685997.8176 | 1221077.7727 | 2686008.1852 | 1221014.524
24 | 2685949.0806 | 1221065.9502 | 2685967.8024 | 1221069.356 | 2685997.8176 | 1221077.7727 | 2686004.0431 | 1221079.0746
25 | 2685949.0806 | 1221065.9502 | 2685944.0914 | 1221057.8393 | 2685937.7289 | 1221047.6295 | 2685934.3333 | 1221038.4521 | 2685932.5061 | 1221027.3182 | 2685930.7918 | 1221009.6349
26 | 2685949.0806 | 1221065.9502 | 2685943.7001 | 1221064.9719 | 2685890.7278 | 1221067.4428 | 2685877.4098 | 1221068.6279
27 | 2685858.3643 | 1221070.3226 | 2685877.4098 | 1221068.6279
28 | 2686008.1852 | 1221014.524 | 2686009.6184 | 1221005.7817
29 | 2686008.1852 | 1221014.524 | 2686060.6575 | 1221026.2105
30 | 2686009.6184 | 1221005.7817 | 2686014.1845 | 1220977.9302 | 2686021.3334 | 1220935.816 | 2686027.3271 | 1220920.0919
31 | 2685761.1745 | 1221092.7266 | 2685812.5263 | 1221075.2766 | 2685845.4468 | 1221070.5922 | 2685858.3643 | 1221070.3226
32 | 2686015.9384 | 1220803.5151 | 2686043.8365 | 1220820.4294 | 2686061.6142 | 1220831.213
33 | 2686015.9384 | 1220803.5151 | 2686014.9624 | 1220804.8908 | 2686005.4893 | 1220818.8079 | 2685989.0708 | 1220842.3646 | 2685985.6458 | 1220848.3526 | 2685983.6536 | 1220857.5745 | 2685983.7358 | 1220858.658
34 | 2686027.3271 | 1220920.0919 | 2685983.7358 | 1220858.658
35 | 2685761.1745 | 1221092.7266 | 2685759.6827 | 1221080.4079 | 2685752.3423 | 1221033.7817

## bus_geodata
| x | y | coords
0 | 2686195.3887 | 1221087.0948
1 | 2686200.7132 | 1221039.524
2 | 2686190.783 | 1221118.8118
3 | 2686196.4477 | 1221005.4326
4 | 2686135.5801 | 1221106.6161
5 | 2686194.0279 | 1220995.3194
6 | 2686092.878 | 1221196.9156
7 | 2686134.4975 | 1221053.4978
8 | 2686107.7227 | 1221100.7833
9 | 2686205.4707 | 1220921.0124
10 | 2686118.5247 | 1221220.3398
11 | 2686114.1937 | 1221049.5687
12 | 2686134.3096 | 1221044.4556
13 | 2686234.8265 | 1220747.9335
14 | 2686238.0546 | 1220761.5681
15 | 2686128.0596 | 1220872.0869
16 | 2686096.1849 | 1220852.1827
17 | 2686085.051 | 1220939.6178
18 | 2686039.2328 | 1220912.1585
19 | 2686018.1857 | 1221201.1353
20 | 2685948.4888 | 1221182.0759
21 | 2686004.0431 | 1221079.0746
22 | 2685949.0806 | 1221065.9502
23 | 2685930.7918 | 1221009.6349
24 | 2685877.4098 | 1221068.6279
25 | 2686008.1852 | 1221014.524
26 | 2686009.6184 | 1221005.7817
27 | 2686060.6575 | 1221026.2105
28 | 2685858.3643 | 1221070.3226
29 | 2686150.9587 | 1221242.9879
30 | 2686061.6142 | 1220831.213
31 | 2686015.9384 | 1220803.5151
32 | 2685983.7358 | 1220858.658
33 | 2686027.3271 | 1220920.0919
34 | 2686126.338 | 1221021.76
35 | 2685761.1745 | 1221092.7266
36 | 2685752.3422 | 1221033.7817
37 | 2686104.5627 | 1220966.042

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97154 | -0.54918 | 0.028104 | 0.0070435
1 | 0.97221 | -0.53587 | 0.0046197 | 0.0011578
2 | 0.97125 | -0.55476 | 0 | 0
3 | 0.97272 | -0.52567 | 0.0091462 | 0.0022923
4 | 0.97076 | -0.56457 | 0 | 0
5 | 0.9729 | -0.52226 | 0.051151 | 0.01282
6 | 0.9705 | -0.56961 | 0 | 0
7 | 0.97052 | -0.56937 | 0 | 0
8 | 0.97052 | -0.56936 | 0.0090824 | 0.0022763
9 | 0.97486 | -0.48354 | 0.018655 | 0.0046755
10 | 0.97041 | -0.57138 | 0.0060207 | 0.0015089
11 | 0.97039 | -0.57187 | 0.0065518 | 0.001642
12 | 0.97049 | -0.56996 | 0.011128 | 0.002789
13 | 0.9771 | -0.43972 | 0.00094178 | 0.00023603
14 | 0.97711 | -0.43948 | 0.0022686 | 0.00056858
15 | 0.97757 | -0.43033 | 0.024581 | 0.0061606
16 | 0.97888 | -0.40478 | 0.092968 | 0.0233
17 | 1 | 0 | -0.54328 | -0.13968
18 | 0.99448 | -0.10443 | 0.045186 | 0.011325
19 | 0.9822 | -0.34083 | 0.0014606 | 0.00036607
20 | 0.9823 | -0.33892 | 0 | 0
21 | 0.98246 | -0.33581 | 0 | 0
22 | 0.98193 | -0.34606 | 0 | 0
23 | 0.9815 | -0.35457 | 0.0077907 | 0.0019525
24 | 0.98179 | -0.34895 | 0.001733 | 0.00043434
25 | 0.9832 | -0.3212 | 0 | 0
26 | 0.98409 | -0.30396 | 0.0037325 | 0.00093544
27 | 0.97839 | -0.41526 | 0.096563 | 0.024201
28 | 0.98178 | -0.34913 | 0 | 0
29 | 0.97034 | -0.57277 | 0.0075949 | 0.0019035
30 | 0.98098 | -0.36374 | 0.05738 | 0.014381
31 | 0.98433 | -0.29876 | 0 | 0
32 | 0.98838 | -0.22069 | 0.0058076 | 0.0014555
33 | 0.99318 | -0.12898 | 0.031695 | 0.0079435
34 | 0.97034 | -0.57294 | 0.0066866 | 0.0016758
35 | 0.98173 | -0.35002 | 0 | 0
36 | 0.9817 | -0.35055 | 0.00049031 | 0.00012288
37 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.075218 | -0.01885 | 0.075266 | 0.018878 | 4.7717e-05 | 2.7569e-05 | 0.1152 | 0.1152 | 0.1152 | 0.97154 | -0.54918 | 0.97221 | -0.53587 | 6.3299
1 | 0.047114 | 0.011807 | -0.047101 | -0.011801 | 1.2516e-05 | 6.0267e-06 | 0.07216 | 0.072161 | 0.072161 | 0.97154 | -0.54918 | 0.97125 | -0.55476 | 3.9649
2 | -0.079885 | -0.020035 | 0.079924 | 0.020058 | 3.8839e-05 | 2.2709e-05 | 0.12227 | 0.12227 | 0.12227 | 0.97221 | -0.53587 | 0.97272 | -0.52567 | 6.7183
3 | 0.047101 | 0.011801 | -0.047079 | -0.01179 | 2.2017e-05 | 1.0604e-05 | 0.072161 | 0.072162 | 0.072162 | 0.97125 | -0.55476 | 0.97076 | -0.56457 | 3.9649
4 | -0.08907 | -0.02235 | 0.089085 | 0.022359 | 1.4481e-05 | 8.6224e-06 | 0.13626 | 0.13626 | 0.13626 | 0.97272 | -0.52567 | 0.9729 | -0.52226 | 7.4871
5 | 0.01362 | 0.0034052 | -0.013617 | -0.0034093 | 3.2638e-06 | -4.0821e-06 | 0.020875 | 0.020877 | 0.020877 | 0.97076 | -0.56457 | 0.9705 | -0.56961 | 1.1471
6 | 0.024374 | 0.0061074 | -0.024369 | -0.0061072 | 5.5634e-06 | 2.7653e-07 | 0.037362 | 0.037363 | 0.037363 | 0.97076 | -0.56457 | 0.97052 | -0.56937 | 2.0529
7 | 0.0090845 | 0.0022772 | -0.0090824 | -0.0022763 | 2.0697e-06 | 9.7279e-07 | 0.013925 | 0.013925 | 0.013925 | 0.97076 | -0.56457 | 0.97052 | -0.56936 | 3.8257
8 | -0.14024 | -0.035179 | 0.14049 | 0.03534 | 0.00025943 | 0.00016136 | 0.2145 | 0.2145 | 0.2145 | 0.9729 | -0.52226 | 0.97486 | -0.48354 | 11.7856
9 | 0.013617 | 0.0034093 | -0.013616 | -0.0034107 | 1.144e-06 | -1.4298e-06 | 0.020877 | 0.020878 | 0.020878 | 0.9705 | -0.56961 | 0.97041 | -0.57138 | 1.1471
10 | 0.0065526 | 0.0016423 | -0.0065518 | -0.001642 | 7.8277e-07 | 2.4546e-07 | 0.010047 | 0.010047 | 0.010047 | 0.97052 | -0.56937 | 0.97039 | -0.57187 | 2.7601
11 | 0.017816 | 0.0044649 | -0.017816 | -0.0044651 | 5.0614e-07 | -2.3485e-07 | 0.027316 | 0.027316 | 0.027316 | 0.97052 | -0.56937 | 0.97049 | -0.56996 | 1.5009
12 | -0.15915 | -0.040015 | 0.15956 | 0.040269 | 0.00040546 | 0.00025377 | 0.24297 | 0.24297 | 0.24297 | 0.97486 | -0.48354 | 0.97757 | -0.43033 | 13.3501
13 | 0.0075954 | 0.0019018 | -0.0075949 | -0.0019035 | 5.0343e-07 | -1.6341e-06 | 0.011646 | 0.011647 | 0.011647 | 0.97041 | -0.57138 | 0.97034 | -0.57277 | 0.79991
14 | 0.0066876 | 0.0016761 | -0.0066866 | -0.0016758 | 9.4845e-07 | 3.0983e-07 | 0.010254 | 0.010254 | 0.010254 | 0.97049 | -0.56996 | 0.97034 | -0.57294 | 2.817
15 | -0.00094178 | -0.00023603 | 0.00094179 | 0.00023586 | 1.0808e-08 | -1.6858e-07 | 0.0014342 | 0.0014342 | 0.0014342 | 0.9771 | -0.43972 | 0.97711 | -0.43948 | 0.39402
16 | -0.0032104 | -0.00080444 | 0.0032118 | 0.00080338 | 1.3975e-06 | -1.0596e-06 | 0.004889 | 0.0048883 | 0.004889 | 0.97711 | -0.43948 | 0.97757 | -0.43033 | 1.3431
17 | -0.18735 | -0.047233 | 0.18758 | 0.047378 | 0.00022937 | 0.00014444 | 0.28527 | 0.28527 | 0.28527 | 0.97757 | -0.43033 | 0.97888 | -0.40478 | 15.6744
18 | -0.28055 | -0.070678 | 0.2811 | 0.071028 | 0.00055186 | 0.00035065 | 0.4266 | 0.42659 | 0.4266 | 0.97888 | -0.40478 | 0.98098 | -0.36374 | 23.4393
19 | 0.54163 | 0.13968 | -0.53889 | -0.13793 | 0.0027401 | 0.00175 | 0.80736 | 0.80736 | 0.80736 | 1 | 0 | 0.99448 | -0.10443 | 44.3604
20 | 0.49371 | 0.12661 | -0.49312 | -0.12623 | 0.00058718 | 0.00037487 | 0.73975 | 0.73975 | 0.73975 | 0.99448 | -0.10443 | 0.99318 | -0.12898 | 40.6456
21 | -0.0014606 | -0.00036607 | 0.0014608 | 0.00036524 | 1.3292e-07 | -8.313e-07 | 0.0022129 | 0.0022125 | 0.0022129 | 0.9822 | -0.34083 | 0.9823 | -0.33892 | 0.60793
22 | -0.0014608 | -0.00036524 | 0.001461 | 0.00036389 | 2.1564e-07 | -1.3496e-06 | 0.0022125 | 0.002212 | 0.0022125 | 0.9823 | -0.33892 | 0.98246 | -0.33581 | 0.60784
23 | -0.011483 | -0.0028744 | 0.011491 | 0.0028786 | 7.9908e-06 | 4.2213e-06 | 0.017391 | 0.017391 | 0.017391 | 0.98246 | -0.33581 | 0.9832 | -0.3212 | 4.7778
24 | 0.010022 | 0.0025105 | -0.010018 | -0.0025081 | 4.8873e-06 | 2.412e-06 | 0.015179 | 0.01518 | 0.01518 | 0.98246 | -0.33581 | 0.98193 | -0.34606 | 4.1702
25 | 0.0077939 | 0.0019538 | -0.0077907 | -0.0019525 | 3.159e-06 | 1.2583e-06 | 0.011811 | 0.011811 | 0.011811 | 0.98193 | -0.34606 | 0.9815 | -0.35457 | 3.2448
26 | 0.0022237 | 0.00055427 | -0.0022234 | -0.00055498 | 3.0587e-07 | -7.1322e-07 | 0.0033687 | 0.003369 | 0.003369 | 0.98193 | -0.34606 | 0.98179 | -0.34895 | 0.92555
27 | 0.00049034 | 0.00012064 | -0.00049034 | -0.00012088 | 3.9522e-09 | -2.3926e-07 | 0.00074238 | 0.00074246 | 0.00074246 | 0.98179 | -0.34895 | 0.98178 | -0.34913 | 0.20397
28 | -0.10849 | -0.027357 | 0.10858 | 0.027414 | 8.9626e-05 | 5.7248e-05 | 0.16425 | 0.16425 | 0.16425 | 0.9832 | -0.3212 | 0.98409 | -0.30396 | 45.124
29 | 0.096998 | 0.024479 | -0.096563 | -0.024201 | 0.00043479 | 0.00027759 | 0.14686 | 0.14686 | 0.14686 | 0.9832 | -0.3212 | 0.97839 | -0.41526 | 40.3463
30 | -0.11231 | -0.02835 | 0.11326 | 0.028957 | 0.00095001 | 0.00060688 | 0.1699 | 0.16989 | 0.1699 | 0.98409 | -0.30396 | 0.99318 | -0.12898 | 46.6745
31 | 0.00049034 | 0.00012088 | -0.00049032 | -0.00012214 | 2.0712e-08 | -1.253e-06 | 0.00074246 | 0.00074291 | 0.00074291 | 0.98178 | -0.34913 | 0.98173 | -0.35002 | 0.2041
32 | -0.33848 | -0.085409 | 0.33953 | 0.086082 | 0.0010569 | 0.00067305 | 0.51363 | 0.51363 | 0.51363 | 0.98098 | -0.36374 | 0.98433 | -0.29876 | 28.2215
33 | -0.33953 | -0.086082 | 0.34081 | 0.086897 | 0.0012793 | 0.00081461 | 0.51363 | 0.51363 | 0.51363 | 0.98433 | -0.29876 | 0.98838 | -0.22069 | 28.2214
34 | -0.34662 | -0.088352 | 0.34816 | 0.089334 | 0.0015416 | 0.00098178 | 0.52237 | 0.52237 | 0.52237 | 0.98838 | -0.22069 | 0.99318 | -0.12898 | 28.7017
35 | 0.00049032 | 0.00012214 | -0.00049031 | -0.00012288 | 1.2343e-08 | -7.4587e-07 | 0.00074291 | 0.00074318 | 0.00074318 | 0.98173 | -0.35002 | 0.9817 | -0.35055 | 0.20417

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.58368 | 0.14981

## res_load
| p_mw | q_mvar
0 | 0.028104 | 0.0070435
1 | 0.0046197 | 0.0011578
2 | 0.0091462 | 0.0022923
3 | 0.051151 | 0.01282
4 | 0.0090824 | 0.0022763
5 | 0.018655 | 0.0046755
6 | 0.0060207 | 0.0015089
7 | 0.0065518 | 0.001642
8 | 0.011128 | 0.002789
9 | 0.00094178 | 0.00023603
10 | 0.0022686 | 0.00056858
11 | 0.024581 | 0.0061606
12 | 0.092968 | 0.0233
13 | 0.0404 | 0.010125
14 | 0.045186 | 0.011325
15 | 0.0014606 | 0.00036607
16 | 0.0077907 | 0.0019525
17 | 0.001733 | 0.00043434
18 | 0.0037325 | 0.00093544
19 | 0.096563 | 0.024201
20 | 0.0075949 | 0.0019035
21 | 0.05738 | 0.014381
22 | 0.0058076 | 0.0014555
23 | 0.031695 | 0.0079435
24 | 0.0066866 | 0.0016758
25 | 0.00049031 | 0.00012288

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1