## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1709-1_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1709-1_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1709-1_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1709-1_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1709-1_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1709-1_0_8_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1709-1_0_8_node_29 | 0.4 | n |  | TRUE
7 | bus_LV_1709-1_0_8_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_1709-1_0_8_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_1709-1_0_8_node_44 | 0.4 | n |  | TRUE
10 | bus_LV_1709-1_0_8_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_1709-1_0_8_node_34 | 0.4 | n |  | TRUE
12 | bus_LV_1709-1_0_8_node_30 | 0.4 | n |  | TRUE
13 | bus_LV_1709-1_0_8_node_43 | 0.4 | n |  | TRUE
14 | bus_LV_1709-1_0_8_node_6 | 0.4 | n |  | TRUE
15 | bus_LV_1709-1_0_8_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_1709-1_0_8_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_1709-1_0_8_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1709-1_0_8_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_1709-1_0_8_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1709-1_0_8_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_1709-1_0_8_node_53 | 0.4 | n |  | TRUE
22 | bus_LV_1709-1_0_8_node_126 | 0.4 | n |  | TRUE
23 | bus_LV_1709-1_0_8_node_55 | 0.4 | n |  | TRUE
24 | bus_LV_1709-1_0_8_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_1709-1_0_8_node_54 | 0.4 | n |  | TRUE
26 | bus_LV_1709-1_0_8_node_127 | 0.4 | n |  | TRUE
27 | bus_LV_1709-1_0_8_node_128 | 0.4 | n |  | TRUE
28 | bus_LV_1709-1_0_8_node_12 | 0.4 | n |  | TRUE
29 | bus_LV_1709-1_0_8_node_13 | 0.4 | n |  | TRUE
30 | bus_LV_1709-1_0_8_node_14 | 0.4 | n |  | TRUE
31 | bus_LV_1709-1_0_8_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_1709-1_0_8_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_1709-1_0_8_node_155 | 0.4 | n |  | TRUE
34 | bus_LV_1709-1_0_8_node_156 | 0.4 | n |  | TRUE
35 | bus_LV_1709-1_0_8_node_157 | 0.4 | n |  | TRUE
36 | bus_LV_1709-1_0_8_node_159 | 0.4 | n |  | TRUE
37 | bus_LV_1709-1_0_8_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1709-1_0_8_node_160 | 0.4 | n |  | TRUE
39 | bus_LV_1709-1_0_8_node_31 | 0.4 | n |  | TRUE
40 | bus_LV_1709-1_0_8_node_45 | 0.4 | n |  | TRUE
41 | bus_LV_1709-1_0_8_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_1709-1_0_8_node_19 | 0.4 | n |  | TRUE
43 | bus_LV_1709-1_0_8_node_20 | 0.4 | n |  | TRUE
44 | bus_LV_1709-1_0_8_node_21 | 0.4 | n |  | TRUE
45 | bus_LV_1709-1_0_8_node_22 | 0.4 | n |  | TRUE
46 | bus_LV_1709-1_0_8_node_23 | 0.4 | n |  | TRUE
47 | bus_LV_1709-1_0_8_node_24 | 0.4 | n |  | TRUE
48 | bus_LV_1709-1_0_8_node_25 | 0.4 | n |  | TRUE
49 | bus_LV_1709-1_0_8_node_56 | 0.4 | n |  | TRUE
50 | bus_LV_1709-1_0_8_node_41 | 0.4 | n |  | TRUE
51 | bus_LV_1709-1_0_8_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_1709-1_0_8_node_42 | 0.4 | n |  | TRUE
53 | bus_LV_1709-1_0_8_node_39 | 0.4 | n |  | TRUE
54 | bus_LV_1709-1_0_8_node_28 | 0.4 | n |  | TRUE
55 | bus_LV_1709-1_0_8_node_35 | 0.4 | n |  | TRUE
56 | bus_LV_1709-1_0_8_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_1709-1_0_8_node_36 | 0.4 | n |  | TRUE
58 | bus_LV_1709-1_0_8_node_37 | 0.4 | n |  | TRUE
59 | bus_LV_1709-1_0_8_node_38 | 0.4 | n |  | TRUE
60 | bus_LV_1709-1_0_8_node_40 | 0.4 | n |  | TRUE
61 | bus_LV_1709-1_0_8_node_146 | 0.4 | n |  | TRUE
62 | bus_LV_1709-1_0_8_node_83 | 0.4 | n |  | TRUE
63 | bus_LV_1709-1_0_8_node_84 | 0.4 | n |  | TRUE
64 | bus_LV_1709-1_0_8_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_1709-1_0_8_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_1709-1_0_8_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_1709-1_0_8_node_51 | 0.4 | n |  | TRUE
68 | bus_LV_1709-1_0_8_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_1709-1_0_8_node_77 | 0.4 | n |  | TRUE
70 | bus_LV_1709-1_0_8_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_1709-1_0_8_node_78 | 0.4 | n |  | TRUE
72 | bus_LV_1709-1_0_8_node_104 | 0.4 | n |  | TRUE
73 | bus_LV_1709-1_0_8_node_105 | 0.4 | n |  | TRUE
74 | bus_LV_1709-1_0_8_node_118 | 0.4 | n |  | TRUE
75 | bus_LV_1709-1_0_8_node_106 | 0.4 | n |  | TRUE
76 | bus_LV_1709-1_0_8_node_130 | 0.4 | n |  | TRUE
77 | bus_LV_1709-1_0_8_node_140 | 0.4 | n |  | TRUE
78 | bus_LV_1709-1_0_8_node_158 | 0.4 | n |  | TRUE
79 | bus_LV_1709-1_0_8_node_138 | 0.4 | n |  | TRUE
80 | bus_LV_1709-1_0_8_node_139 | 0.4 | n |  | TRUE
81 | bus_LV_1709-1_0_8_node_141 | 0.4 | n |  | TRUE
82 | bus_LV_1709-1_0_8_node_122 | 0.4 | n |  | TRUE
83 | bus_LV_1709-1_0_8_node_142 | 0.4 | n |  | TRUE
84 | bus_LV_1709-1_0_8_node_59 | 0.4 | n |  | TRUE
85 | bus_LV_1709-1_0_8_node_60 | 0.4 | n |  | TRUE
86 | bus_LV_1709-1_0_8_node_61 | 0.4 | n |  | TRUE
87 | bus_LV_1709-1_0_8_node_62 | 0.4 | n |  | TRUE
88 | bus_LV_1709-1_0_8_node_63 | 0.4 | n |  | TRUE
89 | bus_LV_1709-1_0_8_node_64 | 0.4 | n |  | TRUE
90 | bus_LV_1709-1_0_8_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_1709-1_0_8_node_76 | 0.4 | n |  | TRUE
92 | bus_LV_1709-1_0_8_node_107 | 0.4 | n |  | TRUE
93 | bus_LV_1709-1_0_8_node_85 | 0.4 | n |  | TRUE
94 | bus_LV_1709-1_0_8_node_70 | 0.4 | n |  | TRUE
95 | bus_LV_1709-1_0_8_node_75 | 0.4 | n |  | TRUE
96 | bus_LV_1709-1_0_8_node_100 | 0.4 | n |  | TRUE
97 | bus_LV_1709-1_0_8_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_1709-1_0_8_node_66 | 0.4 | n |  | TRUE
99 | bus_LV_1709-1_0_8_node_67 | 0.4 | n |  | TRUE
100 | bus_LV_1709-1_0_8_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_1709-1_0_8_node_69 | 0.4 | n |  | TRUE
102 | bus_LV_1709-1_0_8_node_68 | 0.4 | n |  | TRUE
103 | bus_LV_1709-1_0_8_node_71 | 0.4 | n |  | TRUE
104 | bus_LV_1709-1_0_8_node_119 | 0.4 | n |  | TRUE
105 | bus_LV_1709-1_0_8_node_121 | 0.4 | n |  | TRUE
106 | bus_LV_1709-1_0_8_node_143 | 0.4 | n |  | TRUE
107 | bus_LV_1709-1_0_8_node_72 | 0.4 | n |  | TRUE
108 | bus_LV_1709-1_0_8_node_91 | 0.4 | n |  | TRUE
109 | bus_LV_1709-1_0_8_node_73 | 0.4 | n |  | TRUE
110 | bus_LV_1709-1_0_8_node_89 | 0.4 | n |  | TRUE
111 | bus_LV_1709-1_0_8_node_79 | 0.4 | n |  | TRUE
112 | bus_LV_1709-1_0_8_node_80 | 0.4 | n |  | TRUE
113 | bus_LV_1709-1_0_8_node_81 | 0.4 | n |  | TRUE
114 | bus_LV_1709-1_0_8_node_101 | 0.4 | n |  | TRUE
115 | bus_LV_1709-1_0_8_node_103 | 0.4 | n |  | TRUE
116 | bus_LV_1709-1_0_8_node_124 | 0.4 | n |  | TRUE
117 | bus_LV_1709-1_0_8_node_129 | 0.4 | n |  | TRUE
118 | bus_LV_1709-1_0_8_node_145 | 0.4 | n |  | TRUE
119 | bus_LV_1709-1_0_8_node_144 | 0.4 | n |  | TRUE
120 | bus_LV_1709-1_0_8_node_87 | 0.4 | n |  | TRUE
121 | bus_LV_1709-1_0_8_node_88 | 0.4 | n |  | TRUE
122 | bus_LV_1709-1_0_8_node_90 | 0.4 | n |  | TRUE
123 | bus_LV_1709-1_0_8_node_92 | 0.4 | n |  | TRUE
124 | bus_LV_1709-1_0_8_node_93 | 0.4 | n |  | TRUE
125 | bus_LV_1709-1_0_8_node_94 | 0.4 | n |  | TRUE
126 | bus_LV_1709-1_0_8_node_95 | 0.4 | n |  | TRUE
127 | bus_LV_1709-1_0_8_node_96 | 0.4 | n |  | TRUE
128 | bus_LV_1709-1_0_8_node_98 | 0.4 | n |  | TRUE
129 | bus_LV_1709-1_0_8_node_99 | 0.4 | n |  | TRUE
130 | bus_LV_1709-1_0_8_node_132 | 0.4 | n |  | TRUE
131 | bus_LV_1709-1_0_8_node_97 | 0.4 | n |  | TRUE
132 | bus_LV_1709-1_0_8_node_125 | 0.4 | n |  | TRUE
133 | bus_LV_1709-1_0_8_node_116 | 0.4 | n |  | TRUE
134 | bus_LV_1709-1_0_8_node_102 | 0.4 | n |  | TRUE
135 | bus_LV_1709-1_0_8_node_131 | 0.4 | n |  | TRUE
136 | bus_LV_1709-1_0_8_node_109 | 0.4 | n |  | TRUE
137 | bus_LV_1709-1_0_8_node_108 | 0.4 | n |  | TRUE
138 | bus_LV_1709-1_0_8_node_110 | 0.4 | n |  | TRUE
139 | bus_LV_1709-1_0_8_node_111 | 0.4 | n |  | TRUE
140 | bus_LV_1709-1_0_8_node_112 | 0.4 | n |  | TRUE
141 | bus_LV_1709-1_0_8_node_113 | 0.4 | n |  | TRUE
142 | bus_LV_1709-1_0_8_node_115 | 0.4 | n |  | TRUE
143 | bus_LV_1709-1_0_8_node_114 | 0.4 | n |  | TRUE
144 | bus_LV_1709-1_0_8_node_117 | 0.4 | n |  | TRUE
145 | bus_LV_1709-1_0_8_node_133 | 0.4 | n |  | TRUE
146 | bus_LV_1709-1_0_8_node_151 | 0.4 | n |  | TRUE
147 | bus_LV_1709-1_0_8_node_134 | 0.4 | n |  | TRUE
148 | bus_LV_1709-1_0_8_node_150 | 0.4 | n |  | TRUE
149 | bus_LV_1709-1_0_8_node_135 | 0.4 | n |  | TRUE
150 | bus_LV_1709-1_0_8_node_136 | 0.4 | n |  | TRUE
151 | bus_LV_1709-1_0_8_node_147 | 0.4 | n |  | TRUE
152 | bus_LV_1709-1_0_8_node_137 | 0.4 | n |  | TRUE
153 | bus_LV_1709-1_0_8_node_162 | 0.4 | n |  | TRUE
154 | bus_LV_1709-1_0_8_node_161 | 0.4 | n |  | TRUE
155 | bus_LV_1709-1_0_8_node_148 | 0.4 | n |  | TRUE
156 | bus_LV_1709-1_0_8_node_149 | 0.4 | n |  | TRUE
157 | bus_MV_25_0_node_62 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1709-1_0_8_load_0 | 0 | 0.0014983 | 0.00037551 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1709-1_0_8_load_1 | 1 | 0.0019587 | 0.0004909 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1709-1_0_8_load_18 | 5 | 0.002787 | 0.00069848 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1709-1_0_8_load_29 | 6 | 0.003191 | 0.00079974 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1709-1_0_8_load_17 | 7 | 0.0026647 | 0.00066784 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1709-1_0_8_load_44 | 9 | 0.0032008 | 0.0008022 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1709-1_0_8_load_5 | 10 | 0.0013322 | 0.00033388 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1709-1_0_8_load_30 | 12 | 0.0027309 | 0.00068444 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1709-1_0_8_load_43 | 13 | 0.002796 | 0.00070074 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1709-1_0_8_load_6 | 14 | 0.0015783 | 0.00039556 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1709-1_0_8_load_7 | 15 | 0.00257 | 0.00064411 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1709-1_0_8_load_8 | 16 | 0.0026162 | 0.00065567 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1709-1_0_8_load_11 | 19 | 0.0020892 | 0.00052361 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1709-1_0_8_load_26 | 20 | 0.0024616 | 0.00061693 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1709-1_0_8_load_53 | 21 | 0.0015332 | 0.00038424 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1709-1_0_8_load_55 | 23 | 0.0030009 | 0.0007521 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1709-1_0_8_load_27 | 24 | 0.0022745 | 0.00057004 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1709-1_0_8_load_54 | 25 | 0.00076781 | 0.00019243 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1709-1_0_8_load_128 | 27 | 0.0029056 | 0.0007282 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1709-1_0_8_load_12 | 28 | 0.0055206 | 0.0013836 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1709-1_0_8_load_13 | 29 | 0.00282 | 0.00070675 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1709-1_0_8_load_14 | 30 | 0.0040403 | 0.0010126 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1709-1_0_8_load_15 | 31 | 0.0034058 | 0.00085359 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1709-1_0_8_load_16 | 32 | 0.0042066 | 0.0010543 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1709-1_0_8_load_155 | 33 | 0.0035748 | 0.00089592 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1709-1_0_8_load_156 | 34 | 0.001025 | 0.00025688 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1709-1_0_8_load_157 | 35 | 0.00504 | 0.0012631 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1709-1_0_8_load_159 | 36 | 0.0030362 | 0.00076093 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1709-1_0_8_load_33 | 37 | 0.0024876 | 0.00062346 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1709-1_0_8_load_160 | 38 | 0.0015015 | 0.00037632 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1709-1_0_8_load_31 | 39 | 0.0039399 | 0.00098744 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1709-1_0_8_load_45 | 40 | 0.0069002 | 0.0017294 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1709-1_0_8_load_46 | 41 | 0.0031463 | 0.00078854 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1709-1_0_8_load_19 | 42 | 0.0022207 | 0.00055656 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1709-1_0_8_load_22 | 45 | 0.011583 | 0.0029029 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1709-1_0_8_load_23 | 46 | 0.0033086 | 0.00082922 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1709-1_0_8_load_24 | 47 | 0.0023899 | 0.00059896 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1709-1_0_8_load_25 | 48 | 0.0033112 | 0.00082986 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1709-1_0_8_load_56 | 49 | 0.0048582 | 0.0012176 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1709-1_0_8_load_42 | 52 | 0.0030249 | 0.00075811 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1709-1_0_8_load_39 | 53 | 0.0028704 | 0.0007194 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1709-1_0_8_load_28 | 54 | 0.0027472 | 0.00068852 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1709-1_0_8_load_35 | 55 | 0.0026036 | 0.00065253 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1709-1_0_8_load_52 | 56 | 0.0027863 | 0.00069832 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1709-1_0_8_load_36 | 57 | 0.0025002 | 0.00062661 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1709-1_0_8_load_37 | 58 | 0.0028689 | 0.00071901 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1709-1_0_8_load_38 | 59 | 0.0016774 | 0.00042039 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1709-1_0_8_load_40 | 60 | 0.0011426 | 0.00028637 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1709-1_0_8_load_146 | 61 | 0.0028522 | 0.00071483 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1709-1_0_8_load_83 | 62 | 0.0023899 | 0.00059896 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1709-1_0_8_load_84 | 63 | 0.003022 | 0.00075739 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1709-1_0_8_load_47 | 64 | 0.0032611 | 0.00081731 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1709-1_0_8_load_48 | 65 | 0.0028606 | 0.00071695 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1709-1_0_8_load_49 | 66 | 0.0032636 | 0.00081792 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1709-1_0_8_load_51 | 67 | 0.0023893 | 0.00059882 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1709-1_0_8_load_57 | 68 | 0.0030591 | 0.00076669 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1709-1_0_8_load_77 | 69 | 0.0023638 | 0.00059242 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1709-1_0_8_load_58 | 70 | 0.0026074 | 0.00065348 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1709-1_0_8_load_78 | 71 | 0.0013997 | 0.00035079 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1709-1_0_8_load_104 | 72 | 0.0093381 | 0.0023404 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1709-1_0_8_load_105 | 73 | 0.0074069 | 0.0018563 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1709-1_0_8_load_118 | 74 | 0.011228 | 0.002814 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1709-1_0_8_load_130 | 76 | 0.0073664 | 0.0018462 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1709-1_0_8_load_140 | 77 | 0.020134 | 0.0050462 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1709-1_0_8_load_158 | 78 | 0.0025476 | 0.0006385 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1709-1_0_8_load_138 | 79 | 0.01163 | 0.0029147 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1709-1_0_8_load_139 | 80 | 0.0067423 | 0.0016898 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1709-1_0_8_load_142 | 83 | 0.0032639 | 0.000818 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1709-1_0_8_load_59 | 84 | 0.0068937 | 0.0017277 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1709-1_0_8_load_63 | 88 | 0.0043357 | 0.0010866 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1709-1_0_8_load_64 | 89 | 0.0039721 | 0.00099549 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1709-1_0_8_load_65 | 90 | 0.0044514 | 0.0011156 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1709-1_0_8_load_107 | 92 | 0.005172 | 0.0012962 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1709-1_0_8_load_85 | 93 | 0.0043191 | 0.0010825 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1709-1_0_8_load_70 | 94 | 0.0018157 | 0.00045506 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1709-1_0_8_load_75 | 95 | 0.0057587 | 0.0014433 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1709-1_0_8_load_100 | 96 | 0.0021181 | 0.00053085 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1709-1_0_8_load_86 | 97 | 0.0029562 | 0.0007409 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1709-1_0_8_load_66 | 98 | 0.0063514 | 0.0015918 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1709-1_0_8_load_71 | 103 | 0.0021162 | 0.00053036 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1709-1_0_8_load_119 | 104 | 0.016327 | 0.004092 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1709-1_0_8_load_143 | 106 | 0.003048 | 0.00076389 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1709-1_0_8_load_72 | 107 | 0.0070253 | 0.0017607 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1709-1_0_8_load_91 | 108 | 0.0012416 | 0.00031116 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1709-1_0_8_load_73 | 109 | 0.00812 | 0.0020351 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1709-1_0_8_load_89 | 110 | 0.0021165 | 0.00053045 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1709-1_0_8_load_79 | 111 | 0.0020832 | 0.00052209 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1709-1_0_8_load_80 | 112 | 0.0011078 | 0.00027763 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1709-1_0_8_load_81 | 113 | 0.0015998 | 0.00040094 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1709-1_0_8_load_103 | 115 | 0.0022428 | 0.00056211 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1709-1_0_8_load_124 | 116 | 0.0023899 | 0.00059896 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1709-1_0_8_load_129 | 117 | 0.0043182 | 0.0010823 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1709-1_0_8_load_145 | 118 | 0.0039689 | 0.0009947 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1709-1_0_8_load_144 | 119 | 0.0023879 | 0.00059848 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1709-1_0_8_load_87 | 120 | 0.0012529 | 0.00031402 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1709-1_0_8_load_88 | 121 | 0.0020039 | 0.00050224 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1709-1_0_8_load_90 | 122 | 0.0046281 | 0.0011599 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1709-1_0_8_load_92 | 123 | 0.0015105 | 0.00037857 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1709-1_0_8_load_95 | 126 | 0.0023903 | 0.00059907 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1709-1_0_8_load_96 | 127 | 0.002136 | 0.00053533 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1709-1_0_8_load_98 | 128 | 0.0022447 | 0.00056256 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1709-1_0_8_load_99 | 129 | 0.0019967 | 0.00050041 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1709-1_0_8_load_132 | 130 | 0.0027805 | 0.00069686 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_1709-1_0_8_load_97 | 131 | 0.0026244 | 0.00065773 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_1709-1_0_8_load_116 | 133 | 0.00092652 | 0.00023221 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_1709-1_0_8_load_131 | 135 | 0.0033837 | 0.00084804 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_1709-1_0_8_load_109 | 136 | 0.0017348 | 0.00043477 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_1709-1_0_8_load_108 | 137 | 0.0020559 | 0.00051527 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_1709-1_0_8_load_110 | 138 | 0.0014794 | 0.00037077 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_1709-1_0_8_load_111 | 139 | 0.012153 | 0.0030458 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_1709-1_0_8_load_112 | 140 | 0.0033098 | 0.00082951 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_1709-1_0_8_load_113 | 141 | 0.0035869 | 0.00089897 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_1709-1_0_8_load_115 | 142 | 0.0022255 | 0.00055777 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_1709-1_0_8_load_117 | 144 | 0.0028086 | 0.00070391 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_1709-1_0_8_load_133 | 145 | 0.0022404 | 0.00056151 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_1709-1_0_8_load_151 | 146 | 0.0053414 | 0.0013387 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_1709-1_0_8_load_150 | 148 | 0.0038938 | 0.00097589 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_1709-1_0_8_load_135 | 149 | 0.0025298 | 0.00063403 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_1709-1_0_8_load_136 | 150 | 0.0031759 | 0.00079594 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_1709-1_0_8_load_162 | 153 | 0.0048315 | 0.0012109 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_1709-1_0_8_load_161 | 154 | 0.0041352 | 0.0010364 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_1709-1_0_8_load_148 | 155 | 0.00057287 | 0.00014357 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_1709-1_0_8_load_149 | 156 | 0.0011778 | 0.00029518 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 64 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1709-1_0_8_line_0 |  | 0 | 1 | 0.0035937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1709-1_0_8_line_1 |  | 0 | 2 | 0.014286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1709-1_0_8_line_2 |  | 2 | 3 | 0.035731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1709-1_0_8_line_3 |  | 2 | 4 | 0.011014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1709-1_0_8_line_4 |  | 3 | 8 | 0.061085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1709-1_0_8_line_5 |  | 3 | 9 | 0.015272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1709-1_0_8_line_6 |  | 4 | 10 | 0.029183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1709-1_0_8_line_7 |  | 5 | 6 | 0.024584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1709-1_0_8_line_8 |  | 5 | 7 | 0.027574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1709-1_0_8_line_9 |  | 6 | 23 | 0.042121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1709-1_0_8_line_10 |  | 6 | 18 | 0.010034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1709-1_0_8_line_11 |  | 7 | 32 | 0.028662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1709-1_0_8_line_12 |  | 8 | 11 | 0.028644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1709-1_0_8_line_13 |  | 8 | 12 | 0.016709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1709-1_0_8_line_14 |  | 9 | 13 | 0.005434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1709-1_0_8_line_15 |  | 10 | 14 | 0.010963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1709-1_0_8_line_16 |  | 11 | 21 | 0.019016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1709-1_0_8_line_17 |  | 12 | 39 | 0.0020436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1709-1_0_8_line_18 |  | 13 | 40 | 0.013399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1709-1_0_8_line_19 |  | 15 | 16 | 0.028409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1709-1_0_8_line_20 |  | 15 | 17 | 0.035654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1709-1_0_8_line_21 |  | 16 | 18 | 0.021646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1709-1_0_8_line_22 |  | 17 | 19 | 0.020286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1709-1_0_8_line_23 |  | 18 | 20 | 0.024773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1709-1_0_8_line_24 |  | 19 | 22 | 0.016406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1709-1_0_8_line_25 |  | 20 | 24 | 0.018286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1709-1_0_8_line_26 |  | 21 | 25 | 0.0098515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1709-1_0_8_line_27 |  | 22 | 26 | 0.036283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1709-1_0_8_line_28 |  | 22 | 27 | 0.025436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1709-1_0_8_line_29 |  | 23 | 25 | 0.0038302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1709-1_0_8_line_30 |  | 24 | 54 | 0.011661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1709-1_0_8_line_31 |  | 26 | 117 | 0.023219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1709-1_0_8_line_32 |  | 26 | 135 | 0.017908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1709-1_0_8_line_33 |  | 27 | 148 | 0.0208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1709-1_0_8_line_34 |  | 28 | 29 | 0.0089741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1709-1_0_8_line_35 |  | 28 | 30 | 0.014861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1709-1_0_8_line_36 |  | 29 | 31 | 0.020575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1709-1_0_8_line_37 |  | 31 | 32 | 0.0092555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1709-1_0_8_line_38 |  | 33 | 34 | 0.043504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1709-1_0_8_line_39 |  | 34 | 35 | 0.016495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1709-1_0_8_line_40 |  | 35 | 36 | 0.021372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1709-1_0_8_line_41 |  | 36 | 78 | 0.0015681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1709-1_0_8_line_42 |  | 37 | 38 | 0.00051286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1709-1_0_8_line_43 |  | 37 | 39 | 0.037458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1709-1_0_8_line_44 |  | 40 | 41 | 0.016019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1709-1_0_8_line_45 |  | 42 | 43 | 0.02252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_1709-1_0_8_line_46 |  | 42 | 44 | 0.0024805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1709-1_0_8_line_47 |  | 43 | 45 | 0.025547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_1709-1_0_8_line_48 |  | 43 | 46 | 0.02135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1709-1_0_8_line_49 |  | 44 | 47 | 0.026484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1709-1_0_8_line_50 |  | 44 | 48 | 0.018046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1709-1_0_8_line_51 |  | 45 | 49 | 0.013357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1709-1_0_8_line_52 |  | 47 | 50 | 0.0029091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1709-1_0_8_line_53 |  | 49 | 51 | 0.019265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1709-1_0_8_line_54 |  | 50 | 52 | 0.017392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1709-1_0_8_line_55 |  | 50 | 53 | 0.01788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1709-1_0_8_line_56 |  | 51 | 68 | 0.017225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1709-1_0_8_line_57 |  | 51 | 65 | 0.026622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_1709-1_0_8_line_58 |  | 52 | 62 | 0.0075978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_1709-1_0_8_line_59 |  | 53 | 58 | 0.027751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1709-1_0_8_line_60 |  | 54 | 55 | 0.011128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1709-1_0_8_line_61 |  | 55 | 56 | 0.027198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1709-1_0_8_line_62 |  | 57 | 58 | 0.011577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1709-1_0_8_line_63 |  | 57 | 59 | 0.015688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1709-1_0_8_line_64 |  | 59 | 60 | 0.00049014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1709-1_0_8_line_65 |  | 60 | 61 | 0.0073697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1709-1_0_8_line_66 |  | 62 | 63 | 0.019846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_1709-1_0_8_line_67 |  | 63 | 116 | 0.0096252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1709-1_0_8_line_68 |  | 64 | 65 | 0.015303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1709-1_0_8_line_69 |  | 64 | 66 | 0.009408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_1709-1_0_8_line_70 |  | 66 | 67 | 0.019094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_1709-1_0_8_line_71 |  | 67 | 69 | 0.007501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_1709-1_0_8_line_72 |  | 68 | 70 | 0.0083806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1709-1_0_8_line_73 |  | 69 | 71 | 0.022996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_1709-1_0_8_line_74 |  | 71 | 111 | 0.0039365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_1709-1_0_8_line_75 |  | 72 | 73 | 0.01117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1709-1_0_8_line_76 |  | 72 | 74 | 0.065113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1709-1_0_8_line_77 |  | 73 | 75 | 0.019895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1709-1_0_8_line_78 |  | 74 | 77 | 0.044131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1709-1_0_8_line_79 |  | 75 | 76 | 0.011689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1709-1_0_8_line_80 |  | 76 | 78 | 0.01909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1709-1_0_8_line_81 |  | 77 | 79 | 0.043804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_1709-1_0_8_line_82 |  | 79 | 80 | 0.00025908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_1709-1_0_8_line_83 |  | 80 | 81 | 0.01926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_1709-1_0_8_line_84 |  | 81 | 82 | 0.026948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1709-1_0_8_line_85 |  | 82 | 83 | 0.016333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1709-1_0_8_line_86 |  | 82 | 105 | 0.021709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1709-1_0_8_line_87 |  | 84 | 85 | 0.0083939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1709-1_0_8_line_88 |  | 84 | 86 | 0.039281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1709-1_0_8_line_89 |  | 85 | 87 | 0.013711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1709-1_0_8_line_90 |  | 85 | 88 | 0.01723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1709-1_0_8_line_91 |  | 86 | 89 | 0.039741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1709-1_0_8_line_92 |  | 86 | 90 | 0.0033484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1709-1_0_8_line_93 |  | 87 | 91 | 0.04015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_1709-1_0_8_line_94 |  | 87 | 92 | 0.005103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_1709-1_0_8_line_95 |  | 88 | 93 | 0.017924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1709-1_0_8_line_96 |  | 91 | 94 | 0.0037964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1709-1_0_8_line_97 |  | 91 | 95 | 0.028578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_1709-1_0_8_line_98 |  | 92 | 96 | 0.016256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_1709-1_0_8_line_99 |  | 93 | 97 | 0.016508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1709-1_0_8_line_100 |  | 94 | 102 | 0.020005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1709-1_0_8_line_101 |  | 95 | 101 | 0.021537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_1709-1_0_8_line_102 |  | 96 | 129 | 0.019622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_1709-1_0_8_line_103 |  | 97 | 118 | 0.006713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1709-1_0_8_line_104 |  | 98 | 99 | 0.0088459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_1709-1_0_8_line_105 |  | 98 | 100 | 0.056097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
106 | LV_1709-1_0_8_line_106 |  | 99 | 101 | 0.021902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_1709-1_0_8_line_107 |  | 100 | 106 | 0.016811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1709-1_0_8_line_108 |  | 100 | 105 | 0.030991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_1709-1_0_8_line_109 |  | 101 | 107 | 0.024078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1709-1_0_8_line_110 |  | 102 | 103 | 0.01195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1709-1_0_8_line_111 |  | 103 | 108 | 0.021626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1709-1_0_8_line_112 |  | 104 | 105 | 0.024695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1709-1_0_8_line_113 |  | 107 | 109 | 0.022487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1709-1_0_8_line_114 |  | 108 | 110 | 0.0085507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1709-1_0_8_line_115 |  | 110 | 120 | 0.014838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1709-1_0_8_line_116 |  | 111 | 112 | 0.021212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
117 | LV_1709-1_0_8_line_117 |  | 112 | 113 | 0.0020505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
118 | LV_1709-1_0_8_line_118 |  | 113 | 114 | 0.018398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
119 | LV_1709-1_0_8_line_119 |  | 114 | 115 | 0.015627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
120 | LV_1709-1_0_8_line_120 |  | 115 | 132 | 0.019727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
121 | LV_1709-1_0_8_line_121 |  | 116 | 117 | 0.016262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
122 | LV_1709-1_0_8_line_122 |  | 118 | 119 | 0.037206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1709-1_0_8_line_123 |  | 119 | 146 | 0.046749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1709-1_0_8_line_124 |  | 119 | 142 | 0.0062262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1709-1_0_8_line_125 |  | 120 | 121 | 0.01099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_1709-1_0_8_line_126 |  | 121 | 122 | 0.01465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_1709-1_0_8_line_127 |  | 123 | 124 | 0.0055608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
128 | LV_1709-1_0_8_line_128 |  | 123 | 125 | 0.023528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
129 | LV_1709-1_0_8_line_129 |  | 124 | 126 | 0.017287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
130 | LV_1709-1_0_8_line_130 |  | 124 | 127 | 0.019297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_1709-1_0_8_line_131 |  | 125 | 128 | 0.014915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
132 | LV_1709-1_0_8_line_132 |  | 126 | 129 | 0.0088102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
133 | LV_1709-1_0_8_line_133 |  | 127 | 130 | 0.012093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_1709-1_0_8_line_134 |  | 128 | 132 | 0.0078213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
135 | LV_1709-1_0_8_line_135 |  | 130 | 133 | 0.00099385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_1709-1_0_8_line_136 |  | 131 | 132 | 0.018694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_1709-1_0_8_line_137 |  | 133 | 143 | 0.016522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_1709-1_0_8_line_138 |  | 134 | 135 | 0.012157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_1709-1_0_8_line_139 |  | 134 | 136 | 0.011847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_1709-1_0_8_line_140 |  | 136 | 137 | 0.014447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_1709-1_0_8_line_141 |  | 137 | 138 | 0.011163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_1709-1_0_8_line_142 |  | 138 | 139 | 0.0279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_1709-1_0_8_line_143 |  | 140 | 141 | 0.00087939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
144 | LV_1709-1_0_8_line_144 |  | 141 | 142 | 0.021697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
145 | LV_1709-1_0_8_line_145 |  | 143 | 144 | 0.019765 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
146 | LV_1709-1_0_8_line_146 |  | 144 | 145 | 0.0059338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
147 | LV_1709-1_0_8_line_147 |  | 145 | 147 | 0.019255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
148 | LV_1709-1_0_8_line_148 |  | 147 | 149 | 0.025526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
149 | LV_1709-1_0_8_line_149 |  | 147 | 150 | 0.051932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
150 | LV_1709-1_0_8_line_150 |  | 149 | 151 | 0.013727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
151 | LV_1709-1_0_8_line_151 |  | 151 | 155 | 0.03999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
152 | LV_1709-1_0_8_line_152 |  | 151 | 156 | 0.0083398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
153 | LV_1709-1_0_8_line_153 |  | 152 | 153 | 0.023078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
154 | LV_1709-1_0_8_line_154 |  | 152 | 154 | 0.0025036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
155 | LV_1709-1_0_8_line_155 |  | 154 | 156 | 0.018811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1709-1_0_8_trafo_47 | 0.63 MVA 20/0.4 kV | 157 | 64 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2687590.8527 | 1220805.3709 | 2687594.0986 | 1220803.8284
1 | 2687577.9491 | 1220811.5026 | 2687590.8527 | 1220805.3709
2 | 2687577.9491 | 1220811.5026 | 2687553.9161 | 1220838.0007
3 | 2687573.2472 | 1220801.5378 | 2687577.9491 | 1220811.5026
4 | 2687513.9543 | 1220884.2895 | 2687553.9161 | 1220838.0007
5 | 2687553.9161 | 1220838.0007 | 2687541.9288 | 1220828.5388
6 | 2687573.2472 | 1220801.5378 | 2687594.7292 | 1220781.7852
7 | 2687429.6915 | 1220878.0682 | 2687431.4203 | 1220853.5455
8 | 2687431.4203 | 1220853.5455 | 2687431.4203 | 1220853.5455 | 2687409.3491 | 1220837.0162
9 | 2687429.6915 | 1220878.0682 | 2687471.2912 | 1220884.6742
10 | 2687428.9858 | 1220888.0777 | 2687429.6915 | 1220878.0682
11 | 2687409.3491 | 1220837.0162 | 2687386.4072 | 1220819.8349
12 | 2687495.7148 | 1220906.4144 | 2687513.9543 | 1220884.2895
13 | 2687513.9543 | 1220884.2895 | 2687501.2546 | 1220873.4313
14 | 2687537.6635 | 1220825.1721 | 2687541.9288 | 1220828.5388
15 | 2687602.7991 | 1220774.3649 | 2687594.7292 | 1220781.7852
16 | 2687495.7148 | 1220906.4144 | 2687481.5106 | 1220893.7709
17 | 2687499.7013 | 1220872.1033 | 2687501.2546 | 1220873.4313
18 | 2687527.1465 | 1220816.8707 | 2687527.1465 | 1220816.8707 | 2687537.6635 | 1220825.1721
19 | 2687429.8334 | 1220909.7073 | 2687430.9457 | 1220938.0942
20 | 2687436.6441 | 1220972.114 | 2687432.0543 | 1220966.3872 | 2687430.9457 | 1220938.0942
21 | 2687428.9858 | 1220888.0777 | 2687429.8334 | 1220909.7073
22 | 2687436.6441 | 1220972.114 | 2687421.5117 | 1220985.6247
23 | 2687428.9858 | 1220888.0777 | 2687408.4502 | 1220874.2223
24 | 2687409.2738 | 1220996.5512 | 2687421.5117 | 1220985.6247
25 | 2687393.2918 | 1220863.9949 | 2687408.4502 | 1220874.2223
26 | 2687474.1521 | 1220887.2208 | 2687481.5106 | 1220893.7709
27 | 2687409.2738 | 1220996.5512 | 2687379.6691 | 1221017.6423
28 | 2687409.2738 | 1220996.5512 | 2687429.9816 | 1221011.3215
29 | 2687471.2912 | 1220884.6742 | 2687474.1521 | 1220887.2208
30 | 2687393.2918 | 1220863.9949 | 2687383.6252 | 1220857.4728
31 | 2687379.6691 | 1221017.6423 | 2687370.5665 | 1220996.2825
32 | 2687379.6691 | 1221017.6423 | 2687364.1629 | 1221026.6003
33 | 2687446.9153 | 1221023.3998 | 2687429.9816 | 1221011.3215
34 | 2687362.5306 | 1220801.9535 | 2687355.3475 | 1220796.5741
35 | 2687343.4522 | 1220787.6656 | 2687355.3475 | 1220796.5741
36 | 2687362.5306 | 1220801.9535 | 2687378.9989 | 1220814.2867
37 | 2687378.9989 | 1220814.2867 | 2687386.4072 | 1220819.8349
38 | 2687174.972 | 1220670.0552 | 2687162.3787 | 1220698.5528 | 2687157.39 | 1220709.8484
39 | 2687150.8095 | 1220724.9734 | 2687154.0991 | 1220717.2999 | 2687157.39 | 1220709.8484
40 | 2687142.3886 | 1220744.6169 | 2687150.8095 | 1220724.9734
41 | 2687142.3886 | 1220744.6169 | 2687141.7707 | 1220746.0581
42 | 2687493.7668 | 1220844.8762 | 2687494.1127 | 1220844.4975
43 | 2687499.7013 | 1220872.1033 | 2687484.8573 | 1220859.4118 | 2687485.0289 | 1220854.4443 | 2687493.7668 | 1220844.8762
44 | 2687527.1465 | 1220816.8707 | 2687521.9892 | 1220818.774 | 2687514.1383 | 1220825.7791
45 | 2687313.6183 | 1220887.4407 | 2687323.9948 | 1220893.3523 | 2687329.8707 | 1220902.148
46 | 2687331.2486 | 1220904.2105 | 2687329.8707 | 1220902.148
47 | 2687313.6183 | 1220887.4407 | 2687290.8921 | 1220899.1103
48 | 2687313.6183 | 1220887.4407 | 2687315.0794 | 1220881.458 | 2687325.672 | 1220870.5689
49 | 2687331.2486 | 1220904.2105 | 2687341.6933 | 1220928.5478
50 | 2687331.2486 | 1220904.2105 | 2687347.5939 | 1220896.5621
51 | 2687279.0102 | 1220905.2115 | 2687290.8921 | 1220899.1103
52 | 2687342.8406 | 1220931.2211 | 2687341.6933 | 1220928.5478
53 | 2687265.2009 | 1220917.0068 | 2687267.4722 | 1220911.1361 | 2687279.0102 | 1220905.2115
54 | 2687342.8406 | 1220931.2211 | 2687349.6588 | 1220947.2206
55 | 2687342.8406 | 1220931.2211 | 2687359.2806 | 1220924.1916
56 | 2687265.2009 | 1220917.0068 | 2687252.6398 | 1220911.0521 | 2687249.5076 | 1220912.165
57 | 2687265.2009 | 1220917.0068 | 2687263.2292 | 1220922.1148 | 2687271.8382 | 1220941.4296
58 | 2687349.6588 | 1220947.2206 | 2687352.6374 | 1220954.2101
59 | 2687359.2806 | 1220924.1916 | 2687384.7968 | 1220913.2814
60 | 2687374.4002 | 1220851.2487 | 2687383.6252 | 1220857.4728
61 | 2687374.4002 | 1220851.2487 | 2687351.8542 | 1220836.0368
62 | 2687395.5303 | 1220912.4923 | 2687390.7837 | 1220910.7214 | 2687384.7968 | 1220913.2814
63 | 2687395.5303 | 1220912.4923 | 2687395.5303 | 1220912.4923 | 2687400.8082 | 1220927.2663
64 | 2687400.9731 | 1220927.7279 | 2687400.8082 | 1220927.2663
65 | 2687403.4524 | 1220934.6681 | 2687400.9731 | 1220927.7279
66 | 2687352.6374 | 1220954.2101 | 2687360.4178 | 1220972.4675
67 | 2687364.1912 | 1220981.3223 | 2687360.4178 | 1220972.4675
68 | 2687278.0684 | 1220955.4073 | 2687271.8382 | 1220941.4296
69 | 2687278.0684 | 1220955.4073 | 2687281.8985 | 1220964.0003
70 | 2687289.672 | 1220981.4408 | 2687281.8985 | 1220964.0003
71 | 2687289.672 | 1220981.4408 | 2687292.7258 | 1220988.292
72 | 2687241.6107 | 1220914.971 | 2687249.5076 | 1220912.165
73 | 2687302.0879 | 1221009.2964 | 2687292.7258 | 1220988.292
74 | 2687303.6905 | 1221012.8919 | 2687302.0879 | 1221009.2964
75 | 2687115.1852 | 1220801.8427 | 2687120.3838 | 1220791.9566
76 | 2687152.9285 | 1220854.9005 | 2687115.1852 | 1220801.8427
77 | 2687129.6433 | 1220774.3476 | 2687120.3838 | 1220791.9566
78 | 2687170.3231 | 1220895.4585 | 2687152.9285 | 1220854.9005
79 | 2687129.6433 | 1220774.3476 | 2687134.2489 | 1220763.6041
80 | 2687134.2489 | 1220763.6041 | 2687141.7707 | 1220746.0581
81 | 2687170.3231 | 1220895.4585 | 2687166.9133 | 1220904.4703 | 2687135.9839 | 1220918.9909
82 | 2687135.7494 | 1220919.101 | 2687135.9839 | 1220918.9909
83 | 2687118.3149 | 1220927.286 | 2687135.7494 | 1220919.101
84 | 2687118.3149 | 1220927.286 | 2687128.4276 | 1220952.2732
85 | 2687128.4276 | 1220952.2732 | 2687143.4777 | 1220945.9277
86 | 2687128.4276 | 1220952.2732 | 2687135.7461 | 1220972.7164
87 | 2687167.6598 | 1221118.2602 | 2687159.3375 | 1221119.354
88 | 2687120.3911 | 1221124.4729 | 2687159.3375 | 1221119.354
89 | 2687181.1651 | 1221115.6783 | 2687167.6598 | 1221118.2602
90 | 2687167.6598 | 1221118.2602 | 2687170.6306 | 1221135.2325
91 | 2687120.3911 | 1221124.4729 | 2687123.2265 | 1221150.0317 | 2687137.2033 | 1221148.8648
92 | 2687120.3911 | 1221124.4729 | 2687117.0714 | 1221124.9096
93 | 2687181.1651 | 1221115.6783 | 2687175.0176 | 1221088.8589 | 2687171.1192 | 1221076.8381
94 | 2687181.1651 | 1221115.6783 | 2687186.0693 | 1221114.2679
95 | 2687180.6847 | 1221149.5772 | 2687173.319 | 1221142.1593 | 2687170.9085 | 1221136.8204 | 2687170.6306 | 1221135.2325
96 | 2687171.1192 | 1221076.8381 | 2687170.0231 | 1221073.2034
97 | 2687171.1192 | 1221076.8381 | 2687156.1574 | 1221079.9213 | 2687152.2882 | 1221083.5227 | 2687144.285 | 1221083.0678
98 | 2687186.0693 | 1221114.2679 | 2687196.5791 | 1221111.2453 | 2687201.5377 | 1221109.3176
99 | 2687180.6847 | 1221149.5772 | 2687192.316 | 1221161.2909
100 | 2687166.4712 | 1221054.3548 | 2687165.0265 | 1221056.6352 | 2687170.0231 | 1221073.2034
101 | 2687122.7829 | 1221081.8455 | 2687144.285 | 1221083.0678
102 | 2687201.5377 | 1221109.3176 | 2687219.8261 | 1221102.2077
103 | 2687197.0461 | 1221166.0544 | 2687192.316 | 1221161.2909
104 | 2687123.7025 | 1221059.9663 | 2687124.1443 | 1221057.7712 | 2687130.4304 | 1221055.7377
105 | 2687130.4304 | 1221055.7377 | 2687146.1917 | 1221001.9001
106 | 2687123.7025 | 1221059.9663 | 2687122.7829 | 1221081.8455
107 | 2687146.1917 | 1221001.9001 | 2687161.7699 | 1220995.5817
108 | 2687146.1917 | 1221001.9001 | 2687135.7461 | 1220972.7164
109 | 2687122.7829 | 1221081.8455 | 2687117.5141 | 1221081.546 | 2687098.7136 | 1221081.4677
110 | 2687166.4712 | 1221054.3548 | 2687177.4564 | 1221049.6499
111 | 2687197.3357 | 1221041.1357 | 2687177.4564 | 1221049.6499
112 | 2687135.7461 | 1220972.7164 | 2687112.254 | 1220980.3306
113 | 2687098.7136 | 1221081.4677 | 2687089.9054 | 1221081.4311 | 2687083.0654 | 1221093.2769
114 | 2687205.1959 | 1221037.7693 | 2687197.3357 | 1221041.1357
115 | 2687218.8355 | 1221031.9275 | 2687205.1959 | 1221037.7693
116 | 2687303.6905 | 1221012.8919 | 2687312.3262 | 1221032.2667
117 | 2687313.161 | 1221034.1396 | 2687312.3262 | 1221032.2667
118 | 2687320.6511 | 1221050.944 | 2687313.161 | 1221034.1396
119 | 2687320.6511 | 1221050.944 | 2687306.9384 | 1221058.4392
120 | 2687289.6281 | 1221067.9009 | 2687306.9384 | 1221058.4392
121 | 2687364.1912 | 1220981.3223 | 2687370.5665 | 1220996.2825
122 | 2687228.0257 | 1221177.6961 | 2687223.1339 | 1221180.6814 | 2687215.6545 | 1221180.5718 | 2687208.3858 | 1221177.4744 | 2687197.0461 | 1221166.0544
123 | 2687228.0257 | 1221177.6961 | 2687199.4732 | 1221214.7122
124 | 2687228.0257 | 1221177.6961 | 2687229.5034 | 1221176.7943 | 2687232.6741 | 1221173.608
125 | 2687218.8355 | 1221031.9275 | 2687228.9376 | 1221027.6009
126 | 2687242.4042 | 1221021.8332 | 2687228.9376 | 1221027.6009
127 | 2687244.1494 | 1221092.7515 | 2687249.0398 | 1221090.1047
128 | 2687269.732 | 1221078.9057 | 2687249.0398 | 1221090.1047
129 | 2687244.1494 | 1221092.7515 | 2687228.0376 | 1221099.0153
130 | 2687244.1494 | 1221092.7515 | 2687257.613 | 1221106.5751
131 | 2687269.732 | 1221078.9057 | 2687282.7839 | 1221071.6865
132 | 2687228.0376 | 1221099.0153 | 2687219.8261 | 1221102.2077
133 | 2687266.0504 | 1221115.2382 | 2687257.613 | 1221106.5751
134 | 2687289.6281 | 1221067.9009 | 2687282.7839 | 1221071.6865
135 | 2687266.7438 | 1221115.9501 | 2687266.0504 | 1221115.2382
136 | 2687289.6281 | 1221067.9009 | 2687285.2253 | 1221059.7641 | 2687282.1277 | 1221057.8285 | 2687277.1065 | 1221057.199 | 2687276.4576 | 1221057.5326
137 | 2687278.2718 | 1221127.7864 | 2687266.7438 | 1221115.9501
138 | 2687353.6359 | 1221032.6819 | 2687364.1629 | 1221026.6003
139 | 2687353.6359 | 1221032.6819 | 2687363.1164 | 1221039.7864
140 | 2687374.6777 | 1221048.4503 | 2687363.1164 | 1221039.7864
141 | 2687383.6107 | 1221055.1447 | 2687374.6777 | 1221048.4503
142 | 2687405.937 | 1221071.8758 | 2687383.6107 | 1221055.1447
143 | 2687247.9787 | 1221158.2283 | 2687248.599 | 1221157.605
144 | 2687247.9787 | 1221158.2283 | 2687232.6741 | 1221173.608
145 | 2687278.2718 | 1221127.7864 | 2687292.5598 | 1221141.4432
146 | 2687296.8493 | 1221145.5432 | 2687292.5598 | 1221141.4432
147 | 2687310.9374 | 1221158.6639 | 2687306.3532 | 1221154.6273 | 2687296.8493 | 1221145.5432
148 | 2687310.9374 | 1221158.6639 | 2687327.6868 | 1221177.9257
149 | 2687310.9374 | 1221158.6639 | 2687333.8373 | 1221136.3177 | 2687348.6573 | 1221149.6523
150 | 2687336.694 | 1221188.2839 | 2687327.6868 | 1221177.9257
151 | 2687336.694 | 1221188.2839 | 2687360.9424 | 1221212.6006 | 2687365.0123 | 1221216.5185
152 | 2687336.694 | 1221188.2839 | 2687330.3221 | 1221193.6646
153 | 2687314.0312 | 1221207.4092 | 2687298.793 | 1221221.0729 | 2687296.939 | 1221222.9114
154 | 2687314.0312 | 1221207.4092 | 2687315.9448 | 1221205.7948
155 | 2687330.3221 | 1221193.6646 | 2687328.7735 | 1221194.9724 | 2687315.9448 | 1221205.7948

## bus_geodata
| x | y | coords
0 | 2687590.8527 | 1220805.3709
1 | 2687594.0986 | 1220803.8284
2 | 2687577.9491 | 1220811.5026
3 | 2687553.9161 | 1220838.0007
4 | 2687573.2472 | 1220801.5378
5 | 2687431.4203 | 1220853.5455
6 | 2687429.6915 | 1220878.0682
7 | 2687409.3491 | 1220837.0162
8 | 2687513.9543 | 1220884.2895
9 | 2687541.9288 | 1220828.5388
10 | 2687594.7292 | 1220781.7852
11 | 2687495.7148 | 1220906.4144
12 | 2687501.2546 | 1220873.4313
13 | 2687537.6635 | 1220825.1721
14 | 2687602.7991 | 1220774.3649
15 | 2687430.9457 | 1220938.0942
16 | 2687429.8334 | 1220909.7073
17 | 2687436.6441 | 1220972.114
18 | 2687428.9858 | 1220888.0777
19 | 2687421.5117 | 1220985.6247
20 | 2687408.4502 | 1220874.2223
21 | 2687481.5106 | 1220893.7709
22 | 2687409.2738 | 1220996.5512
23 | 2687471.2912 | 1220884.6742
24 | 2687393.2918 | 1220863.9949
25 | 2687474.1521 | 1220887.2208
26 | 2687379.6691 | 1221017.6423
27 | 2687429.9816 | 1221011.3215
28 | 2687355.3475 | 1220796.5741
29 | 2687362.5306 | 1220801.9535
30 | 2687343.4522 | 1220787.6656
31 | 2687378.9989 | 1220814.2867
32 | 2687386.4072 | 1220819.8349
33 | 2687174.972 | 1220670.0552
34 | 2687157.39 | 1220709.8484
35 | 2687150.8095 | 1220724.9734
36 | 2687142.3886 | 1220744.6169
37 | 2687493.7668 | 1220844.8762
38 | 2687494.1127 | 1220844.4975
39 | 2687499.7013 | 1220872.1033
40 | 2687527.1465 | 1220816.8707
41 | 2687514.1383 | 1220825.7791
42 | 2687329.8707 | 1220902.148
43 | 2687313.6183 | 1220887.4407
44 | 2687331.2486 | 1220904.2105
45 | 2687290.8921 | 1220899.1103
46 | 2687325.672 | 1220870.5689
47 | 2687341.6933 | 1220928.5478
48 | 2687347.5939 | 1220896.5621
49 | 2687279.0102 | 1220905.2115
50 | 2687342.8406 | 1220931.2211
51 | 2687265.2009 | 1220917.0068
52 | 2687349.6588 | 1220947.2206
53 | 2687359.2806 | 1220924.1916
54 | 2687383.6252 | 1220857.4728
55 | 2687374.4002 | 1220851.2487
56 | 2687351.8542 | 1220836.0368
57 | 2687395.5303 | 1220912.4923
58 | 2687384.7968 | 1220913.2814
59 | 2687400.8082 | 1220927.2663
60 | 2687400.9731 | 1220927.7279
61 | 2687403.4524 | 1220934.6681
62 | 2687352.6374 | 1220954.2101
63 | 2687360.4178 | 1220972.4675
64 | 2687278.0684 | 1220955.4073
65 | 2687271.8382 | 1220941.4296
66 | 2687281.8985 | 1220964.0003
67 | 2687289.672 | 1220981.4408
68 | 2687249.5076 | 1220912.165
69 | 2687292.7258 | 1220988.292
70 | 2687241.6107 | 1220914.971
71 | 2687302.0879 | 1221009.2964
72 | 2687115.1852 | 1220801.8427
73 | 2687120.3838 | 1220791.9566
74 | 2687152.9285 | 1220854.9005
75 | 2687129.6433 | 1220774.3476
76 | 2687134.2489 | 1220763.6041
77 | 2687170.3231 | 1220895.4585
78 | 2687141.7707 | 1220746.0581
79 | 2687135.9839 | 1220918.9909
80 | 2687135.7494 | 1220919.101
81 | 2687118.3149 | 1220927.286
82 | 2687128.4275 | 1220952.2732
83 | 2687143.4777 | 1220945.9277
84 | 2687159.3375 | 1221119.354
85 | 2687167.6598 | 1221118.2602
86 | 2687120.3911 | 1221124.4729
87 | 2687181.1651 | 1221115.6783
88 | 2687170.6306 | 1221135.2325
89 | 2687137.2033 | 1221148.8648
90 | 2687117.0714 | 1221124.9096
91 | 2687171.1192 | 1221076.8381
92 | 2687186.0693 | 1221114.2679
93 | 2687180.6847 | 1221149.5772
94 | 2687170.0231 | 1221073.2034
95 | 2687144.285 | 1221083.0678
96 | 2687201.5377 | 1221109.3176
97 | 2687192.316 | 1221161.2909
98 | 2687130.4304 | 1221055.7377
99 | 2687123.7025 | 1221059.9663
100 | 2687146.1917 | 1221001.9001
101 | 2687122.7829 | 1221081.8455
102 | 2687166.4712 | 1221054.3548
103 | 2687177.4564 | 1221049.6499
104 | 2687112.254 | 1220980.3306
105 | 2687135.7461 | 1220972.7164
106 | 2687161.7699 | 1220995.5817
107 | 2687098.7136 | 1221081.4677
108 | 2687197.3357 | 1221041.1357
109 | 2687083.0654 | 1221093.2769
110 | 2687205.1959 | 1221037.7693
111 | 2687303.6905 | 1221012.8919
112 | 2687312.3262 | 1221032.2667
113 | 2687313.161 | 1221034.1396
114 | 2687320.6511 | 1221050.944
115 | 2687306.9384 | 1221058.4392
116 | 2687364.1912 | 1220981.3223
117 | 2687370.5665 | 1220996.2825
118 | 2687197.0461 | 1221166.0544
119 | 2687228.0257 | 1221177.6961
120 | 2687218.8355 | 1221031.9275
121 | 2687228.9376 | 1221027.6009
122 | 2687242.4042 | 1221021.8332
123 | 2687249.0398 | 1221090.1047
124 | 2687244.1494 | 1221092.7515
125 | 2687269.732 | 1221078.9057
126 | 2687228.0376 | 1221099.0153
127 | 2687257.613 | 1221106.5751
128 | 2687282.7839 | 1221071.6865
129 | 2687219.8261 | 1221102.2077
130 | 2687266.0504 | 1221115.2382
131 | 2687276.4576 | 1221057.5326
132 | 2687289.6281 | 1221067.9009
133 | 2687266.7438 | 1221115.9501
134 | 2687353.6359 | 1221032.6819
135 | 2687364.1629 | 1221026.6003
136 | 2687363.1164 | 1221039.7864
137 | 2687374.6777 | 1221048.4503
138 | 2687383.6107 | 1221055.1447
139 | 2687405.937 | 1221071.8758
140 | 2687248.599 | 1221157.605
141 | 2687247.9787 | 1221158.2283
142 | 2687232.6741 | 1221173.608
143 | 2687278.2718 | 1221127.7864
144 | 2687292.5598 | 1221141.4432
145 | 2687296.8493 | 1221145.5432
146 | 2687199.4732 | 1221214.7122
147 | 2687310.9374 | 1221158.6639
148 | 2687446.9153 | 1221023.3998
149 | 2687327.6868 | 1221177.9257
150 | 2687348.6573 | 1221149.6523
151 | 2687336.694 | 1221188.2839
152 | 2687314.0312 | 1221207.4092
153 | 2687296.939 | 1221222.9114
154 | 2687315.9448 | 1221205.7948
155 | 2687365.0123 | 1221216.5185
156 | 2687330.3221 | 1221193.6646
157 | 2687265.2009 | 1220917.0068

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97092 | -0.5614 | 0.0014983 | 0.00037551
1 | 0.97091 | -0.56153 | 0.0019587 | 0.0004909
2 | 0.97097 | -0.56049 | 0 | 0
3 | 0.97118 | -0.55628 | 0 | 0
4 | 0.97094 | -0.56108 | 0 | 0
5 | 0.9753 | -0.47507 | 0.002787 | 0.00069848
6 | 0.97588 | -0.46361 | 0.003191 | 0.00079974
7 | 0.97472 | -0.48652 | 0.0026647 | 0.00066784
8 | 0.97246 | -0.53101 | 0 | 0
9 | 0.97095 | -0.56081 | 0.0032008 | 0.0008022
10 | 0.97086 | -0.56265 | 0.0013322 | 0.00033388
11 | 0.97334 | -0.51356 | 0 | 0
12 | 0.97229 | -0.5343 | 0.0027309 | 0.00068444
13 | 0.97088 | -0.5621 | 0.002796 | 0.00070074
14 | 0.97084 | -0.56297 | 0.0015783 | 0.00039556
15 | 0.9803 | -0.37714 | 0.00257 | 0.00064411
16 | 0.97812 | -0.41975 | 0.0026162 | 0.00065567
17 | 0.98313 | -0.32227 | 0 | 0
18 | 0.97651 | -0.45131 | 0 | 0
19 | 0.98474 | -0.29119 | 0.0020892 | 0.00052361
20 | 0.97621 | -0.45714 | 0.0024616 | 0.00061693
21 | 0.97393 | -0.502 | 0.0015332 | 0.00038424
22 | 0.98607 | -0.26552 | 0 | 0
23 | 0.97437 | -0.49325 | 0.0030009 | 0.0007521
24 | 0.97603 | -0.46062 | 0.0022745 | 0.00057004
25 | 0.97425 | -0.49573 | 0.00076781 | 0.00019243
26 | 0.98925 | -0.20459 | 0 | 0
27 | 0.98591 | -0.26862 | 0.0029056 | 0.0007282
28 | 0.97373 | -0.50599 | 0.0055206 | 0.0013836
29 | 0.97381 | -0.50441 | 0.00282 | 0.00070675
30 | 0.97367 | -0.50709 | 0.0040403 | 0.0010126
31 | 0.97405 | -0.49973 | 0.0034058 | 0.00085359
32 | 0.97418 | -0.49704 | 0.0042066 | 0.0010543
33 | 0.97049 | -0.57084 | 0.0035748 | 0.00089592
34 | 0.97063 | -0.56796 | 0.001025 | 0.00025688
35 | 0.9707 | -0.56656 | 0.00504 | 0.0012631
36 | 0.9709 | -0.56275 | 0.0030362 | 0.00076093
37 | 0.97214 | -0.53735 | 0.0024876 | 0.00062346
38 | 0.97214 | -0.53736 | 0.0015015 | 0.00037632
39 | 0.97228 | -0.53459 | 0.0039399 | 0.00098744
40 | 0.97076 | -0.56459 | 0.0069002 | 0.0017294
41 | 0.97071 | -0.56552 | 0.0031463 | 0.00078854
42 | 0.99529 | -0.089248 | 0.0022207 | 0.00055656
43 | 0.99608 | -0.074224 | 0 | 0
44 | 0.99521 | -0.09088 | 0 | 0
45 | 0.997 | -0.056838 | 0.011583 | 0.0029029
46 | 0.99602 | -0.075465 | 0.0033086 | 0.00082922
47 | 0.99431 | -0.10794 | 0.0023899 | 0.00059896
48 | 0.99515 | -0.091932 | 0.0033112 | 0.00082986
49 | 0.99751 | -0.047083 | 0.0048582 | 0.0012176
50 | 0.99421 | -0.10978 | 0 | 0
51 | 0.99828 | -0.032622 | 0 | 0
52 | 0.99369 | -0.11975 | 0.0030249 | 0.00075811
53 | 0.99399 | -0.11417 | 0.0028704 | 0.0007194
54 | 0.97595 | -0.46236 | 0.0027472 | 0.00068852
55 | 0.97589 | -0.46346 | 0.0026036 | 0.00065253
56 | 0.97582 | -0.46485 | 0.0027863 | 0.00069832
57 | 0.99362 | -0.12125 | 0.0025002 | 0.00062661
58 | 0.99371 | -0.11958 | 0.0028689 | 0.00071901
59 | 0.99354 | -0.12282 | 0.0016774 | 0.00042039
60 | 0.99354 | -0.12285 | 0.0011426 | 0.00028637
61 | 0.99352 | -0.12322 | 0.0028522 | 0.00071483
62 | 0.99346 | -0.124 | 0.0023899 | 0.00059896
63 | 0.99289 | -0.13492 | 0.003022 | 0.00075739
64 | 1 | 0 | -0.45268 | -0.11581
65 | 0.99936 | -0.012016 | 0.0028606 | 0.00071695
66 | 0.99943 | -0.010821 | 0.0032636 | 0.00081792
67 | 0.99828 | -0.032549 | 0.0023893 | 0.00059882
68 | 0.99819 | -0.034329 | 0.0030591 | 0.00076669
69 | 0.99783 | -0.04102 | 0.0023638 | 0.00059242
70 | 0.99817 | -0.034712 | 0.0026074 | 0.00065348
71 | 0.99647 | -0.066798 | 0.0013997 | 0.00035079
72 | 0.97216 | -0.53765 | 0.0093381 | 0.0023404
73 | 0.97185 | -0.54383 | 0.0074069 | 0.0018563
74 | 0.97456 | -0.49052 | 0.011228 | 0.002814
75 | 0.97143 | -0.55213 | 0 | 0
76 | 0.97119 | -0.55701 | 0.0073664 | 0.0018462
77 | 0.97664 | -0.44966 | 0.020134 | 0.0050462
78 | 0.97091 | -0.56238 | 0.0025476 | 0.0006385
79 | 0.97808 | -0.4214 | 0.01163 | 0.0029147
80 | 0.97808 | -0.4213 | 0.0067423 | 0.0016898
81 | 0.97848 | -0.41349 | 0 | 0
82 | 0.97904 | -0.40257 | 0 | 0
83 | 0.97899 | -0.40354 | 0.0032639 | 0.000818
84 | 0.9849 | -0.28882 | 0.0068937 | 0.0017277
85 | 0.98501 | -0.28651 | 0 | 0
86 | 0.98459 | -0.29477 | 0 | 0
87 | 0.98562 | -0.27476 | 0 | 0
88 | 0.9845 | -0.29656 | 0.0043357 | 0.0010866
89 | 0.98445 | -0.29761 | 0.0039721 | 0.00099549
90 | 0.98458 | -0.29504 | 0.0044514 | 0.0011156
91 | 0.98418 | -0.30257 | 0 | 0
92 | 0.98586 | -0.27014 | 0.005172 | 0.0012962
93 | 0.98403 | -0.30562 | 0.0043191 | 0.0010825
94 | 0.98413 | -0.3036 | 0.0018157 | 0.00045506
95 | 0.98326 | -0.32045 | 0.0057587 | 0.0014433
96 | 0.98664 | -0.25505 | 0.0021181 | 0.00053085
97 | 0.98367 | -0.31269 | 0.0029562 | 0.0007409
98 | 0.98175 | -0.3498 | 0.0063514 | 0.0015918
99 | 0.98199 | -0.34508 | 0 | 0
100 | 0.98029 | -0.37818 | 0 | 0
101 | 0.98259 | -0.3334 | 0 | 0
102 | 0.98388 | -0.30841 | 0 | 0
103 | 0.98373 | -0.31129 | 0.0021162 | 0.00053036
104 | 0.97914 | -0.40079 | 0.016327 | 0.004092
105 | 0.97951 | -0.39346 | 0 | 0
106 | 0.98024 | -0.37911 | 0.003048 | 0.00076389
107 | 0.98226 | -0.33998 | 0.0070253 | 0.0017607
108 | 0.98351 | -0.31567 | 0.0012416 | 0.00031116
109 | 0.98209 | -0.34328 | 0.00812 | 0.0020351
110 | 0.98343 | -0.31721 | 0.0021165 | 0.00053045
111 | 0.99623 | -0.071193 | 0.0020832 | 0.00052209
112 | 0.995 | -0.09472 | 0.0011078 | 0.00027763
113 | 0.99488 | -0.096987 | 0.0015998 | 0.00040094
114 | 0.99381 | -0.11722 | 0 | 0
115 | 0.99291 | -0.13445 | 0.0022428 | 0.00056211
116 | 0.99262 | -0.14009 | 0.0023899 | 0.00059896
117 | 0.99172 | -0.15724 | 0.0043182 | 0.0010823
118 | 0.98354 | -0.31521 | 0.0039689 | 0.0009947
119 | 0.98297 | -0.32651 | 0.0023879 | 0.00059848
120 | 0.98332 | -0.31932 | 0.0012529 | 0.00031402
121 | 0.98326 | -0.32064 | 0.0020039 | 0.00050224
122 | 0.98319 | -0.32186 | 0.0046281 | 0.0011599
123 | 0.98918 | -0.20594 | 0.0015105 | 0.00037857
124 | 0.98887 | -0.21191 | 0 | 0
125 | 0.9905 | -0.18057 | 0 | 0
126 | 0.98802 | -0.22838 | 0.0023903 | 0.00059907
127 | 0.98839 | -0.22131 | 0.002136 | 0.00053533
128 | 0.99134 | -0.16452 | 0.0022447 | 0.00056256
129 | 0.98759 | -0.23669 | 0.0019967 | 0.00050041
130 | 0.98811 | -0.22675 | 0.0027805 | 0.00069686
131 | 0.99174 | -0.15691 | 0.0026244 | 0.00065773
132 | 0.99178 | -0.15604 | 0 | 0
133 | 0.98809 | -0.22715 | 0.00092652 | 0.00023221
134 | 0.98871 | -0.21501 | 0 | 0
135 | 0.9889 | -0.21123 | 0.0033837 | 0.00084804
136 | 0.98852 | -0.21869 | 0.0017348 | 0.00043477
137 | 0.98831 | -0.22273 | 0.0020559 | 0.00051527
138 | 0.98817 | -0.22545 | 0.0014794 | 0.00037077
139 | 0.98786 | -0.2315 | 0.012153 | 0.0030458
140 | 0.98277 | -0.33029 | 0.0033098 | 0.00082951
141 | 0.98278 | -0.33024 | 0.0035869 | 0.00089897
142 | 0.98291 | -0.32754 | 0.0022255 | 0.00055777
143 | 0.98776 | -0.23348 | 0 | 0
144 | 0.98737 | -0.24107 | 0.0028086 | 0.00070391
145 | 0.98727 | -0.24305 | 0.0022404 | 0.00056151
146 | 0.98274 | -0.33102 | 0.0053414 | 0.0013387
147 | 0.98698 | -0.24871 | 0 | 0
148 | 0.98584 | -0.27007 | 0.0038938 | 0.00097589
149 | 0.98667 | -0.25476 | 0.0025298 | 0.00063403
150 | 0.98683 | -0.25166 | 0.0031759 | 0.00079594
151 | 0.98653 | -0.2574 | 0 | 0
152 | 0.98629 | -0.26215 | 0 | 0
153 | 0.98619 | -0.26415 | 0.0048315 | 0.0012109
154 | 0.9863 | -0.26194 | 0.0041352 | 0.0010364
155 | 0.98651 | -0.25781 | 0.00057287 | 0.00014357
156 | 0.98646 | -0.25892 | 0.0011778 | 0.00029518
157 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0019587 | 0.00049086 | -0.0019587 | -0.0004909 | 1.2144e-08 | -3.6672e-08 | 0.0030019 | 0.0030019 | 0.0030019 | 0.97092 | -0.5614 | 0.97091 | -0.56153 | 0.8247
1 | -0.003457 | -0.00086638 | 0.0034572 | 0.00086629 | 1.5038e-07 | -8.0447e-08 | 0.0052982 | 0.0052981 | 0.0052982 | 0.97092 | -0.5614 | 0.97097 | -0.56049 | 1.4555
2 | -0.006368 | -0.0015953 | 0.0063693 | 0.0015957 | 1.276e-06 | 3.7463e-07 | 0.0097588 | 0.0097587 | 0.0097588 | 0.97097 | -0.56049 | 0.97118 | -0.55628 | 2.681
3 | 0.0029108 | 0.00072902 | -0.0029108 | -0.0007291 | 8.2184e-08 | -8.3625e-08 | 0.0044607 | 0.0044608 | 0.0044608 | 0.97097 | -0.56049 | 0.97094 | -0.56108 | 1.2255
4 | -0.022418 | -0.0056195 | 0.022445 | 0.005636 | 2.7026e-05 | 1.654e-05 | 0.034349 | 0.034349 | 0.034349 | 0.97118 | -0.55628 | 0.97246 | -0.53101 | 9.4365
5 | 0.016049 | 0.0040238 | -0.016045 | -0.0040218 | 3.4629e-06 | 2.0274e-06 | 0.02459 | 0.02459 | 0.02459 | 0.97118 | -0.55628 | 0.97095 | -0.56081 | 6.7556
6 | 0.0029108 | 0.0007291 | -0.0029105 | -0.00072932 | 2.1777e-07 | -2.2153e-07 | 0.0044608 | 0.0044609 | 0.0044609 | 0.97094 | -0.56108 | 0.97086 | -0.56265 | 1.2255
7 | -0.025473 | -0.0063938 | 0.025487 | 0.0064024 | 1.3927e-05 | 8.6063e-06 | 0.038868 | 0.038868 | 0.038868 | 0.9753 | -0.47507 | 0.97588 | -0.46361 | 10.678
8 | 0.022686 | 0.0056953 | -0.022674 | -0.0056877 | 1.2391e-05 | 7.586e-06 | 0.034616 | 0.034616 | 0.034616 | 0.9753 | -0.47507 | 0.97472 | -0.48652 | 9.5099
9 | 0.038524 | 0.0097095 | -0.03847 | -0.0096752 | 5.454e-05 | 3.438e-05 | 0.058761 | 0.058762 | 0.058762 | 0.97588 | -0.46361 | 0.97437 | -0.49325 | 16.1433
10 | -0.067202 | -0.016912 | 0.067242 | 0.016937 | 3.953e-05 | 2.5174e-05 | 0.10249 | 0.10249 | 0.10249 | 0.97588 | -0.46361 | 0.97651 | -0.45131 | 28.1579
11 | 0.020009 | 0.0050199 | -0.019999 | -0.0050138 | 1.003e-05 | 6.0623e-06 | 0.030548 | 0.030548 | 0.030548 | 0.97472 | -0.48652 | 0.97418 | -0.49704 | 8.3923
12 | -0.033108 | -0.0083084 | 0.033135 | 0.0083257 | 2.7571e-05 | 1.729e-05 | 0.050664 | 0.050664 | 0.050664 | 0.97246 | -0.53101 | 0.97334 | -0.51356 | 13.9186
13 | 0.010662 | 0.0026724 | -0.010661 | -0.0026716 | 1.6679e-06 | 8.6017e-07 | 0.016315 | 0.016315 | 0.016315 | 0.97246 | -0.53101 | 0.97229 | -0.5343 | 4.4822
14 | 0.012845 | 0.0032196 | -0.012844 | -0.0032191 | 7.8962e-07 | 4.3816e-07 | 0.019685 | 0.019685 | 0.019685 | 0.97095 | -0.56081 | 0.97088 | -0.5621 | 5.408
15 | 0.0015783 | 0.00039544 | -0.0015783 | -0.00039556 | 2.4058e-08 | -1.2016e-07 | 0.0024191 | 0.0024191 | 0.0024191 | 0.97086 | -0.56265 | 0.97084 | -0.56297 | 0.66459
16 | -0.033135 | -0.0083257 | 0.033153 | 0.0083372 | 1.8304e-05 | 1.1478e-05 | 0.050664 | 0.050664 | 0.050664 | 0.97334 | -0.51356 | 0.97393 | -0.502 | 13.9186
17 | 0.0079297 | 0.0019871 | -0.0079296 | -0.0019871 | 1.1287e-07 | 4.689e-08 | 0.012136 | 0.012136 | 0.012136 | 0.97229 | -0.5343 | 0.97228 | -0.53459 | 3.334
18 | 0.010048 | 0.0025184 | -0.010047 | -0.0025178 | 1.1916e-06 | 5.9693e-07 | 0.0154 | 0.0154 | 0.0154 | 0.97088 | -0.5621 | 0.97076 | -0.56459 | 4.2307
19 | 0.083028 | 0.021007 | -0.082859 | -0.020899 | 0.0001694 | 0.00010806 | 0.1261 | 0.1261 | 0.1261 | 0.9803 | -0.37714 | 0.97812 | -0.41975 | 34.6432
20 | -0.085598 | -0.021651 | 0.085824 | 0.021795 | 0.00022596 | 0.00014417 | 0.13 | 0.13 | 0.13 | 0.9803 | -0.37714 | 0.98313 | -0.32227 | 35.7149
21 | 0.080243 | 0.020243 | -0.080122 | -0.020166 | 0.00012106 | 7.7207e-05 | 0.12212 | 0.12212 | 0.12212 | 0.97812 | -0.41975 | 0.97651 | -0.45131 | 33.5499
22 | -0.085824 | -0.021795 | 0.085953 | 0.021877 | 0.00012857 | 8.2026e-05 | 0.13 | 0.13 | 0.13 | 0.98313 | -0.32227 | 0.98474 | -0.29119 | 35.7149
23 | 0.01288 | 0.0032293 | -0.012876 | -0.0032273 | 3.5785e-06 | 1.9805e-06 | 0.019627 | 0.019627 | 0.019627 | 0.97651 | -0.45131 | 0.97621 | -0.45714 | 5.392
24 | -0.088042 | -0.022401 | 0.088151 | 0.022471 | 0.00010909 | 6.9607e-05 | 0.13316 | 0.13316 | 0.13316 | 0.98474 | -0.29119 | 0.98607 | -0.26552 | 36.5821
25 | 0.010415 | 0.0026104 | -0.010413 | -0.0026095 | 1.7281e-06 | 8.774e-07 | 0.015875 | 0.015875 | 0.015875 | 0.97621 | -0.45714 | 0.97603 | -0.46062 | 4.3612
26 | -0.034687 | -0.0087214 | 0.034697 | 0.008728 | 1.038e-05 | 6.5203e-06 | 0.053006 | 0.053006 | 0.053006 | 0.97393 | -0.502 | 0.97425 | -0.49573 | 14.5621
27 | -0.094952 | -0.024175 | 0.095232 | 0.024354 | 0.00027987 | 0.00017865 | 0.14342 | 0.14342 | 0.14342 | 0.98607 | -0.26552 | 0.98925 | -0.20459 | 39.4015
28 | 0.0068007 | 0.0017043 | -0.0067997 | -0.001704 | 1.0046e-06 | 3.1851e-07 | 0.010262 | 0.010263 | 0.010263 | 0.98607 | -0.26552 | 0.98591 | -0.26862 | 2.8194
29 | 0.035469 | 0.008923 | -0.035465 | -0.0089204 | 4.2161e-06 | 2.6506e-06 | 0.054179 | 0.054179 | 0.054179 | 0.97437 | -0.49325 | 0.97425 | -0.49573 | 14.8843
30 | 0.0081383 | 0.0020395 | -0.0081377 | -0.0020392 | 6.7317e-07 | 2.851e-07 | 0.012407 | 0.012407 | 0.012407 | 0.97603 | -0.46062 | 0.97595 | -0.46236 | 3.4086
31 | -0.11606 | -0.029581 | 0.11633 | 0.02975 | 0.0002659 | 0.00016988 | 0.17475 | 0.17475 | 0.17475 | 0.98925 | -0.20459 | 0.99172 | -0.15724 | 48.009
32 | 0.020828 | 0.005227 | -0.020821 | -0.005223 | 6.5924e-06 | 3.9893e-06 | 0.031332 | 0.031332 | 0.031332 | 0.98925 | -0.20459 | 0.9889 | -0.21123 | 8.6076
33 | 0.0038941 | 0.0009758 | -0.0038938 | -0.00097589 | 2.6943e-07 | -9.2789e-08 | 0.0058773 | 0.0058773 | 0.0058773 | 0.98591 | -0.26862 | 0.98584 | -0.27007 | 1.6147
34 | -0.0095611 | -0.0023961 | 0.0095619 | 0.0023965 | 7.1842e-07 | 3.4815e-07 | 0.014611 | 0.014611 | 0.014611 | 0.97373 | -0.50599 | 0.97381 | -0.50441 | 4.014
35 | 0.0040405 | 0.0010125 | -0.0040403 | -0.0010126 | 2.1247e-07 | -4.887e-08 | 0.0061745 | 0.0061746 | 0.0061746 | 0.97373 | -0.50599 | 0.97367 | -0.50709 | 1.6963
36 | -0.012382 | -0.0031032 | 0.012385 | 0.0031048 | 2.7618e-06 | 1.5115e-06 | 0.01892 | 0.01892 | 0.01892 | 0.97381 | -0.50441 | 0.97405 | -0.49973 | 5.1978
37 | -0.01579 | -0.0039583 | 0.015792 | 0.0039595 | 2.0197e-06 | 1.1774e-06 | 0.024123 | 0.024123 | 0.024123 | 0.97405 | -0.49973 | 0.97418 | -0.49704 | 6.6271
38 | -0.0035748 | -0.00089592 | 0.0035753 | 0.0008957 | 4.901e-07 | -2.2397e-07 | 0.0054811 | 0.0054809 | 0.0054811 | 0.97049 | -0.57084 | 0.97063 | -0.56796 | 1.5058
39 | -0.0046002 | -0.0011526 | 0.0046006 | 0.0011526 | 3.0763e-07 | -7.0088e-09 | 0.0070522 | 0.0070522 | 0.0070522 | 0.97063 | -0.56796 | 0.9707 | -0.56656 | 1.9374
40 | -0.0096406 | -0.0024157 | 0.0096423 | 0.0024166 | 1.7503e-06 | 8.5595e-07 | 0.014778 | 0.014778 | 0.014778 | 0.9707 | -0.56656 | 0.9709 | -0.56275 | 4.0599
41 | -0.012678 | -0.0031775 | 0.012679 | 0.0031776 | 2.2203e-07 | 1.227e-07 | 0.019431 | 0.019431 | 0.019431 | 0.9709 | -0.56275 | 0.97091 | -0.56238 | 5.3383
42 | 0.0015015 | 0.00037631 | -0.0015015 | -0.00037632 | 1.0157e-09 | -5.7087e-09 | 0.0022983 | 0.0022983 | 0.0022983 | 0.97214 | -0.53735 | 0.97214 | -0.53736 | 0.63141
43 | -0.0039892 | -0.00099977 | 0.0039897 | 0.00099964 | 5.2371e-07 | -1.2931e-07 | 0.0061061 | 0.0061059 | 0.0061061 | 0.97214 | -0.53735 | 0.97228 | -0.53459 | 1.6775
44 | 0.0031464 | 0.00078843 | -0.0031463 | -0.00078854 | 1.3973e-07 | -1.0861e-07 | 0.0048229 | 0.004823 | 0.004823 | 0.97076 | -0.56459 | 0.97071 | -0.56552 | 1.325
45 | -0.15375 | -0.039295 | 0.15386 | 0.039365 | 0.00011181 | 7.0388e-05 | 0.23013 | 0.23013 | 0.23013 | 0.99529 | -0.089248 | 0.99608 | -0.074224 | 15.8056
46 | 0.15153 | 0.038738 | -0.15151 | -0.038731 | 1.1963e-05 | 7.5272e-06 | 0.22681 | 0.22681 | 0.22681 | 0.99529 | -0.089248 | 0.99521 | -0.09088 | 15.5776
47 | -0.15717 | -0.040194 | 0.1573 | 0.040278 | 0.00013235 | 8.3371e-05 | 0.23507 | 0.23507 | 0.23507 | 0.99608 | -0.074224 | 0.997 | -0.056838 | 16.1451
48 | 0.0033088 | 0.00082907 | -0.0033086 | -0.00082922 | 1.9561e-07 | -1.5269e-07 | 0.0049429 | 0.004943 | 0.004943 | 0.99608 | -0.074224 | 0.99602 | -0.075465 | 1.358
49 | 0.1482 | 0.037901 | -0.14808 | -0.037824 | 0.00012221 | 7.6839e-05 | 0.22186 | 0.22186 | 0.22186 | 0.99521 | -0.09088 | 0.99431 | -0.10794 | 15.2376
50 | 0.0033114 | 0.00082974 | -0.0033112 | -0.00082986 | 1.6589e-07 | -1.2831e-07 | 0.004951 | 0.0049511 | 0.0049511 | 0.99521 | -0.09088 | 0.99515 | -0.091932 | 1.3602
51 | -0.16888 | -0.04318 | 0.16896 | 0.043231 | 7.9746e-05 | 5.0341e-05 | 0.25236 | 0.25236 | 0.25236 | 0.997 | -0.056838 | 0.99751 | -0.047083 | 17.3323
52 | 0.14569 | 0.037225 | -0.14568 | -0.037217 | 1.2995e-05 | 8.1658e-06 | 0.21828 | 0.21828 | 0.21828 | 0.99431 | -0.10794 | 0.99421 | -0.10978 | 14.992
53 | -0.17382 | -0.044448 | 0.17394 | 0.044525 | 0.00012172 | 7.6895e-05 | 0.25961 | 0.25961 | 0.25961 | 0.99751 | -0.047083 | 0.99828 | -0.032622 | 17.83
54 | 0.13176 | 0.033727 | -0.13169 | -0.033687 | 6.3567e-05 | 3.9781e-05 | 0.19745 | 0.19745 | 0.19745 | 0.99421 | -0.10978 | 0.99369 | -0.11975 | 13.5612
55 | 0.013919 | 0.00349 | -0.013916 | -0.0034883 | 2.9099e-06 | 1.6305e-06 | 0.020832 | 0.020832 | 0.020832 | 0.99421 | -0.10978 | 0.99399 | -0.11417 | 5.7232
56 | 0.0056671 | 0.0014202 | -0.0056666 | -0.0014201 | 4.6092e-07 | 6.9805e-08 | 0.0084472 | 0.0084473 | 0.0084473 | 0.99828 | -0.032622 | 0.99819 | -0.034329 | 2.3207
57 | -0.17961 | -0.045945 | 0.17979 | 0.046059 | 0.00017933 | 0.00011338 | 0.26805 | 0.26805 | 0.26805 | 0.99828 | -0.032622 | 0.99936 | -0.012016 | 18.4102
58 | 0.12867 | 0.032929 | -0.12864 | -0.032912 | 2.6511e-05 | 1.6573e-05 | 0.19292 | 0.19292 | 0.19292 | 0.99369 | -0.11975 | 0.99346 | -0.124 | 13.2501
59 | 0.011045 | 0.002769 | -0.011042 | -0.0027675 | 2.8453e-06 | 1.4614e-06 | 0.016535 | 0.016535 | 0.016535 | 0.99399 | -0.11417 | 0.99371 | -0.11958 | 4.5427
60 | 0.0053904 | 0.0013507 | -0.0053901 | -0.0013506 | 2.8188e-07 | 4.1353e-08 | 0.0082186 | 0.0082187 | 0.0082187 | 0.97595 | -0.46236 | 0.97589 | -0.46346 | 2.2579
61 | 0.0027865 | 0.00069809 | -0.0027863 | -0.00069832 | 1.8411e-07 | -2.2196e-07 | 0.0042487 | 0.0042488 | 0.0042488 | 0.97589 | -0.46346 | 0.97582 | -0.46485 | 1.1673
62 | -0.0081729 | -0.0020482 | 0.0081736 | 0.0020485 | 6.5038e-07 | 2.6628e-07 | 0.012239 | 0.012239 | 0.012239 | 0.99362 | -0.12125 | 0.99371 | -0.11958 | 3.3625
63 | 0.0056727 | 0.0014216 | -0.0056723 | -0.0014215 | 4.2459e-07 | 6.8551e-08 | 0.0084953 | 0.0084954 | 0.0084954 | 0.99362 | -0.12125 | 0.99354 | -0.12282 | 2.3339
64 | 0.0039949 | 0.0010011 | -0.0039949 | -0.0010011 | 6.5797e-09 | -2.1362e-09 | 0.0059831 | 0.0059831 | 0.0059831 | 0.99354 | -0.12282 | 0.99354 | -0.12285 | 1.6437
65 | 0.0028523 | 0.00071477 | -0.0028522 | -0.00071483 | 5.0432e-08 | -6.3161e-08 | 0.0042718 | 0.0042718 | 0.0042718 | 0.99354 | -0.12285 | 0.99352 | -0.12322 | 1.1736
66 | 0.12625 | 0.032314 | -0.12619 | -0.032272 | 6.6703e-05 | 4.1662e-05 | 0.18934 | 0.18934 | 0.18934 | 0.99346 | -0.124 | 0.99289 | -0.13492 | 13.0043
67 | 0.12316 | 0.031514 | -0.12313 | -0.031495 | 3.0821e-05 | 1.9228e-05 | 0.18481 | 0.18481 | 0.18481 | 0.99289 | -0.13492 | 0.99262 | -0.14009 | 12.6933
68 | 0.18275 | 0.046843 | -0.18265 | -0.046776 | 0.00010639 | 6.7285e-05 | 0.27231 | 0.27231 | 0.27231 | 1 | 0 | 0.99936 | -0.012016 | 18.7027
69 | 0.26827 | 0.06897 | -0.26813 | -0.068881 | 0.00014098 | 8.9737e-05 | 0.39981 | 0.39981 | 0.39981 | 1 | 0 | 0.99943 | -0.010821 | 27.4594
70 | 0.26487 | 0.068063 | -0.26459 | -0.067885 | 0.00027923 | 0.00017771 | 0.39495 | 0.39495 | 0.39495 | 0.99943 | -0.010821 | 0.99828 | -0.032549 | 27.1257
71 | 0.2622 | 0.067286 | -0.26209 | -0.067218 | 0.00010772 | 6.8551e-05 | 0.39139 | 0.39139 | 0.39139 | 0.99828 | -0.032549 | 0.99783 | -0.04102 | 26.8811
72 | 0.0026075 | 0.0006534 | -0.0026074 | -0.00065348 | 4.7483e-08 | -7.9158e-08 | 0.003887 | 0.003887 | 0.003887 | 0.99819 | -0.034329 | 0.99817 | -0.034712 | 1.0679
73 | 0.25973 | 0.066625 | -0.2594 | -0.066419 | 0.00032433 | 0.00020637 | 0.38786 | 0.38786 | 0.38786 | 0.99783 | -0.04102 | 0.99647 | -0.066798 | 26.6391
74 | 0.258 | 0.066068 | -0.25795 | -0.066033 | 5.4922e-05 | 3.4945e-05 | 0.38577 | 0.38577 | 0.38577 | 0.99647 | -0.066798 | 0.99623 | -0.071193 | 26.4955
75 | 0.030027 | 0.0075351 | -0.030018 | -0.0075296 | 8.8488e-06 | 5.5248e-06 | 0.045963 | 0.045963 | 0.045963 | 0.97216 | -0.53765 | 0.97185 | -0.54383 | 12.6272
76 | -0.039365 | -0.0098755 | 0.039453 | 0.0099314 | 8.8654e-05 | 5.5929e-05 | 0.060256 | 0.060256 | 0.060256 | 0.97216 | -0.53765 | 0.97456 | -0.49052 | 16.5539
77 | 0.022611 | 0.0056733 | -0.022602 | -0.0056678 | 8.943e-06 | 5.4771e-06 | 0.034622 | 0.034622 | 0.034622 | 0.97185 | -0.54383 | 0.97143 | -0.55213 | 9.5116
78 | -0.050681 | -0.012745 | 0.05078 | 0.012808 | 9.9139e-05 | 6.2898e-05 | 0.077399 | 0.077399 | 0.077399 | 0.97456 | -0.49052 | 0.97664 | -0.44966 | 21.2636
79 | 0.022602 | 0.0056678 | -0.022597 | -0.0056646 | 5.2544e-06 | 3.2181e-06 | 0.034622 | 0.034622 | 0.034622 | 0.97143 | -0.55213 | 0.97119 | -0.55701 | 9.5116
80 | 0.01523 | 0.0038184 | -0.015226 | -0.0038161 | 3.8984e-06 | 2.2588e-06 | 0.023336 | 0.023336 | 0.023336 | 0.97119 | -0.55701 | 0.97091 | -0.56238 | 6.4109
81 | -0.070915 | -0.017854 | 0.071011 | 0.017915 | 9.5933e-05 | 6.0299e-05 | 0.10808 | 0.10808 | 0.10808 | 0.97664 | -0.44966 | 0.97808 | -0.4214 | 14.8456
82 | -0.082641 | -0.02083 | 0.082641 | 0.02083 | 3.8419e-07 | 2.3288e-07 | 0.12577 | 0.12577 | 0.12577 | 0.97808 | -0.4214 | 0.97808 | -0.4213 | 8.638
83 | -0.089383 | -0.02252 | 0.089417 | 0.02254 | 3.341e-05 | 2.0415e-05 | 0.13603 | 0.13603 | 0.13603 | 0.97808 | -0.4213 | 0.97848 | -0.41349 | 9.3425
84 | -0.089417 | -0.02254 | 0.089464 | 0.022568 | 4.6746e-05 | 2.8562e-05 | 0.13603 | 0.13603 | 0.13603 | 0.97848 | -0.41349 | 0.97904 | -0.40257 | 9.3424
85 | 0.003264 | 0.0008179 | -0.0032639 | -0.000818 | 1.5074e-07 | -1.0891e-07 | 0.0049608 | 0.0049609 | 0.0049609 | 0.97904 | -0.40257 | 0.97899 | -0.40354 | 1.3629
86 | -0.092728 | -0.023386 | 0.092768 | 0.023411 | 4.0454e-05 | 2.4798e-05 | 0.14099 | 0.14099 | 0.14099 | 0.97904 | -0.40257 | 0.97951 | -0.39346 | 9.6831
87 | -0.01532 | -0.0038397 | 0.015322 | 0.0038407 | 1.6864e-06 | 9.7246e-07 | 0.023146 | 0.023146 | 0.023146 | 0.9849 | -0.28882 | 0.98501 | -0.28651 | 6.3589
88 | 0.0084265 | 0.002112 | -0.0084241 | -0.002111 | 2.3876e-06 | 1.0283e-06 | 0.012731 | 0.012731 | 0.012731 | 0.9849 | -0.28882 | 0.98459 | -0.29477 | 3.4976
89 | -0.047803 | -0.011998 | 0.04783 | 0.012015 | 2.6818e-05 | 1.6989e-05 | 0.07222 | 0.07222 | 0.07222 | 0.98501 | -0.28651 | 0.98562 | -0.27476 | 19.8408
90 | 0.032481 | 0.0081578 | -0.032466 | -0.0081481 | 1.5561e-05 | 9.7397e-06 | 0.049074 | 0.049074 | 0.049074 | 0.98501 | -0.28651 | 0.9845 | -0.29656 | 13.4819
91 | 0.0039726 | 0.00099533 | -0.0039721 | -0.00099549 | 5.3718e-07 | -1.6156e-07 | 0.0060037 | 0.0060039 | 0.0060039 | 0.98459 | -0.29477 | 0.98445 | -0.29761 | 1.6494
92 | 0.0044515 | 0.0011156 | -0.0044514 | -0.0011156 | 5.683e-08 | -6.2128e-09 | 0.0067276 | 0.0067276 | 0.0067276 | 0.98459 | -0.29477 | 0.98458 | -0.29504 | 1.8482
93 | 0.15533 | 0.039374 | -0.15512 | -0.039243 | 0.00020728 | 0.00013062 | 0.23467 | 0.23467 | 0.23467 | 0.98562 | -0.27476 | 0.98418 | -0.30257 | 16.1174
94 | -0.20316 | -0.051389 | 0.20321 | 0.051418 | 4.5056e-05 | 2.8576e-05 | 0.30689 | 0.30689 | 0.30689 | 0.98562 | -0.27476 | 0.98586 | -0.27014 | 21.0775
95 | 0.02813 | 0.0070614 | -0.028118 | -0.0070539 | 1.2152e-05 | 7.5498e-06 | 0.042521 | 0.042521 | 0.042521 | 0.9845 | -0.29656 | 0.98403 | -0.30562 | 11.6816
96 | 0.015185 | 0.0038084 | -0.015184 | -0.0038079 | 7.5049e-07 | 4.3207e-07 | 0.02296 | 0.02296 | 0.02296 | 0.98418 | -0.30257 | 0.98413 | -0.3036 | 6.3077
97 | 0.13994 | 0.035435 | -0.13982 | -0.035359 | 0.00012008 | 7.5403e-05 | 0.21171 | 0.21171 | 0.21171 | 0.98418 | -0.30257 | 0.98326 | -0.32045 | 14.5405
98 | -0.20838 | -0.052714 | 0.20853 | 0.05281 | 0.00015093 | 9.5763e-05 | 0.31469 | 0.31469 | 0.31469 | 0.98586 | -0.27014 | 0.98664 | -0.25505 | 21.6137
99 | 0.023799 | 0.0059714 | -0.023791 | -0.0059665 | 8.0183e-06 | 4.9221e-06 | 0.03599 | 0.03599 | 0.03599 | 0.98403 | -0.30562 | 0.98367 | -0.31269 | 9.8874
100 | 0.013369 | 0.0033529 | -0.013366 | -0.0033512 | 3.0654e-06 | 1.7077e-06 | 0.020214 | 0.020215 | 0.020215 | 0.98413 | -0.3036 | 0.98388 | -0.30841 | 5.5534
101 | 0.13406 | 0.033916 | -0.13398 | -0.033864 | 8.32e-05 | 5.2156e-05 | 0.20299 | 0.203 | 0.203 | 0.98326 | -0.32045 | 0.98259 | -0.3334 | 13.942
102 | -0.21065 | -0.053341 | 0.21083 | 0.053458 | 0.00018589 | 0.00011797 | 0.31789 | 0.31789 | 0.31789 | 0.98664 | -0.25505 | 0.98759 | -0.23669 | 21.833
103 | 0.020835 | 0.0052256 | -0.020832 | -0.0052241 | 2.5007e-06 | 1.5153e-06 | 0.031518 | 0.031518 | 0.031518 | 0.98367 | -0.31269 | 0.98354 | -0.31521 | 8.6589
104 | -0.11873 | -0.030007 | 0.11876 | 0.030023 | 2.6884e-05 | 1.6759e-05 | 0.18005 | 0.18005 | 0.18005 | 0.98175 | -0.3498 | 0.98199 | -0.34508 | 12.3661
105 | 0.11238 | 0.028415 | -0.11223 | -0.02832 | 0.00015275 | 9.4926e-05 | 0.17042 | 0.17042 | 0.17042 | 0.98175 | -0.3498 | 0.98029 | -0.37818 | 11.705
106 | -0.11876 | -0.030023 | 0.11883 | 0.030065 | 6.6564e-05 | 4.1492e-05 | 0.18005 | 0.18005 | 0.18005 | 0.98199 | -0.34508 | 0.98259 | -0.3334 | 12.3661
107 | 0.0030481 | 0.00076377 | -0.003048 | -0.00076389 | 1.3495e-07 | -1.2556e-07 | 0.0046267 | 0.0046268 | 0.0046268 | 0.98029 | -0.37818 | 0.98024 | -0.37911 | 1.2711
108 | 0.10918 | 0.027556 | -0.1091 | -0.027506 | 7.9867e-05 | 4.9553e-05 | 0.1658 | 0.1658 | 0.1658 | 0.98029 | -0.37818 | 0.97951 | -0.39346 | 11.3873
109 | 0.015151 | 0.003799 | -0.015147 | -0.0037963 | 4.7538e-06 | 2.7376e-06 | 0.022945 | 0.022946 | 0.022946 | 0.98259 | -0.3334 | 0.98226 | -0.33998 | 6.3037
110 | 0.013366 | 0.0033512 | -0.013364 | -0.0033502 | 1.8312e-06 | 1.0202e-06 | 0.020215 | 0.020215 | 0.020215 | 0.98388 | -0.30841 | 0.98373 | -0.31129 | 5.5535
111 | 0.011248 | 0.0028198 | -0.011245 | -0.0028186 | 2.3475e-06 | 1.2279e-06 | 0.017014 | 0.017014 | 0.017014 | 0.98373 | -0.31129 | 0.98351 | -0.31567 | 4.6741
112 | -0.016327 | -0.004092 | 0.016333 | 0.0040953 | 5.7015e-06 | 3.3383e-06 | 0.024813 | 0.024813 | 0.024813 | 0.97914 | -0.40079 | 0.97951 | -0.39346 | 6.8167
113 | 0.0081212 | 0.0020356 | -0.00812 | -0.0020351 | 1.2764e-06 | 5.323e-07 | 0.012303 | 0.012303 | 0.012303 | 0.98226 | -0.33998 | 0.98209 | -0.34328 | 3.3799
114 | 0.010004 | 0.0025074 | -0.010003 | -0.002507 | 7.3454e-07 | 3.6161e-07 | 0.015135 | 0.015135 | 0.015135 | 0.98351 | -0.31567 | 0.98343 | -0.31721 | 4.1581
115 | 0.0078864 | 0.0019766 | -0.0078857 | -0.0019763 | 7.9232e-07 | 3.1884e-07 | 0.011933 | 0.011933 | 0.011933 | 0.98343 | -0.31721 | 0.98332 | -0.31932 | 3.2783
116 | 0.25587 | 0.065511 | -0.25557 | -0.065326 | 0.0002912 | 0.00018526 | 0.38266 | 0.38266 | 0.38266 | 0.99623 | -0.071193 | 0.995 | -0.09472 | 26.2819
117 | 0.25447 | 0.065048 | -0.25444 | -0.06503 | 2.7907e-05 | 1.7754e-05 | 0.38101 | 0.38101 | 0.38101 | 0.995 | -0.09472 | 0.99488 | -0.096987 | 26.1681
118 | 0.25284 | 0.064629 | -0.25259 | -0.064472 | 0.00024725 | 0.00015729 | 0.37861 | 0.37861 | 0.37861 | 0.99488 | -0.096987 | 0.99381 | -0.11722 | 26.0038
119 | 0.25259 | 0.064472 | -0.25238 | -0.064339 | 0.00021002 | 0.0001336 | 0.37861 | 0.37862 | 0.37862 | 0.99381 | -0.11722 | 0.99291 | -0.13445 | 26.0038
120 | 0.25014 | 0.063776 | -0.24988 | -0.063611 | 0.00026043 | 0.00016566 | 0.37525 | 0.37525 | 0.37525 | 0.99291 | -0.13445 | 0.99178 | -0.15604 | 25.773
121 | 0.12074 | 0.030896 | -0.12064 | -0.030833 | 0.00010015 | 6.3675e-05 | 0.18123 | 0.18123 | 0.18123 | 0.99262 | -0.14009 | 0.99172 | -0.15724 | 24.8945
122 | 0.016863 | 0.0042294 | -0.016854 | -0.004224 | 9.0822e-06 | 5.3407e-06 | 0.025514 | 0.025514 | 0.025514 | 0.98354 | -0.31521 | 0.98297 | -0.32651 | 7.0093
123 | 0.0053425 | 0.0013388 | -0.0053414 | -0.0013387 | 1.1467e-06 | 1.4142e-07 | 0.0080875 | 0.0080877 | 0.0080877 | 0.98297 | -0.32651 | 0.98274 | -0.33102 | 2.2219
124 | 0.0091236 | 0.0022868 | -0.0091232 | -0.0022865 | 4.4538e-07 | 2.0612e-07 | 0.013811 | 0.013811 | 0.013811 | 0.98297 | -0.32651 | 0.98291 | -0.32754 | 3.7944
125 | 0.0066327 | 0.0016623 | -0.0066323 | -0.0016621 | 4.1516e-07 | 1.2631e-07 | 0.010037 | 0.010037 | 0.010037 | 0.98332 | -0.31932 | 0.98326 | -0.32064 | 2.7574
126 | 0.0046283 | 0.0011599 | -0.0046281 | -0.0011599 | 2.6952e-07 | -1.3306e-08 | 0.0070043 | 0.0070044 | 0.0070044 | 0.98326 | -0.32064 | 0.98319 | -0.32186 | 1.9243
127 | 0.24291 | 0.061637 | -0.24284 | -0.061593 | 6.9711e-05 | 4.4329e-05 | 0.36568 | 0.36568 | 0.36568 | 0.98918 | -0.20594 | 0.98887 | -0.21191 | 25.1151
128 | -0.24442 | -0.062016 | 0.24472 | 0.062206 | 0.00029863 | 0.00018991 | 0.36795 | 0.36795 | 0.36795 | 0.98918 | -0.20594 | 0.9905 | -0.18057 | 25.2712
129 | 0.21548 | 0.05472 | -0.21531 | -0.054612 | 0.00017065 | 0.00010833 | 0.3245 | 0.3245 | 0.3245 | 0.98887 | -0.21191 | 0.98802 | -0.22838 | 22.2869
130 | 0.027363 | 0.0068729 | -0.027351 | -0.0068653 | 1.2271e-05 | 7.6061e-06 | 0.04118 | 0.04118 | 0.04118 | 0.98887 | -0.21191 | 0.98839 | -0.22131 | 11.3132
131 | -0.24472 | -0.062206 | 0.24491 | 0.062326 | 0.00018931 | 0.00012039 | 0.36795 | 0.36795 | 0.36795 | 0.9905 | -0.18057 | 0.99134 | -0.16452 | 25.2712
132 | 0.21292 | 0.054013 | -0.21283 | -0.053959 | 8.5053e-05 | 5.3983e-05 | 0.3209 | 0.3209 | 0.3209 | 0.98802 | -0.22838 | 0.98759 | -0.23669 | 22.0396
133 | 0.025215 | 0.0063299 | -0.025208 | -0.0063259 | 6.5361e-06 | 4.0281e-06 | 0.037964 | 0.037964 | 0.037964 | 0.98839 | -0.22131 | 0.98811 | -0.22675 | 10.4298
134 | -0.24715 | -0.062889 | 0.24725 | 0.062953 | 0.0001011 | 6.4299e-05 | 0.37132 | 0.37132 | 0.37132 | 0.99134 | -0.16452 | 0.99178 | -0.15604 | 25.5025
135 | 0.022428 | 0.0056291 | -0.022427 | -0.0056288 | 4.252e-07 | 2.594e-07 | 0.033777 | 0.033777 | 0.033777 | 0.98811 | -0.22675 | 0.98809 | -0.22715 | 9.2794
136 | -0.0026244 | -0.00065773 | 0.0026245 | 0.00065756 | 1.0869e-07 | -1.7167e-07 | 0.0039376 | 0.0039376 | 0.0039376 | 0.99174 | -0.15691 | 0.99178 | -0.15604 | 1.0818
137 | 0.021501 | 0.0053966 | -0.021494 | -0.0053926 | 6.497e-06 | 3.9465e-06 | 0.032382 | 0.032382 | 0.032382 | 0.98809 | -0.22715 | 0.98776 | -0.23348 | 8.8961
138 | -0.017434 | -0.0043731 | 0.017438 | 0.0043749 | 3.1391e-06 | 1.8531e-06 | 0.02624 | 0.02624 | 0.02624 | 0.98871 | -0.21501 | 0.9889 | -0.21123 | 7.2089
139 | 0.017434 | 0.0043731 | -0.017431 | -0.0043713 | 3.059e-06 | 1.8059e-06 | 0.02624 | 0.02624 | 0.02624 | 0.98871 | -0.21501 | 0.98852 | -0.21869 | 7.2089
140 | 0.015697 | 0.0039365 | -0.015694 | -0.0039348 | 3.0249e-06 | 1.7508e-06 | 0.023629 | 0.023629 | 0.023629 | 0.98852 | -0.21869 | 0.98831 | -0.22273 | 6.4915
141 | 0.013638 | 0.0034195 | -0.013636 | -0.0034185 | 1.765e-06 | 9.8658e-07 | 0.020534 | 0.020534 | 0.020534 | 0.98831 | -0.22273 | 0.98817 | -0.22545 | 5.6411
142 | 0.012157 | 0.0030477 | -0.012153 | -0.0030458 | 3.5061e-06 | 1.8866e-06 | 0.018306 | 0.018306 | 0.018306 | 0.98817 | -0.22545 | 0.98786 | -0.2315 | 5.0292
143 | -0.0033098 | -0.00082951 | 0.0033098 | 0.00082951 | 8.2818e-09 | -5.8425e-09 | 0.0050114 | 0.0050114 | 0.0050114 | 0.98277 | -0.33029 | 0.98278 | -0.33024 | 1.3767
144 | -0.0068967 | -0.0017285 | 0.0068976 | 0.0017288 | 8.8721e-07 | 2.9284e-07 | 0.010442 | 0.010442 | 0.010442 | 0.98278 | -0.33024 | 0.98291 | -0.32754 | 2.8688
145 | 0.021494 | 0.0053926 | -0.021486 | -0.0053879 | 7.772e-06 | 4.7212e-06 | 0.032382 | 0.032382 | 0.032382 | 0.98776 | -0.23348 | 0.98737 | -0.24107 | 8.8962
146 | 0.018678 | 0.004684 | -0.018676 | -0.004683 | 1.7632e-06 | 1.0526e-06 | 0.028149 | 0.028149 | 0.028149 | 0.98737 | -0.24107 | 0.98727 | -0.24305 | 7.7333
147 | 0.016436 | 0.0041214 | -0.016431 | -0.0041189 | 4.4312e-06 | 2.5898e-06 | 0.024773 | 0.024773 | 0.024773 | 0.98727 | -0.24305 | 0.98698 | -0.24871 | 6.8057
148 | 0.013255 | 0.0033233 | -0.013251 | -0.0033212 | 3.8228e-06 | 2.1205e-06 | 0.019984 | 0.019984 | 0.019984 | 0.98698 | -0.24871 | 0.98667 | -0.25476 | 5.4902
149 | 0.0031763 | 0.00079557 | -0.0031759 | -0.00079594 | 4.4658e-07 | -3.7777e-07 | 0.0047886 | 0.0047888 | 0.0047888 | 0.98698 | -0.24871 | 0.98683 | -0.25166 | 1.3156
150 | 0.010721 | 0.0026871 | -0.01072 | -0.0026865 | 1.3457e-06 | 6.8598e-07 | 0.016169 | 0.016169 | 0.016169 | 0.98667 | -0.25476 | 0.98653 | -0.2574 | 4.442
151 | 0.00057288 | 0.00014307 | -0.00057287 | -0.00014357 | 1.1195e-08 | -5.0343e-07 | 0.00086391 | 0.00086409 | 0.00086409 | 0.98653 | -0.2574 | 0.98651 | -0.25781 | 0.23739
152 | 0.010147 | 0.0025434 | -0.010146 | -0.002543 | 7.3258e-07 | 3.6238e-07 | 0.015305 | 0.015305 | 0.015305 | 0.98653 | -0.2574 | 0.98646 | -0.25892 | 4.2047
153 | 0.0048319 | 0.0012109 | -0.0048315 | -0.0012109 | 4.5991e-07 | -1.4842e-10 | 0.0072899 | 0.00729 | 0.00729 | 0.98629 | -0.26215 | 0.98619 | -0.26415 | 2.0027
154 | -0.0048319 | -0.0012109 | 0.004832 | 0.0012109 | 4.9892e-08 | -2.0263e-11 | 0.0072899 | 0.0072899 | 0.0072899 | 0.98629 | -0.26215 | 0.9863 | -0.26194 | 2.0027
155 | -0.0089672 | -0.0022473 | 0.0089685 | 0.0022478 | 1.2911e-06 | 5.8616e-07 | 0.013529 | 0.013529 | 0.013529 | 0.9863 | -0.26194 | 0.98646 | -0.25892 | 3.7166

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.45594 | 0.11663

## res_load
| p_mw | q_mvar
0 | 0.0014983 | 0.00037551
1 | 0.0019587 | 0.0004909
2 | 0.002787 | 0.00069848
3 | 0.003191 | 0.00079974
4 | 0.0026647 | 0.00066784
5 | 0.0032008 | 0.0008022
6 | 0.0013322 | 0.00033388
7 | 0.0027309 | 0.00068444
8 | 0.002796 | 0.00070074
9 | 0.0015783 | 0.00039556
10 | 0.00257 | 0.00064411
11 | 0.0026162 | 0.00065567
12 | 0.0020892 | 0.00052361
13 | 0.0024616 | 0.00061693
14 | 0.0015332 | 0.00038424
15 | 0.0030009 | 0.0007521
16 | 0.0022745 | 0.00057004
17 | 0.00076781 | 0.00019243
18 | 0.0029056 | 0.0007282
19 | 0.0055206 | 0.0013836
20 | 0.00282 | 0.00070675
21 | 0.0040403 | 0.0010126
22 | 0.0034058 | 0.00085359
23 | 0.0042066 | 0.0010543
24 | 0.0035748 | 0.00089592
25 | 0.001025 | 0.00025688
26 | 0.00504 | 0.0012631
27 | 0.0030362 | 0.00076093
28 | 0.0024876 | 0.00062346
29 | 0.0015015 | 0.00037632
30 | 0.0039399 | 0.00098744
31 | 0.0069002 | 0.0017294
32 | 0.0031463 | 0.00078854
33 | 0.0022207 | 0.00055656
34 | 0.011583 | 0.0029029
35 | 0.0033086 | 0.00082922
36 | 0.0023899 | 0.00059896
37 | 0.0033112 | 0.00082986
38 | 0.0048582 | 0.0012176
39 | 0.0030249 | 0.00075811
40 | 0.0028704 | 0.0007194
41 | 0.0027472 | 0.00068852
42 | 0.0026036 | 0.00065253
43 | 0.0027863 | 0.00069832
44 | 0.0025002 | 0.00062661
45 | 0.0028689 | 0.00071901
46 | 0.0016774 | 0.00042039
47 | 0.0011426 | 0.00028637
48 | 0.0028522 | 0.00071483
49 | 0.0023899 | 0.00059896
50 | 0.003022 | 0.00075739
51 | 0.0032611 | 0.00081731
52 | 0.0028606 | 0.00071695
53 | 0.0032636 | 0.00081792
54 | 0.0023893 | 0.00059882
55 | 0.0030591 | 0.00076669
56 | 0.0023638 | 0.00059242
57 | 0.0026074 | 0.00065348
58 | 0.0013997 | 0.00035079
59 | 0.0093381 | 0.0023404
60 | 0.0074069 | 0.0018563
61 | 0.011228 | 0.002814
62 | 0.0073664 | 0.0018462
63 | 0.020134 | 0.0050462
64 | 0.0025476 | 0.0006385
65 | 0.01163 | 0.0029147
66 | 0.0067423 | 0.0016898
67 | 0.0032639 | 0.000818
68 | 0.0068937 | 0.0017277
69 | 0.0043357 | 0.0010866
70 | 0.0039721 | 0.00099549
71 | 0.0044514 | 0.0011156
72 | 0.005172 | 0.0012962
73 | 0.0043191 | 0.0010825
74 | 0.0018157 | 0.00045506
75 | 0.0057587 | 0.0014433
76 | 0.0021181 | 0.00053085
77 | 0.0029562 | 0.0007409
78 | 0.0063514 | 0.0015918
79 | 0.0021162 | 0.00053036
80 | 0.016327 | 0.004092
81 | 0.003048 | 0.00076389
82 | 0.0070253 | 0.0017607
83 | 0.0012416 | 0.00031116
84 | 0.00812 | 0.0020351
85 | 0.0021165 | 0.00053045
86 | 0.0020832 | 0.00052209
87 | 0.0011078 | 0.00027763
88 | 0.0015998 | 0.00040094
89 | 0.0022428 | 0.00056211
90 | 0.0023899 | 0.00059896
91 | 0.0043182 | 0.0010823
92 | 0.0039689 | 0.0009947
93 | 0.0023879 | 0.00059848
94 | 0.0012529 | 0.00031402
95 | 0.0020039 | 0.00050224
96 | 0.0046281 | 0.0011599
97 | 0.0015105 | 0.00037857
98 | 0.0023903 | 0.00059907
99 | 0.002136 | 0.00053533
100 | 0.0022447 | 0.00056256
101 | 0.0019967 | 0.00050041
102 | 0.0027805 | 0.00069686
103 | 0.0026244 | 0.00065773
104 | 0.00092652 | 0.00023221
105 | 0.0033837 | 0.00084804
106 | 0.0017348 | 0.00043477
107 | 0.0020559 | 0.00051527
108 | 0.0014794 | 0.00037077
109 | 0.012153 | 0.0030458
110 | 0.0033098 | 0.00082951
111 | 0.0035869 | 0.00089897
112 | 0.0022255 | 0.00055777
113 | 0.0028086 | 0.00070391
114 | 0.0022404 | 0.00056151
115 | 0.0053414 | 0.0013387
116 | 0.0038938 | 0.00097589
117 | 0.0025298 | 0.00063403
118 | 0.0031759 | 0.00079594
119 | 0.0048315 | 0.0012109
120 | 0.0041352 | 0.0010364
121 | 0.00057287 | 0.00014357
122 | 0.0011778 | 0.00029518

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1