## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1709-23_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1709-23_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1709-23_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1709-23_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1709-23_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1709-23_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1709-23_0_4_node_124 | 0.4 | n |  | TRUE
7 | bus_LV_1709-23_0_4_node_83 | 0.4 | n |  | TRUE
8 | bus_LV_1709-23_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1709-23_0_4_node_127 | 0.4 | n |  | TRUE
10 | bus_LV_1709-23_0_4_node_125 | 0.4 | n |  | TRUE
11 | bus_LV_1709-23_0_4_node_81 | 0.4 | n |  | TRUE
12 | bus_LV_1709-23_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1709-23_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1709-23_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_1709-23_0_4_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1709-23_0_4_node_29 | 0.4 | n |  | TRUE
17 | bus_LV_1709-23_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1709-23_0_4_node_11 | 0.4 | n |  | TRUE
19 | bus_LV_1709-23_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1709-23_0_4_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_1709-23_0_4_node_40 | 0.4 | n |  | TRUE
22 | bus_LV_1709-23_0_4_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1709-23_0_4_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_1709-23_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_1709-23_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_1709-23_0_4_node_128 | 0.4 | n |  | TRUE
27 | bus_LV_1709-23_0_4_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_1709-23_0_4_node_54 | 0.4 | n |  | TRUE
29 | bus_LV_1709-23_0_4_node_17 | 0.4 | n |  | TRUE
30 | bus_LV_1709-23_0_4_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_1709-23_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_1709-23_0_4_node_34 | 0.4 | n |  | TRUE
33 | bus_LV_1709-23_0_4_node_20 | 0.4 | n |  | TRUE
34 | bus_LV_1709-23_0_4_node_130 | 0.4 | n |  | TRUE
35 | bus_LV_1709-23_0_4_node_131 | 0.4 | n |  | TRUE
36 | bus_LV_1709-23_0_4_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_1709-23_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_1709-23_0_4_node_22 | 0.4 | n |  | TRUE
39 | bus_LV_1709-23_0_4_node_23 | 0.4 | n |  | TRUE
40 | bus_LV_1709-23_0_4_node_24 | 0.4 | n |  | TRUE
41 | bus_LV_1709-23_0_4_node_25 | 0.4 | n |  | TRUE
42 | bus_LV_1709-23_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_1709-23_0_4_node_27 | 0.4 | n |  | TRUE
44 | bus_LV_1709-23_0_4_node_32 | 0.4 | n |  | TRUE
45 | bus_LV_1709-23_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_1709-23_0_4_node_55 | 0.4 | n |  | TRUE
47 | bus_LV_1709-23_0_4_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_1709-23_0_4_node_46 | 0.4 | n |  | TRUE
49 | bus_LV_1709-23_0_4_node_30 | 0.4 | n |  | TRUE
50 | bus_LV_1709-23_0_4_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_1709-23_0_4_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_1709-23_0_4_node_132 | 0.4 | n |  | TRUE
53 | bus_LV_1709-23_0_4_node_42 | 0.4 | n |  | TRUE
54 | bus_LV_1709-23_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_1709-23_0_4_node_36 | 0.4 | n |  | TRUE
56 | bus_LV_1709-23_0_4_node_37 | 0.4 | n |  | TRUE
57 | bus_LV_1709-23_0_4_node_38 | 0.4 | n |  | TRUE
58 | bus_LV_1709-23_0_4_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_1709-23_0_4_node_68 | 0.4 | n |  | TRUE
60 | bus_LV_1709-23_0_4_node_66 | 0.4 | n |  | TRUE
61 | bus_LV_1709-23_0_4_node_43 | 0.4 | n |  | TRUE
62 | bus_LV_1709-23_0_4_node_44 | 0.4 | n |  | TRUE
63 | bus_LV_1709-23_0_4_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_1709-23_0_4_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_1709-23_0_4_node_53 | 0.4 | n |  | TRUE
66 | bus_LV_1709-23_0_4_node_62 | 0.4 | n |  | TRUE
67 | bus_LV_1709-23_0_4_node_70 | 0.4 | n |  | TRUE
68 | bus_LV_1709-23_0_4_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_1709-23_0_4_node_114 | 0.4 | n |  | TRUE
70 | bus_LV_1709-23_0_4_node_115 | 0.4 | n |  | TRUE
71 | bus_LV_1709-23_0_4_node_116 | 0.4 | n |  | TRUE
72 | bus_LV_1709-23_0_4_node_113 | 0.4 | n |  | TRUE
73 | bus_LV_1709-23_0_4_node_59 | 0.4 | n |  | TRUE
74 | bus_LV_1709-23_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_1709-23_0_4_node_61 | 0.4 | n |  | TRUE
76 | bus_LV_1709-23_0_4_node_63 | 0.4 | n |  | TRUE
77 | bus_LV_1709-23_0_4_node_64 | 0.4 | n |  | TRUE
78 | bus_LV_1709-23_0_4_node_69 | 0.4 | n |  | TRUE
79 | bus_LV_1709-23_0_4_node_71 | 0.4 | n |  | TRUE
80 | bus_LV_1709-23_0_4_node_74 | 0.4 | n |  | TRUE
81 | bus_LV_1709-23_0_4_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_1709-23_0_4_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_1709-23_0_4_node_73 | 0.4 | n |  | TRUE
84 | bus_LV_1709-23_0_4_node_75 | 0.4 | n |  | TRUE
85 | bus_LV_1709-23_0_4_node_100 | 0.4 | n |  | TRUE
86 | bus_LV_1709-23_0_4_node_101 | 0.4 | n |  | TRUE
87 | bus_LV_1709-23_0_4_node_122 | 0.4 | n |  | TRUE
88 | bus_LV_1709-23_0_4_node_76 | 0.4 | n |  | TRUE
89 | bus_LV_1709-23_0_4_node_77 | 0.4 | n |  | TRUE
90 | bus_LV_1709-23_0_4_node_78 | 0.4 | n |  | TRUE
91 | bus_LV_1709-23_0_4_node_79 | 0.4 | n |  | TRUE
92 | bus_LV_1709-23_0_4_node_82 | 0.4 | n |  | TRUE
93 | bus_LV_1709-23_0_4_node_84 | 0.4 | n |  | TRUE
94 | bus_LV_1709-23_0_4_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_1709-23_0_4_node_109 | 0.4 | n |  | TRUE
96 | bus_LV_1709-23_0_4_node_108 | 0.4 | n |  | TRUE
97 | bus_LV_1709-23_0_4_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_1709-23_0_4_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_1709-23_0_4_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_1709-23_0_4_node_88 | 0.4 | n |  | TRUE
101 | bus_LV_1709-23_0_4_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_1709-23_0_4_node_90 | 0.4 | n |  | TRUE
103 | bus_LV_1709-23_0_4_node_123 | 0.4 | n |  | TRUE
104 | bus_LV_1709-23_0_4_node_121 | 0.4 | n |  | TRUE
105 | bus_LV_1709-23_0_4_node_112 | 0.4 | n |  | TRUE
106 | bus_LV_1709-23_0_4_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_1709-23_0_4_node_99 | 0.4 | n |  | TRUE
108 | bus_LV_1709-23_0_4_node_120 | 0.4 | n |  | TRUE
109 | bus_LV_1709-23_0_4_node_117 | 0.4 | n |  | TRUE
110 | bus_LV_1709-23_0_4_node_111 | 0.4 | n |  | TRUE
111 | bus_LV_1709-23_0_4_node_91 | 0.4 | n |  | TRUE
112 | bus_LV_1709-23_0_4_node_92 | 0.4 | n |  | TRUE
113 | bus_LV_1709-23_0_4_node_93 | 0.4 | n |  | TRUE
114 | bus_LV_1709-23_0_4_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_1709-23_0_4_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_1709-23_0_4_node_105 | 0.4 | n |  | TRUE
117 | bus_LV_1709-23_0_4_node_104 | 0.4 | n |  | TRUE
118 | bus_LV_1709-23_0_4_node_106 | 0.4 | n |  | TRUE
119 | bus_LV_1709-23_0_4_node_103 | 0.4 | n |  | TRUE
120 | bus_LV_1709-23_0_4_node_97 | 0.4 | n |  | TRUE
121 | bus_LV_1709-23_0_4_node_98 | 0.4 | n |  | TRUE
122 | bus_LV_1709-23_0_4_node_102 | 0.4 | n |  | TRUE
123 | bus_LV_1709-23_0_4_node_107 | 0.4 | n |  | TRUE
124 | bus_LV_1709-23_0_4_node_118 | 0.4 | n |  | TRUE
125 | bus_LV_1709-23_0_4_node_119 | 0.4 | n |  | TRUE
126 | bus_LV_1709-23_0_4_node_126 | 0.4 | n |  | TRUE
127 | bus_MV_25_0_node_189 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1709-23_0_4_load_0 | 0 | 0.0082605 | 0.0020703 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1709-23_0_4_load_4 | 4 | 0.0019271 | 0.00048297 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1709-23_0_4_load_5 | 5 | 0.0094899 | 0.0023784 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1709-23_0_4_load_83 | 7 | 0.0033767 | 0.00084628 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1709-23_0_4_load_125 | 10 | 0.0033781 | 0.00084663 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1709-23_0_4_load_8 | 12 | 0.0056457 | 0.001415 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1709-23_0_4_load_31 | 14 | 0.0014107 | 0.00035357 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1709-23_0_4_load_28 | 15 | 0.0070609 | 0.0017696 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1709-23_0_4_load_29 | 16 | 0.0012292 | 0.00030807 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1709-23_0_4_load_10 | 17 | 0.0023886 | 0.00059864 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1709-23_0_4_load_11 | 18 | 0.0024858 | 0.00062301 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1709-23_0_4_load_12 | 19 | 0.0031198 | 0.00078188 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1709-23_0_4_load_39 | 20 | 0.0014333 | 0.00035922 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1709-23_0_4_load_13 | 22 | 0.0021267 | 0.00053301 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1709-23_0_4_load_14 | 23 | 0.0022785 | 0.00057105 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1709-23_0_4_load_15 | 24 | 0.0033352 | 0.00083589 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1709-23_0_4_load_16 | 25 | 0.0015389 | 0.00038569 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1709-23_0_4_load_128 | 26 | 0.0028928 | 0.000725 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1709-23_0_4_load_52 | 27 | 0.0011815 | 0.0002961 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1709-23_0_4_load_17 | 29 | 0.0020145 | 0.00050488 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1709-23_0_4_load_21 | 31 | 0.001477 | 0.00037017 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1709-23_0_4_load_20 | 33 | 0.0021241 | 0.00053235 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1709-23_0_4_load_130 | 34 | 0.0012901 | 0.00032333 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1709-23_0_4_load_131 | 35 | 0.0012896 | 0.0003232 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1709-23_0_4_load_35 | 36 | 0.0012023 | 0.00030133 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1709-23_0_4_load_33 | 37 | 0.0031485 | 0.00078908 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1709-23_0_4_load_22 | 38 | 0.0045228 | 0.0011335 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1709-23_0_4_load_23 | 39 | 0.0042855 | 0.001074 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1709-23_0_4_load_27 | 43 | 0.0011814 | 0.0002961 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1709-23_0_4_load_32 | 44 | 0.0025289 | 0.00063379 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1709-23_0_4_load_45 | 45 | 0.0041691 | 0.0010449 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1709-23_0_4_load_55 | 46 | 0.0015389 | 0.00038569 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1709-23_0_4_load_57 | 47 | 0.003273 | 0.00082028 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1709-23_0_4_load_30 | 49 | 0.0012428 | 0.00031148 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1709-23_0_4_load_49 | 50 | 0.0073712 | 0.0018474 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1709-23_0_4_load_50 | 51 | 0.0066633 | 0.00167 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1709-23_0_4_load_132 | 52 | 0.0013636 | 0.00034174 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1709-23_0_4_load_42 | 53 | 0.0017449 | 0.00043732 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1709-23_0_4_load_41 | 54 | 0.0014304 | 0.0003585 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1709-23_0_4_load_36 | 55 | 0.0022182 | 0.00055593 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1709-23_0_4_load_37 | 56 | 0.0020737 | 0.00051972 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1709-23_0_4_load_56 | 58 | 0.00098545 | 0.00024698 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1709-23_0_4_load_43 | 61 | 0.0023881 | 0.00059853 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1709-23_0_4_load_44 | 62 | 0.00253 | 0.00063407 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1709-23_0_4_load_47 | 63 | 0.0027779 | 0.00069622 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1709-23_0_4_load_48 | 64 | 0.0031665 | 0.0007936 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1709-23_0_4_load_53 | 65 | 0.0016892 | 0.00042337 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1709-23_0_4_load_70 | 67 | 0.011517 | 0.0028863 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1709-23_0_4_load_115 | 70 | 0.0014475 | 0.00036279 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1709-23_0_4_load_116 | 71 | 0.0013916 | 0.00034876 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1709-23_0_4_load_113 | 72 | 0.0070498 | 0.0017668 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1709-23_0_4_load_59 | 73 | 0.011433 | 0.0028653 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1709-23_0_4_load_64 | 77 | 0.0054909 | 0.0013762 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1709-23_0_4_load_71 | 79 | 0.0095597 | 0.0023959 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1709-23_0_4_load_74 | 80 | 0.0094517 | 0.0023688 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1709-23_0_4_load_65 | 81 | 0.0095599 | 0.0023959 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1709-23_0_4_load_72 | 82 | 0.0092139 | 0.0023092 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1709-23_0_4_load_73 | 83 | 0.0046472 | 0.0011647 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1709-23_0_4_load_122 | 87 | 0.010292 | 0.0025795 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1709-23_0_4_load_76 | 88 | 0.0020069 | 0.00050298 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1709-23_0_4_load_77 | 89 | 0.0028915 | 0.00072468 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1709-23_0_4_load_78 | 90 | 0.0035287 | 0.00088439 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1709-23_0_4_load_79 | 91 | 0.0024197 | 0.00060643 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1709-23_0_4_load_84 | 93 | 0.0046605 | 0.001168 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1709-23_0_4_load_80 | 94 | 0.002602 | 0.00065213 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1709-23_0_4_load_108 | 96 | 0.0081567 | 0.0020443 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1709-23_0_4_load_85 | 97 | 0.0022111 | 0.00055416 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1709-23_0_4_load_86 | 98 | 0.0020589 | 0.00051601 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1709-23_0_4_load_90 | 102 | 0.016426 | 0.0041168 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1709-23_0_4_load_123 | 103 | 0.01643 | 0.0041178 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1709-23_0_4_load_121 | 104 | 0.0027663 | 0.00069329 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1709-23_0_4_load_110 | 106 | 0.0031898 | 0.00079944 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1709-23_0_4_load_120 | 108 | 0.006539 | 0.0016388 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1709-23_0_4_load_117 | 109 | 0.0018763 | 0.00047026 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1709-23_0_4_load_111 | 110 | 0.0046464 | 0.0011645 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1709-23_0_4_load_91 | 111 | 0.0080663 | 0.0020216 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1709-23_0_4_load_92 | 112 | 0.0021602 | 0.0005414 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1709-23_0_4_load_93 | 113 | 0.0043488 | 0.0010899 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1709-23_0_4_load_94 | 114 | 0.0057845 | 0.0014497 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1709-23_0_4_load_95 | 115 | 0.0090161 | 0.0022597 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1709-23_0_4_load_105 | 116 | 0.0034716 | 0.00087006 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1709-23_0_4_load_104 | 117 | 0.0062189 | 0.0015586 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1709-23_0_4_load_106 | 118 | 0.0035159 | 0.00088117 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1709-23_0_4_load_103 | 119 | 0.011279 | 0.0028267 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1709-23_0_4_load_97 | 120 | 0.0036559 | 0.00091626 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1709-23_0_4_load_98 | 121 | 0.0071109 | 0.0017822 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1709-23_0_4_load_102 | 122 | 0.0051919 | 0.0013012 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1709-23_0_4_load_107 | 123 | 0.0038227 | 0.00095805 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1709-23_0_4_load_118 | 124 | 0.0060689 | 0.001521 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1709-23_0_4_load_119 | 125 | 0.0026265 | 0.00065827 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1709-23_0_4_load_126 | 126 | 0.0035469 | 0.00088895 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 86 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1709-23_0_4_line_0 |  | 0 | 1 | 0.019513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1709-23_0_4_line_1 |  | 0 | 2 | 0.012458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1709-23_0_4_line_2 |  | 1 | 3 | 0.005797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1709-23_0_4_line_3 |  | 1 | 4 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1709-23_0_4_line_4 |  | 2 | 5 | 0.026211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1709-23_0_4_line_5 |  | 3 | 6 | 0.003862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1709-23_0_4_line_6 |  | 3 | 7 | 0.017853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1709-23_0_4_line_7 |  | 4 | 8 | 0.022779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1709-23_0_4_line_8 |  | 6 | 9 | 0.030984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1709-23_0_4_line_9 |  | 6 | 10 | 0.017163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1709-23_0_4_line_10 |  | 7 | 11 | 0.055201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1709-23_0_4_line_11 |  | 8 | 12 | 0.018467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1709-23_0_4_line_12 |  | 8 | 13 | 0.036787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1709-23_0_4_line_13 |  | 9 | 52 | 0.021359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1709-23_0_4_line_14 |  | 10 | 126 | 0.016973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1709-23_0_4_line_15 |  | 11 | 94 | 0.019293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1709-23_0_4_line_16 |  | 13 | 14 | 0.0052362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1709-23_0_4_line_17 |  | 13 | 15 | 0.020654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1709-23_0_4_line_18 |  | 15 | 16 | 0.0016601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1709-23_0_4_line_19 |  | 16 | 49 | 0.024247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1709-23_0_4_line_20 |  | 17 | 18 | 0.004894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1709-23_0_4_line_21 |  | 18 | 19 | 0.020924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1709-23_0_4_line_22 |  | 19 | 20 | 0.00057109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1709-23_0_4_line_23 |  | 20 | 21 | 0.016318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1709-23_0_4_line_24 |  | 21 | 47 | 0.028992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1709-23_0_4_line_25 |  | 21 | 42 | 0.026072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1709-23_0_4_line_26 |  | 22 | 23 | 0.012554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1709-23_0_4_line_27 |  | 22 | 24 | 0.0013459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1709-23_0_4_line_28 |  | 23 | 25 | 0.012257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1709-23_0_4_line_29 |  | 23 | 26 | 0.21704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1709-23_0_4_line_30 |  | 25 | 27 | 0.0075381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1709-23_0_4_line_31 |  | 27 | 28 | 0.010663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1709-23_0_4_line_32 |  | 28 | 65 | 0.0076862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1709-23_0_4_line_33 |  | 28 | 46 | 0.0052505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1709-23_0_4_line_34 |  | 29 | 30 | 0.011649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1709-23_0_4_line_35 |  | 30 | 31 | 0.0090841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1709-23_0_4_line_36 |  | 31 | 32 | 0.021812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1709-23_0_4_line_37 |  | 32 | 36 | 0.016001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1709-23_0_4_line_38 |  | 32 | 37 | 0.016235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1709-23_0_4_line_39 |  | 33 | 34 | 0.030638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1709-23_0_4_line_40 |  | 34 | 35 | 0.031552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1709-23_0_4_line_41 |  | 35 | 70 | 0.029242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1709-23_0_4_line_42 |  | 36 | 53 | 0.015227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1709-23_0_4_line_43 |  | 37 | 41 | 0.01888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1709-23_0_4_line_44 |  | 38 | 39 | 0.021266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1709-23_0_4_line_45 |  | 38 | 40 | 0.035521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1709-23_0_4_line_46 |  | 39 | 41 | 0.0040926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1709-23_0_4_line_47 |  | 40 | 42 | 0.048475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1709-23_0_4_line_48 |  | 40 | 43 | 0.012754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1709-23_0_4_line_49 |  | 41 | 44 | 0.03733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1709-23_0_4_line_50 |  | 42 | 45 | 0.021836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1709-23_0_4_line_51 |  | 43 | 46 | 0.0076117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1709-23_0_4_line_52 |  | 45 | 48 | 0.029074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1709-23_0_4_line_53 |  | 47 | 60 | 0.0037358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1709-23_0_4_line_54 |  | 48 | 63 | 0.016999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1709-23_0_4_line_55 |  | 48 | 64 | 0.013769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1709-23_0_4_line_56 |  | 49 | 50 | 0.0068883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1709-23_0_4_line_57 |  | 50 | 51 | 0.019479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1709-23_0_4_line_58 |  | 52 | 71 | 0.020407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1709-23_0_4_line_59 |  | 53 | 54 | 0.017298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1709-23_0_4_line_60 |  | 54 | 61 | 0.022989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1709-23_0_4_line_61 |  | 55 | 56 | 0.021468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1709-23_0_4_line_62 |  | 56 | 57 | 0.022251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1709-23_0_4_line_63 |  | 57 | 58 | 0.055102 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1709-23_0_4_line_64 |  | 58 | 59 | 0.012075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1709-23_0_4_line_65 |  | 59 | 60 | 0.014547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1709-23_0_4_line_66 |  | 59 | 66 | 0.016484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1709-23_0_4_line_67 |  | 61 | 62 | 0.019399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1709-23_0_4_line_68 |  | 66 | 74 | 0.028223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1709-23_0_4_line_69 |  | 67 | 68 | 0.017608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1709-23_0_4_line_70 |  | 68 | 78 | 0.026576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1709-23_0_4_line_71 |  | 68 | 81 | 0.02662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1709-23_0_4_line_72 |  | 69 | 70 | 0.05643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1709-23_0_4_line_73 |  | 69 | 71 | 0.0304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1709-23_0_4_line_74 |  | 69 | 72 | 0.025337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1709-23_0_4_line_75 |  | 72 | 86 | 0.014942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1709-23_0_4_line_76 |  | 73 | 74 | 0.034262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1709-23_0_4_line_77 |  | 73 | 75 | 0.027006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1709-23_0_4_line_78 |  | 75 | 76 | 0.031034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1709-23_0_4_line_79 |  | 75 | 77 | 0.0017752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1709-23_0_4_line_80 |  | 76 | 78 | 0.004308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1709-23_0_4_line_81 |  | 76 | 79 | 0.025781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1709-23_0_4_line_82 |  | 78 | 80 | 0.017563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1709-23_0_4_line_83 |  | 80 | 82 | 0.00018295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1709-23_0_4_line_84 |  | 82 | 83 | 0.027434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
85 | LV_1709-23_0_4_line_85 |  | 83 | 84 | 0.015695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_1709-23_0_4_line_86 |  | 84 | 85 | 0.008791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_1709-23_0_4_line_87 |  | 84 | 86 | 0.035515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_1709-23_0_4_line_88 |  | 85 | 87 | 0.0069058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_1709-23_0_4_line_89 |  | 87 | 107 | 0.029003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1709-23_0_4_line_90 |  | 88 | 89 | 0.011758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1709-23_0_4_line_91 |  | 88 | 90 | 0.00097669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1709-23_0_4_line_92 |  | 89 | 91 | 0.0063157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1709-23_0_4_line_93 |  | 91 | 92 | 0.024129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1709-23_0_4_line_94 |  | 92 | 93 | 0.04605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1709-23_0_4_line_95 |  | 92 | 94 | 0.0073303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1709-23_0_4_line_96 |  | 93 | 95 | 0.0092869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1709-23_0_4_line_97 |  | 95 | 96 | 0.023739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1709-23_0_4_line_98 |  | 97 | 98 | 0.0027802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1709-23_0_4_line_99 |  | 97 | 99 | 0.022847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1709-23_0_4_line_100 |  | 98 | 100 | 0.014418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1709-23_0_4_line_101 |  | 99 | 101 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1709-23_0_4_line_102 |  | 99 | 102 | 0.02916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1709-23_0_4_line_103 |  | 100 | 103 | 0.029926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1709-23_0_4_line_104 |  | 100 | 104 | 0.0058331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1709-23_0_4_line_105 |  | 101 | 105 | 0.026257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1709-23_0_4_line_106 |  | 101 | 106 | 0.017918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1709-23_0_4_line_107 |  | 103 | 107 | 0.032415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1709-23_0_4_line_108 |  | 104 | 108 | 0.016162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1709-23_0_4_line_109 |  | 105 | 109 | 0.032311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1709-23_0_4_line_110 |  | 106 | 110 | 0.0060066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1709-23_0_4_line_111 |  | 107 | 121 | 0.01084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1709-23_0_4_line_112 |  | 108 | 124 | 0.013637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1709-23_0_4_line_113 |  | 110 | 123 | 0.02052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1709-23_0_4_line_114 |  | 111 | 112 | 0.024161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1709-23_0_4_line_115 |  | 111 | 113 | 0.0046573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1709-23_0_4_line_116 |  | 112 | 114 | 0.0042179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1709-23_0_4_line_117 |  | 113 | 115 | 0.014649 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1709-23_0_4_line_118 |  | 114 | 116 | 0.027904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1709-23_0_4_line_119 |  | 115 | 117 | 0.010378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1709-23_0_4_line_120 |  | 116 | 118 | 0.021047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_1709-23_0_4_line_121 |  | 117 | 119 | 0.021597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_1709-23_0_4_line_122 |  | 118 | 123 | 0.0047532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_1709-23_0_4_line_123 |  | 119 | 122 | 0.0048301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_1709-23_0_4_line_124 |  | 120 | 121 | 0.0041949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_1709-23_0_4_line_125 |  | 124 | 125 | 0.019778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1709-23_0_4_trafo_101 | 0.63 MVA 20/0.4 kV | 127 | 86 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2686091.229 | 1221393.2807 | 2686102.3728 | 1221399.6683 | 2686108.3037 | 1221402.7156
1 | 2686119.3851 | 1221408.4091 | 2686108.3037 | 1221402.7156
2 | 2686091.229 | 1221393.2807 | 2686087.7177 | 1221397.8997
3 | 2686091.229 | 1221393.2807 | 2686100.6281 | 1221380.9327
4 | 2686119.3851 | 1221408.4091 | 2686126.7759 | 1221414.0976 | 2686135.3268 | 1221418.78 | 2686140.5871 | 1221413.8861
5 | 2686087.7177 | 1221397.8997 | 2686084.2215 | 1221396.237
6 | 2686087.7177 | 1221397.8997 | 2686087.7629 | 1221397.9226 | 2686103.2554 | 1221406.6916
7 | 2686114.423 | 1221362.8064 | 2686103.2165 | 1221377.5321 | 2686100.6281 | 1221380.9327
8 | 2686084.2215 | 1221396.237 | 2686069.5512 | 1221389.2202 | 2686055.7915 | 1221383.7732
9 | 2686084.2215 | 1221396.237 | 2686078.6546 | 1221406.0743 | 2686076.2463 | 1221411.416
10 | 2686149.6759 | 1221436.444 | 2686124.2304 | 1221418.5638 | 2686103.2554 | 1221406.6916
11 | 2686114.423 | 1221362.8064 | 2686118.435 | 1221366.0555 | 2686126.2058 | 1221369.6036 | 2686130.7787 | 1221370.9319
12 | 2686082.8991 | 1221346.0282 | 2686098.2653 | 1221358.4365 | 2686111.6633 | 1221360.5761 | 2686114.423 | 1221362.8064
13 | 2686055.7915 | 1221383.7732 | 2686040.2353 | 1221378.2114 | 2686035.5886 | 1221376.8623
14 | 2686076.2463 | 1221411.416 | 2686073.5048 | 1221417.4965 | 2686066.542 | 1221425.0905
15 | 2686149.6759 | 1221436.444 | 2686136.3721 | 1221450.4162
16 | 2686082.8991 | 1221346.0282 | 2686079.741 | 1221350.2048
17 | 2686082.8991 | 1221346.0282 | 2686095.3585 | 1221329.5555
18 | 2686095.3585 | 1221329.5555 | 2686096.36 | 1221328.2314
19 | 2686111.7629 | 1221309.5798 | 2686106.9237 | 1221314.265 | 2686096.36 | 1221328.2314
20 | 2685832.581 | 1221313.8583 | 2685830.315 | 1221312.8273 | 2685828.0294 | 1221312.0805
21 | 2685851.2574 | 1221323.2587 | 2685841.772 | 1221318.0404 | 2685832.581 | 1221313.8583
22 | 2685851.7578 | 1221323.5339 | 2685851.2574 | 1221323.2587
23 | 2685866.055 | 1221331.3994 | 2685851.7578 | 1221323.5339
24 | 2685866.055 | 1221331.3994 | 2685851.9987 | 1221356.7561
25 | 2685866.055 | 1221331.3994 | 2685869.1086 | 1221325.8842 | 2685878.66 | 1221308.5768
26 | 2685850.4422 | 1221244.5155 | 2685850.4422 | 1221244.5155 | 2685843.1342 | 1221254.7232
27 | 2685842.3507 | 1221255.8176 | 2685843.1342 | 1221254.7232
28 | 2685850.4422 | 1221244.5155 | 2685861.9657 | 1221248.6907
29 | 2685850.4422 | 1221244.5155 | 2685677.5859 | 1221113.2599
30 | 2685869.053 | 1221251.2586 | 2685861.9657 | 1221248.6907
31 | 2685879.0779 | 1221254.8908 | 2685869.053 | 1221251.2586
32 | 2685879.0779 | 1221254.8908 | 2685872.0375 | 1221257.9747
33 | 2685879.0779 | 1221254.8908 | 2685883.7971 | 1221257.1923
34 | 2685963.3186 | 1221154.9716 | 2685974.6088 | 1221157.8396
35 | 2685963.3186 | 1221154.9716 | 2685958.9583 | 1221162.9408
36 | 2685948.4888 | 1221182.0759 | 2685958.9583 | 1221162.9408
37 | 2685948.4888 | 1221182.0759 | 2685934.3907 | 1221174.5083
38 | 2685948.4888 | 1221182.0759 | 2685940.6434 | 1221196.2896
39 | 2686066.4926 | 1221238.15 | 2686049.9793 | 1221263.9565
40 | 2686049.9793 | 1221263.9565 | 2686032.9732 | 1221290.5332
41 | 2686032.9732 | 1221290.5332 | 2686017.2122 | 1221315.164
42 | 2685920.1759 | 1221171.8524 | 2685925.81 | 1221170.5632 | 2685933.3333 | 1221173.9406 | 2685934.3907 | 1221174.5083
43 | 2685931.5201 | 1221212.8186 | 2685940.6434 | 1221196.2896
44 | 2685919.2664 | 1221235.0204 | 2685929.5425 | 1221216.4017
45 | 2685902.102 | 1221266.1194 | 2685919.2664 | 1221235.0204
46 | 2685931.5201 | 1221212.8186 | 2685929.5425 | 1221216.4017
47 | 2685902.102 | 1221266.1194 | 2685878.66 | 1221308.5768
48 | 2685902.102 | 1221266.1194 | 2685890.6385 | 1221260.5288
49 | 2685931.5201 | 1221212.8186 | 2685943.9125 | 1221217.3672 | 2685967.5537 | 1221222.1947
50 | 2685878.66 | 1221308.5768 | 2685858.8778 | 1221299.3306
51 | 2685883.7971 | 1221257.1923 | 2685890.6385 | 1221260.5288
52 | 2685832.5384 | 1221287.0196 | 2685858.8778 | 1221299.3306
53 | 2685850.1875 | 1221360.0235 | 2685851.9987 | 1221356.7561
54 | 2685832.5384 | 1221287.0196 | 2685826.46 | 1221288.6776 | 2685818.3617 | 1221295.7212
55 | 2685832.5384 | 1221287.0196 | 2685831.874 | 1221281.5285 | 2685835.2677 | 1221274.0217
56 | 2686116.7117 | 1221304.7884 | 2686111.7629 | 1221309.5798
57 | 2686116.7117 | 1221304.7884 | 2686124.7449 | 1221297.0109 | 2686131.8147 | 1221292.6672
58 | 2686015.9912 | 1221371.1722 | 2686035.5886 | 1221376.8623
59 | 2685907.4719 | 1221182.4745 | 2685915.3888 | 1221172.9478 | 2685920.1759 | 1221171.8524
60 | 2685907.4719 | 1221182.4745 | 2685904.3319 | 1221186.2529 | 2685892.975 | 1221199.8539 | 2685892.7793 | 1221200.1529
61 | 2685794.2073 | 1221307.6146 | 2685787.3647 | 1221327.963
62 | 2685780.2727 | 1221349.0532 | 2685787.3647 | 1221327.963
63 | 2685780.2727 | 1221349.0532 | 2685831.8316 | 1221368.4927
64 | 2685843.1301 | 1221372.7526 | 2685831.8316 | 1221368.4927
65 | 2685850.1875 | 1221360.0235 | 2685843.1301 | 1221372.7526
66 | 2685835.1605 | 1221387.192 | 2685843.1301 | 1221372.7526
67 | 2685882.1599 | 1221216.3869 | 2685892.7793 | 1221200.1529
68 | 2685821.5118 | 1221411.9121 | 2685835.1605 | 1221387.192
69 | 2685909.1723 | 1221374.4615 | 2685916.7321 | 1221358.5587
70 | 2685909.1723 | 1221374.4615 | 2685895.6332 | 1221397.3484
71 | 2685909.1723 | 1221374.4615 | 2685883.7955 | 1221366.4203
72 | 2685986.7971 | 1221362.6958 | 2686017.2122 | 1221315.164
73 | 2685986.7971 | 1221362.6958 | 2686015.9912 | 1221371.1722
74 | 2685986.7971 | 1221362.6958 | 2685974.7255 | 1221384.9726
75 | 2685967.6066 | 1221398.1095 | 2685974.7255 | 1221384.9726
76 | 2685821.5118 | 1221411.9121 | 2685846.0351 | 1221419.6263 | 2685849.8135 | 1221416.9901 | 2685853.4919 | 1221418.4197
77 | 2685878.6638 | 1221428.2025 | 2685853.4919 | 1221418.4197
78 | 2685892.697 | 1221400.5082 | 2685878.6638 | 1221428.2025
79 | 2685878.6638 | 1221428.2025 | 2685877.7587 | 1221429.7295
80 | 2685892.697 | 1221400.5082 | 2685895.6332 | 1221397.3484
81 | 2685892.697 | 1221400.5082 | 2685868.2262 | 1221392.3956
82 | 2685895.6332 | 1221397.3484 | 2685910.8197 | 1221406.1713
83 | 2685910.8197 | 1221406.1713 | 2685910.9779 | 1221406.2632
84 | 2685910.9779 | 1221406.2632 | 2685934.6988 | 1221420.0443
85 | 2685948.2695 | 1221427.9285 | 2685934.6988 | 1221420.0443
86 | 2685948.2695 | 1221427.9285 | 2685943.4819 | 1221435.3089
87 | 2685967.6066 | 1221398.1095 | 2685948.2695 | 1221427.9285
88 | 2685943.4819 | 1221435.3089 | 2685940.1568 | 1221441.3615
89 | 2685926.1924 | 1221466.7808 | 2685940.1568 | 1221441.3615
90 | 2686092.6758 | 1221439.4862 | 2686103.0802 | 1221444.9623
91 | 2686091.8115 | 1221439.0313 | 2686092.6758 | 1221439.4862
92 | 2686103.0802 | 1221444.9623 | 2686108.669 | 1221447.9039
93 | 2686131.3174 | 1221455.7249 | 2686116.7267 | 1221452.1448 | 2686108.669 | 1221447.9039
94 | 2686131.3174 | 1221455.7249 | 2686121.4704 | 1221469.8365 | 2686119.3436 | 1221478.9231 | 2686117.4619 | 1221494.1395 | 2686116.2624 | 1221498.141
95 | 2686131.3174 | 1221455.7249 | 2686136.3721 | 1221450.4162
96 | 2686113.5958 | 1221507.0368 | 2686116.2624 | 1221498.141
97 | 2686113.5958 | 1221507.0368 | 2686096.7285 | 1221523.7416
98 | 2685993.992 | 1221472.569 | 2685992.5392 | 1221474.9396
99 | 2686005.9302 | 1221453.089 | 2685993.992 | 1221472.569
100 | 2685985.0057 | 1221487.2323 | 2685992.5392 | 1221474.9396
101 | 2686005.9302 | 1221453.089 | 2686014.3795 | 1221442.7596
102 | 2686005.9302 | 1221453.089 | 2685977.8852 | 1221445.1041
103 | 2685985.0057 | 1221487.2323 | 2685976.6126 | 1221483.1751 | 2685957.0189 | 1221476.8041
104 | 2685985.0057 | 1221487.2323 | 2685981.9575 | 1221492.2056
105 | 2686029.1465 | 1221421.0247 | 2686014.3795 | 1221442.7596
106 | 2686014.3795 | 1221442.7596 | 2686031.022 | 1221449.3997
107 | 2685926.1924 | 1221466.7808 | 2685957.0189 | 1221476.8041
108 | 2685981.9575 | 1221492.2056 | 2685973.5119 | 1221505.9853
109 | 2686029.1465 | 1221421.0247 | 2686021.6298 | 1221418.2699 | 2686013.5781 | 1221414.7401 | 2686001.2636 | 1221411.6602 | 2685998.7898 | 1221410.3063
110 | 2686031.022 | 1221449.3997 | 2686036.6009 | 1221451.6257
111 | 2685926.1924 | 1221466.7808 | 2685920.597 | 1221476.0645
112 | 2685965.7289 | 1221517.1598 | 2685970.3206 | 1221511.1922 | 2685973.5119 | 1221505.9853
113 | 2686036.6009 | 1221451.6257 | 2686055.6596 | 1221459.2299
114 | 2686042.8224 | 1221526.9622 | 2686053.2712 | 1221505.1772
115 | 2686042.8224 | 1221526.9622 | 2686042.2246 | 1221528.2087 | 2686040.3374 | 1221530.8852
116 | 2686053.2712 | 1221505.1772 | 2686055.0953 | 1221501.3742
117 | 2686031.8959 | 1221542.8577 | 2686040.3374 | 1221530.8852
118 | 2686067.1628 | 1221476.2142 | 2686055.0953 | 1221501.3742
119 | 2686031.8959 | 1221542.8577 | 2686025.9154 | 1221551.3396
120 | 2686067.1628 | 1221476.2142 | 2686068.4458 | 1221473.5393 | 2686069.1333 | 1221468.4902 | 2686067.9295 | 1221464.1254 | 2686060.0744 | 1221460.9913
121 | 2686025.9154 | 1221551.3396 | 2686013.4701 | 1221568.9906
122 | 2686055.6596 | 1221459.2299 | 2686060.0744 | 1221460.9913
123 | 2686010.6868 | 1221572.9381 | 2686013.4701 | 1221568.9906
124 | 2685918.4315 | 1221479.6573 | 2685920.597 | 1221476.0645
125 | 2685965.7289 | 1221517.1598 | 2685953.6683 | 1221532.8346

## bus_geodata
| x | y | coords
0 | 2686108.3037 | 1221402.7156
1 | 2686091.229 | 1221393.2807
2 | 2686119.3851 | 1221408.4091
3 | 2686087.7177 | 1221397.8997
4 | 2686100.6281 | 1221380.9327
5 | 2686140.5871 | 1221413.8861
6 | 2686084.2215 | 1221396.237
7 | 2686103.2554 | 1221406.6916
8 | 2686114.423 | 1221362.8064
9 | 2686055.7915 | 1221383.7732
10 | 2686076.2463 | 1221411.416
11 | 2686149.6759 | 1221436.444
12 | 2686130.7787 | 1221370.9319
13 | 2686082.8991 | 1221346.0282
14 | 2686079.741 | 1221350.2048
15 | 2686095.3585 | 1221329.5555
16 | 2686096.36 | 1221328.2314
17 | 2685828.0294 | 1221312.0805
18 | 2685832.581 | 1221313.8583
19 | 2685851.2574 | 1221323.2587
20 | 2685851.7578 | 1221323.5339
21 | 2685866.055 | 1221331.3994
22 | 2685843.1342 | 1221254.7232
23 | 2685850.4422 | 1221244.5155
24 | 2685842.3507 | 1221255.8176
25 | 2685861.9657 | 1221248.6907
26 | 2685677.5859 | 1221113.2599
27 | 2685869.053 | 1221251.2586
28 | 2685879.0779 | 1221254.8908
29 | 2685974.6088 | 1221157.8396
30 | 2685963.3186 | 1221154.9716
31 | 2685958.9583 | 1221162.9408
32 | 2685948.4888 | 1221182.0759
33 | 2686066.4926 | 1221238.15
34 | 2686049.9793 | 1221263.9565
35 | 2686032.9732 | 1221290.5332
36 | 2685934.3907 | 1221174.5083
37 | 2685940.6434 | 1221196.2896
38 | 2685919.2664 | 1221235.0204
39 | 2685929.5425 | 1221216.4017
40 | 2685902.102 | 1221266.1194
41 | 2685931.5201 | 1221212.8186
42 | 2685878.66 | 1221308.5768
43 | 2685890.6385 | 1221260.5288
44 | 2685967.5537 | 1221222.1947
45 | 2685858.8778 | 1221299.3306
46 | 2685883.7971 | 1221257.1923
47 | 2685851.9987 | 1221356.7561
48 | 2685832.5384 | 1221287.0196
49 | 2686111.7629 | 1221309.5798
50 | 2686116.7117 | 1221304.7884
51 | 2686131.8147 | 1221292.6672
52 | 2686035.5886 | 1221376.8623
53 | 2685920.1759 | 1221171.8524
54 | 2685907.4719 | 1221182.4745
55 | 2685794.2073 | 1221307.6146
56 | 2685787.3647 | 1221327.963
57 | 2685780.2727 | 1221349.0532
58 | 2685831.8316 | 1221368.4927
59 | 2685843.1301 | 1221372.7526
60 | 2685850.1875 | 1221360.0235
61 | 2685892.7793 | 1221200.1529
62 | 2685882.1599 | 1221216.3869
63 | 2685818.3617 | 1221295.7212
64 | 2685835.2677 | 1221274.0217
65 | 2685872.0375 | 1221257.9747
66 | 2685835.1605 | 1221387.192
67 | 2685916.7321 | 1221358.5587
68 | 2685909.1723 | 1221374.4615
69 | 2685986.7971 | 1221362.6958
70 | 2686017.2122 | 1221315.164
71 | 2686015.9912 | 1221371.1722
72 | 2685974.7255 | 1221384.9726
73 | 2685853.4919 | 1221418.4197
74 | 2685821.5118 | 1221411.9121
75 | 2685878.6638 | 1221428.2025
76 | 2685892.697 | 1221400.5082
77 | 2685877.7586 | 1221429.7295
78 | 2685895.6332 | 1221397.3484
79 | 2685868.2262 | 1221392.3956
80 | 2685910.8197 | 1221406.1713
81 | 2685883.7955 | 1221366.4203
82 | 2685910.9779 | 1221406.2632
83 | 2685934.6988 | 1221420.0443
84 | 2685948.2695 | 1221427.9285
85 | 2685943.4819 | 1221435.3089
86 | 2685967.6066 | 1221398.1095
87 | 2685940.1568 | 1221441.3615
88 | 2686092.6758 | 1221439.4862
89 | 2686103.0802 | 1221444.9623
90 | 2686091.8115 | 1221439.0313
91 | 2686108.669 | 1221447.9039
92 | 2686131.3174 | 1221455.7249
93 | 2686116.2624 | 1221498.141
94 | 2686136.3721 | 1221450.4162
95 | 2686113.5958 | 1221507.0368
96 | 2686096.7285 | 1221523.7416
97 | 2685993.992 | 1221472.569
98 | 2685992.5392 | 1221474.9396
99 | 2686005.9302 | 1221453.089
100 | 2685985.0057 | 1221487.2323
101 | 2686014.3795 | 1221442.7596
102 | 2685977.8853 | 1221445.1041
103 | 2685957.0189 | 1221476.8041
104 | 2685981.9575 | 1221492.2056
105 | 2686029.1465 | 1221421.0247
106 | 2686031.022 | 1221449.3997
107 | 2685926.1924 | 1221466.7808
108 | 2685973.5119 | 1221505.9853
109 | 2685998.7898 | 1221410.3063
110 | 2686036.6009 | 1221451.6257
111 | 2686042.8224 | 1221526.9622
112 | 2686053.2712 | 1221505.1772
113 | 2686040.3374 | 1221530.8852
114 | 2686055.0953 | 1221501.3742
115 | 2686031.8959 | 1221542.8577
116 | 2686067.1628 | 1221476.2142
117 | 2686025.9154 | 1221551.3396
118 | 2686060.0744 | 1221460.9913
119 | 2686013.4701 | 1221568.9906
120 | 2685918.4315 | 1221479.6573
121 | 2685920.597 | 1221476.0645
122 | 2686010.6868 | 1221572.9381
123 | 2686055.6596 | 1221459.2299
124 | 2685965.729 | 1221517.1598
125 | 2685953.6683 | 1221532.8346
126 | 2686066.542 | 1221425.0905
127 | 2685948.2695 | 1221427.9285

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98714 | -0.24692 | 0.0082605 | 0.0020703
1 | 0.98745 | -0.24073 | 0 | 0
2 | 0.98703 | -0.24904 | 0 | 0
3 | 0.98772 | -0.23552 | 0 | 0
4 | 0.98699 | -0.24977 | 0.0019271 | 0.00048297
5 | 0.9868 | -0.25349 | 0.0094899 | 0.0023784
6 | 0.98801 | -0.23 | 0 | 0
7 | 0.98724 | -0.24498 | 0.0033767 | 0.00084628
8 | 0.98635 | -0.26226 | 0 | 0
9 | 0.99048 | -0.18206 | 0 | 0
10 | 0.9879 | -0.23213 | 0.0033781 | 0.00084663
11 | 0.9859 | -0.27095 | 0 | 0
12 | 0.98625 | -0.26413 | 0.0056457 | 0.001415
13 | 0.9855 | -0.27874 | 0 | 0
14 | 0.98549 | -0.27887 | 0.0014107 | 0.00035357
15 | 0.98505 | -0.28748 | 0.0070609 | 0.0017696
16 | 0.98503 | -0.28797 | 0.0012292 | 0.00030807
17 | 0.97873 | -0.40867 | 0.0023886 | 0.00059864
18 | 0.97874 | -0.40846 | 0.0024858 | 0.00062301
19 | 0.97884 | -0.4066 | 0.0031198 | 0.00078188
20 | 0.97884 | -0.40652 | 0.0014333 | 0.00035922
21 | 0.97898 | -0.40372 | 0 | 0
22 | 0.97481 | -0.48568 | 0.0021267 | 0.00053301
23 | 0.97487 | -0.48443 | 0.0022785 | 0.00057105
24 | 0.9748 | -0.48577 | 0.0033352 | 0.00083589
25 | 0.97499 | -0.48203 | 0.0015389 | 0.00038569
26 | 0.97429 | -0.49596 | 0.0028928 | 0.000725
27 | 0.97508 | -0.48035 | 0.0011815 | 0.0002961
28 | 0.97521 | -0.47774 | 0 | 0
29 | 0.97361 | -0.50937 | 0.0020145 | 0.00050488
30 | 0.97363 | -0.50894 | 0 | 0
31 | 0.97365 | -0.5086 | 0.001477 | 0.00037017
32 | 0.97372 | -0.5072 | 0 | 0
33 | 0.99576 | -0.080901 | 0.0021241 | 0.00053235
34 | 0.99582 | -0.079757 | 0.0012901 | 0.00032333
35 | 0.99591 | -0.077863 | 0.0012896 | 0.0003232
36 | 0.97358 | -0.50994 | 0.0012023 | 0.00030133
37 | 0.97391 | -0.50339 | 0.0031485 | 0.00078908
38 | 0.97471 | -0.48759 | 0.0045228 | 0.0011335
39 | 0.97426 | -0.49647 | 0.0042855 | 0.001074
40 | 0.97561 | -0.46983 | 0 | 0
41 | 0.97419 | -0.49786 | 0 | 0
42 | 0.97764 | -0.42992 | 0 | 0
43 | 0.9754 | -0.47398 | 0.0011814 | 0.0002961
44 | 0.9741 | -0.49959 | 0.0025289 | 0.00063379
45 | 0.97744 | -0.43394 | 0.0041691 | 0.0010449
46 | 0.97528 | -0.47629 | 0.0015389 | 0.00038569
47 | 0.98072 | -0.36972 | 0.003273 | 0.00082028
48 | 0.97728 | -0.4371 | 0 | 0
49 | 0.98469 | -0.29462 | 0.0012428 | 0.00031148
50 | 0.9846 | -0.29636 | 0.0073712 | 0.0018474
51 | 0.98448 | -0.2987 | 0.0066633 | 0.00167
52 | 0.99219 | -0.14914 | 0.0013636 | 0.00034174
53 | 0.97346 | -0.51221 | 0.0017449 | 0.00043732
54 | 0.97336 | -0.51423 | 0.0014304 | 0.0003585
55 | 0.98147 | -0.35528 | 0.0022182 | 0.00055593
56 | 0.98151 | -0.35442 | 0.0020737 | 0.00051972
57 | 0.9816 | -0.35269 | 0 | 0
58 | 0.98182 | -0.34841 | 0.00098545 | 0.00024698
59 | 0.98188 | -0.34726 | 0 | 0
60 | 0.98096 | -0.36513 | 0 | 0
61 | 0.97326 | -0.51631 | 0.0023881 | 0.00059853
62 | 0.97321 | -0.51721 | 0.00253 | 0.00063407
63 | 0.97724 | -0.43796 | 0.0027779 | 0.00069622
64 | 0.97724 | -0.43789 | 0.0031665 | 0.0007936
65 | 0.9752 | -0.47798 | 0.0016892 | 0.00042337
66 | 0.983 | -0.32548 | 0 | 0
67 | 0.99166 | -0.15888 | 0.011517 | 0.0028863
68 | 0.99184 | -0.15528 | 0 | 0
69 | 0.99636 | -0.069345 | 0 | 0
70 | 0.99604 | -0.075445 | 0.0014475 | 0.00036279
71 | 0.99385 | -0.11731 | 0.0013916 | 0.00034876
72 | 0.99859 | -0.026823 | 0.0070498 | 0.0017668
73 | 0.98724 | -0.24338 | 0.011433 | 0.0028653
74 | 0.98491 | -0.28831 | 0 | 0
75 | 0.98936 | -0.20261 | 0 | 0
76 | 0.99196 | -0.15296 | 0 | 0
77 | 0.98936 | -0.20279 | 0.0054909 | 0.0013762
78 | 0.99235 | -0.14536 | 0 | 0
79 | 0.99173 | -0.15733 | 0.0095597 | 0.0023959
80 | 0.99431 | -0.10791 | 0.0094517 | 0.0023688
81 | 0.99161 | -0.15979 | 0.0095599 | 0.0023959
82 | 0.99434 | -0.10749 | 0.0092139 | 0.0023092
83 | 0.9961 | -0.073844 | 0.0046472 | 0.0011647
84 | 0.9968 | -0.060616 | 0 | 0
85 | 0.99639 | -0.068268 | 0 | 0
86 | 1 | 0 | -0.40321 | -0.10292
87 | 0.99592 | -0.077291 | 0.010292 | 0.0025795
88 | 0.98492 | -0.28998 | 0.0020069 | 0.00050298
89 | 0.98498 | -0.28881 | 0.0028915 | 0.00072468
90 | 0.98492 | -0.29005 | 0.0035287 | 0.00088439
91 | 0.98503 | -0.28786 | 0.0024197 | 0.00060643
92 | 0.98527 | -0.28316 | 0 | 0
93 | 0.98473 | -0.29376 | 0.0046605 | 0.001168
94 | 0.98543 | -0.28004 | 0.002602 | 0.00065213
95 | 0.98466 | -0.29512 | 0 | 0
96 | 0.98448 | -0.29861 | 0.0081567 | 0.0020443
97 | 0.98379 | -0.31009 | 0.0022111 | 0.00055416
98 | 0.98402 | -0.30552 | 0.0020589 | 0.00051601
99 | 0.9819 | -0.34679 | 0 | 0
100 | 0.98527 | -0.28134 | 0 | 0
101 | 0.981 | -0.3643 | 0 | 0
102 | 0.98145 | -0.35545 | 0.016426 | 0.0041168
103 | 0.98836 | -0.22173 | 0.01643 | 0.0041178
104 | 0.98518 | -0.28323 | 0.0027663 | 0.00069329
105 | 0.98095 | -0.36519 | 0 | 0
106 | 0.97982 | -0.38728 | 0.0031898 | 0.00079944
107 | 0.9922 | -0.14814 | 0 | 0
108 | 0.98495 | -0.28765 | 0.006539 | 0.0016388
109 | 0.9809 | -0.36629 | 0.0018763 | 0.00047026
110 | 0.97944 | -0.39464 | 0.0046464 | 0.0011645
111 | 0.97436 | -0.49426 | 0.0080663 | 0.0020216
112 | 0.97536 | -0.4747 | 0.0021602 | 0.0005414
113 | 0.97421 | -0.49734 | 0.0043488 | 0.0010899
114 | 0.97554 | -0.47113 | 0.0057845 | 0.0014497
115 | 0.97378 | -0.50587 | 0.0090161 | 0.0022597
116 | 0.97689 | -0.44456 | 0.0034716 | 0.00087006
117 | 0.97356 | -0.5102 | 0.0062189 | 0.0015586
118 | 0.97798 | -0.42323 | 0.0035159 | 0.00088117
119 | 0.97322 | -0.51675 | 0.011279 | 0.0028267
120 | 0.99208 | -0.15048 | 0.0036559 | 0.00091626
121 | 0.99209 | -0.15021 | 0.0071109 | 0.0017822
122 | 0.9732 | -0.51721 | 0.0051919 | 0.0013012
123 | 0.97824 | -0.41812 | 0.0038227 | 0.00095805
124 | 0.98484 | -0.28978 | 0.0060689 | 0.001521
125 | 0.98479 | -0.29072 | 0.0026265 | 0.00065827
126 | 0.98784 | -0.2332 | 0.0035469 | 0.00088895
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.017753 | -0.0044501 | 0.017759 | 0.0044532 | 5.2406e-06 | 3.1044e-06 | 0.026762 | 0.026762 | 0.026762 | 0.98714 | -0.24692 | 0.98745 | -0.24073 | 7.3522
1 | 0.0094929 | 0.0023798 | -0.0094919 | -0.0023794 | 9.5669e-07 | 4.5303e-07 | 0.01431 | 0.01431 | 0.01431 | 0.98714 | -0.24692 | 0.98703 | -0.24904 | 3.9313
2 | -0.050379 | -0.012654 | 0.050392 | 0.012661 | 1.2532e-05 | 7.9465e-06 | 0.075927 | 0.075927 | 0.075927 | 0.98745 | -0.24073 | 0.98772 | -0.23552 | 20.8591
3 | 0.03262 | 0.0082003 | -0.032606 | -0.0081915 | 1.4067e-05 | 8.8043e-06 | 0.049165 | 0.049165 | 0.049165 | 0.98745 | -0.24073 | 0.98699 | -0.24977 | 13.507
4 | 0.0094919 | 0.0023794 | -0.0094899 | -0.0023784 | 2.0128e-06 | 9.5324e-07 | 0.01431 | 0.01431 | 0.01431 | 0.98703 | -0.24904 | 0.9868 | -0.25349 | 3.9313
5 | -0.080107 | -0.020134 | 0.080128 | 0.020148 | 2.11e-05 | 1.3454e-05 | 0.1207 | 0.1207 | 0.1207 | 0.98772 | -0.23552 | 0.98801 | -0.23 | 33.16
6 | 0.029715 | 0.0074727 | -0.029702 | -0.0074643 | 1.3422e-05 | 8.3616e-06 | 0.044775 | 0.044775 | 0.044775 | 0.98772 | -0.23552 | 0.98724 | -0.24498 | 12.3009
7 | 0.030679 | 0.0077086 | -0.030661 | -0.0076971 | 1.828e-05 | 1.1408e-05 | 0.04626 | 0.04626 | 0.04626 | 0.98699 | -0.24977 | 0.98635 | -0.26226 | 12.7089
8 | -0.087054 | -0.021883 | 0.087254 | 0.022011 | 0.0001998 | 0.00012747 | 0.13113 | 0.13113 | 0.13113 | 0.98801 | -0.23 | 0.99048 | -0.18206 | 36.0257
9 | 0.0069259 | 0.0017357 | -0.0069252 | -0.0017355 | 7.0027e-07 | 2.2841e-07 | 0.010431 | 0.010431 | 0.010431 | 0.98801 | -0.23 | 0.9879 | -0.23213 | 2.8657
10 | 0.026325 | 0.0066181 | -0.026292 | -0.0065979 | 3.2603e-05 | 2.0161e-05 | 0.039686 | 0.039686 | 0.039686 | 0.98724 | -0.24498 | 0.9859 | -0.27095 | 10.9028
11 | 0.0056463 | 0.001415 | -0.0056457 | -0.001415 | 5.0247e-07 | 8.5898e-08 | 0.008518 | 0.0085181 | 0.0085181 | 0.98635 | -0.26226 | 0.98625 | -0.26413 | 2.3401
12 | 0.025015 | 0.0062821 | -0.024995 | -0.00627 | 1.9651e-05 | 1.2107e-05 | 0.037742 | 0.037742 | 0.037742 | 0.98635 | -0.26226 | 0.9855 | -0.27874 | 10.3688
13 | -0.087254 | -0.022011 | 0.087391 | 0.022099 | 0.00013773 | 8.7874e-05 | 0.13113 | 0.13113 | 0.13113 | 0.99048 | -0.18206 | 0.99219 | -0.14914 | 36.0256
14 | 0.0035471 | 0.00088885 | -0.0035469 | -0.00088895 | 1.8169e-07 | -1.0102e-07 | 0.0053428 | 0.0053429 | 0.0053429 | 0.9879 | -0.23213 | 0.98784 | -0.2332 | 1.4678
15 | 0.026292 | 0.0065979 | -0.026281 | -0.0065909 | 1.1395e-05 | 7.0467e-06 | 0.039686 | 0.039686 | 0.039686 | 0.9859 | -0.27095 | 0.98543 | -0.28004 | 10.9028
16 | 0.0014108 | 0.0003535 | -0.0014107 | -0.00035357 | 8.9093e-09 | -6.1015e-08 | 0.0021301 | 0.0021301 | 0.0021301 | 0.9855 | -0.27874 | 0.98549 | -0.27887 | 0.58519
17 | 0.023584 | 0.0059165 | -0.023575 | -0.0059105 | 9.8228e-06 | 6.0236e-06 | 0.035612 | 0.035612 | 0.035612 | 0.9855 | -0.27874 | 0.98505 | -0.28748 | 9.7836
18 | 0.016514 | 0.0041408 | -0.016513 | -0.0041406 | 3.8742e-07 | 2.2682e-07 | 0.024946 | 0.024946 | 0.024946 | 0.98505 | -0.28748 | 0.98503 | -0.28797 | 6.8534
19 | 0.015284 | 0.0038325 | -0.015279 | -0.0038298 | 4.8475e-06 | 2.7939e-06 | 0.023089 | 0.02309 | 0.02309 | 0.98503 | -0.28797 | 0.98469 | -0.29462 | 6.3433
20 | -0.0023886 | -0.00059864 | 0.0023886 | 0.0005986 | 2.4203e-08 | -4.6014e-08 | 0.0036315 | 0.0036315 | 0.0036315 | 0.97873 | -0.40867 | 0.97874 | -0.40846 | 0.99768
21 | -0.0048745 | -0.0012216 | 0.0048749 | 0.0012216 | 4.3092e-07 | 1.2806e-08 | 0.0074108 | 0.0074107 | 0.0074108 | 0.97874 | -0.40846 | 0.97884 | -0.4066 | 2.0359
22 | -0.0079946 | -0.0020035 | 0.0079947 | 0.0020035 | 3.1632e-08 | 1.3066e-08 | 0.012153 | 0.012153 | 0.012153 | 0.97884 | -0.4066 | 0.97884 | -0.40652 | 3.3388
23 | -0.009428 | -0.0023627 | 0.0094292 | 0.0023633 | 1.257e-06 | 5.9931e-07 | 0.014332 | 0.014332 | 0.014332 | 0.97884 | -0.40652 | 0.97898 | -0.40372 | 3.9374
24 | -0.064794 | -0.016314 | 0.064899 | 0.016381 | 0.00010551 | 6.7159e-05 | 0.098511 | 0.098511 | 0.098511 | 0.97898 | -0.40372 | 0.98072 | -0.36972 | 27.0635
25 | 0.055365 | 0.01395 | -0.055295 | -0.013906 | 6.9281e-05 | 4.4013e-05 | 0.084179 | 0.084179 | 0.084179 | 0.97898 | -0.40372 | 0.97764 | -0.42992 | 23.1261
26 | -0.005462 | -0.0013689 | 0.0054623 | 0.0013689 | 3.2726e-07 | 5.2927e-08 | 0.0083375 | 0.0083375 | 0.0083375 | 0.97481 | -0.48568 | 0.97487 | -0.48443 | 2.2905
27 | 0.0033352 | 0.00083588 | -0.0033352 | -0.00083589 | 1.3082e-08 | -8.4065e-09 | 0.0050911 | 0.0050911 | 0.0050911 | 0.97481 | -0.48568 | 0.9748 | -0.48577 | 1.3987
28 | -0.010635 | -0.0026633 | 0.010636 | 0.0026639 | 1.2111e-06 | 6.2225e-07 | 0.016232 | 0.016232 | 0.016232 | 0.97487 | -0.48443 | 0.97499 | -0.48203 | 4.4595
29 | 0.0028944 | 0.00072331 | -0.0028928 | -0.000725 | 1.5884e-06 | -1.688e-06 | 0.0044171 | 0.0044181 | 0.0044181 | 0.97487 | -0.48443 | 0.97429 | -0.49596 | 1.2138
30 | -0.012175 | -0.0030496 | 0.012176 | 0.0030501 | 9.7597e-07 | 5.306e-07 | 0.018581 | 0.018581 | 0.018581 | 0.97499 | -0.48203 | 0.97508 | -0.48035 | 5.1047
31 | -0.013358 | -0.0033462 | 0.013359 | 0.0033472 | 1.6614e-06 | 9.3028e-07 | 0.020384 | 0.020384 | 0.020384 | 0.97508 | -0.48035 | 0.97521 | -0.47774 | 5.6
32 | 0.0016893 | 0.00042328 | -0.0016892 | -0.00042337 | 1.9149e-08 | -8.3644e-08 | 0.0025775 | 0.0025776 | 0.0025776 | 0.97521 | -0.47774 | 0.9752 | -0.47798 | 0.70812
33 | -0.015049 | -0.0037705 | 0.01505 | 0.0037711 | 1.0381e-06 | 5.9885e-07 | 0.022961 | 0.022961 | 0.022961 | 0.97521 | -0.47774 | 0.97528 | -0.47629 | 6.3081
34 | -0.0020145 | -0.00050488 | 0.0020145 | 0.00050476 | 4.1407e-08 | -1.1837e-07 | 0.0030788 | 0.0030788 | 0.0030788 | 0.97361 | -0.50937 | 0.97363 | -0.50894 | 0.84584
35 | -0.0020145 | -0.00050476 | 0.0020146 | 0.00050467 | 3.229e-08 | -9.231e-08 | 0.0030788 | 0.0030788 | 0.0030788 | 0.97363 | -0.50894 | 0.97365 | -0.5086 | 0.84582
36 | -0.0034916 | -0.00087484 | 0.0034918 | 0.00087472 | 2.3289e-07 | -1.2224e-07 | 0.0053361 | 0.005336 | 0.0053361 | 0.97365 | -0.5086 | 0.97372 | -0.5072 | 1.4659
37 | 0.0092991 | 0.0023307 | -0.0092979 | -0.0023301 | 1.2117e-06 | 5.7651e-07 | 0.014211 | 0.014211 | 0.014211 | 0.97372 | -0.5072 | 0.97358 | -0.50994 | 3.9041
38 | -0.012791 | -0.0032054 | 0.012793 | 0.0032067 | 2.3261e-06 | 1.2867e-06 | 0.019547 | 0.019547 | 0.019547 | 0.97372 | -0.5072 | 0.97391 | -0.50339 | 5.37
39 | -0.0021241 | -0.00053235 | 0.0021242 | 0.00053203 | 1.1575e-07 | -3.2448e-07 | 0.0031742 | 0.003174 | 0.0031742 | 0.99576 | -0.080901 | 0.99582 | -0.079757 | 0.87203
40 | -0.0034143 | -0.00085536 | 0.0034146 | 0.00085514 | 3.0796e-07 | -2.1343e-07 | 0.0051018 | 0.0051016 | 0.0051018 | 0.99582 | -0.079757 | 0.99591 | -0.077863 | 1.4016
41 | -0.0047042 | -0.0011783 | 0.0047047 | 0.0011783 | 5.4168e-07 | -3.3876e-08 | 0.0070284 | 0.0070283 | 0.0070284 | 0.99591 | -0.077863 | 0.99604 | -0.075445 | 1.9309
42 | 0.0080955 | 0.0020288 | -0.0080947 | -0.0020284 | 8.7418e-07 | 3.7015e-07 | 0.012373 | 0.012373 | 0.012373 | 0.97358 | -0.50994 | 0.97346 | -0.51221 | 3.3992
43 | -0.015942 | -0.0039958 | 0.015946 | 0.0039983 | 4.2003e-06 | 2.4532e-06 | 0.024357 | 0.024357 | 0.024357 | 0.97391 | -0.50339 | 0.97419 | -0.49786 | 6.6915
44 | 0.022771 | 0.0057124 | -0.022762 | -0.0057065 | 9.6385e-06 | 5.9037e-06 | 0.034765 | 0.034765 | 0.034765 | 0.97471 | -0.48759 | 0.97426 | -0.49647 | 9.5509
45 | -0.027294 | -0.0068459 | 0.027317 | 0.0068603 | 2.3129e-05 | 1.436e-05 | 0.04167 | 0.04167 | 0.04167 | 0.97471 | -0.48759 | 0.97561 | -0.46983 | 11.4477
46 | 0.018476 | 0.0046325 | -0.018475 | -0.0046317 | 1.2222e-06 | 7.3125e-07 | 0.02822 | 0.02822 | 0.02822 | 0.97426 | -0.49647 | 0.97419 | -0.49786 | 7.7527
47 | -0.045093 | -0.011316 | 0.045179 | 0.011371 | 8.5998e-05 | 5.4432e-05 | 0.068781 | 0.068781 | 0.068781 | 0.97561 | -0.46983 | 0.97764 | -0.42992 | 18.896
48 | 0.017775 | 0.004456 | -0.017772 | -0.0044539 | 3.5155e-06 | 2.0907e-06 | 0.027112 | 0.027112 | 0.027112 | 0.97561 | -0.46983 | 0.9754 | -0.47398 | 7.4483
49 | 0.0025291 | 0.00063346 | -0.0025289 | -0.00063379 | 2.0889e-07 | -3.3105e-07 | 0.0038629 | 0.003863 | 0.003863 | 0.97419 | -0.49786 | 0.9741 | -0.49959 | 1.0613
50 | 0.010117 | 0.0025356 | -0.010115 | -0.0025347 | 1.9415e-06 | 9.6881e-07 | 0.015398 | 0.015398 | 0.015398 | 0.97764 | -0.42992 | 0.97744 | -0.43394 | 4.2302
51 | 0.01659 | 0.0041578 | -0.016589 | -0.0041567 | 1.8284e-06 | 1.0752e-06 | 0.025309 | 0.025309 | 0.025309 | 0.9754 | -0.47398 | 0.97528 | -0.47629 | 6.9531
52 | 0.0059456 | 0.0014898 | -0.0059447 | -0.0014896 | 8.9322e-07 | 2.073e-07 | 0.0090512 | 0.0090513 | 0.0090513 | 0.97744 | -0.43394 | 0.97728 | -0.4371 | 2.4866
53 | -0.068172 | -0.017201 | 0.068187 | 0.017211 | 1.5e-05 | 9.5532e-06 | 0.10348 | 0.10348 | 0.10348 | 0.98072 | -0.36972 | 0.98096 | -0.36513 | 28.4277
54 | 0.002778 | 0.00069608 | -0.0027779 | -0.00069622 | 1.1405e-07 | -1.3999e-07 | 0.0042298 | 0.0042299 | 0.0042299 | 0.97728 | -0.4371 | 0.97724 | -0.43796 | 1.1621
55 | 0.0031666 | 0.0007935 | -0.0031665 | -0.0007936 | 1.2004e-07 | -9.5699e-08 | 0.0048215 | 0.0048215 | 0.0048215 | 0.97728 | -0.4371 | 0.97724 | -0.43789 | 1.3246
56 | 0.014036 | 0.0035183 | -0.014035 | -0.0035176 | 1.1622e-06 | 6.562e-07 | 0.021211 | 0.021211 | 0.021211 | 0.98469 | -0.29462 | 0.9846 | -0.29636 | 5.8273
57 | 0.0066641 | 0.0016702 | -0.0066633 | -0.00167 | 7.4093e-07 | 2.2649e-07 | 0.010071 | 0.010071 | 0.010071 | 0.9846 | -0.29636 | 0.98448 | -0.2987 | 2.7669
58 | -0.088755 | -0.02244 | 0.088891 | 0.022527 | 0.00013573 | 8.6602e-05 | 0.13318 | 0.13318 | 0.13318 | 0.99219 | -0.14914 | 0.99385 | -0.11731 | 36.5874
59 | 0.0063498 | 0.0015911 | -0.0063491 | -0.001591 | 6.1109e-07 | 1.7607e-07 | 0.009706 | 0.0097061 | 0.0097061 | 0.97346 | -0.51221 | 0.97336 | -0.51423 | 2.6665
60 | 0.0049187 | 0.0012325 | -0.0049182 | -0.0012324 | 4.8744e-07 | 2.6246e-08 | 0.0075193 | 0.0075195 | 0.0075195 | 0.97336 | -0.51423 | 0.97326 | -0.51631 | 2.0658
61 | -0.0022182 | -0.00055593 | 0.0022183 | 0.00055571 | 9.1047e-08 | -2.1304e-07 | 0.003363 | 0.0033629 | 0.003363 | 0.98147 | -0.35528 | 0.98151 | -0.35442 | 0.9239
62 | -0.004292 | -0.0010754 | 0.0042923 | 0.0010754 | 3.5326e-07 | -5.5158e-08 | 0.0065067 | 0.0065066 | 0.0065067 | 0.98151 | -0.35442 | 0.9816 | -0.35269 | 1.7876
63 | -0.0042923 | -0.0010754 | 0.0042932 | 0.0010752 | 8.7477e-07 | -1.3684e-07 | 0.0065066 | 0.0065064 | 0.0065066 | 0.9816 | -0.35269 | 0.98182 | -0.34841 | 1.7875
64 | -0.0052786 | -0.0013222 | 0.0052789 | 0.0013222 | 2.8979e-07 | 3.275e-08 | 0.0079999 | 0.0079998 | 0.0079999 | 0.98182 | -0.34841 | 0.98188 | -0.34726 | 2.1978
65 | 0.068246 | 0.017248 | -0.068187 | -0.017211 | 5.841e-05 | 3.7199e-05 | 0.10348 | 0.10348 | 0.10348 | 0.98188 | -0.34726 | 0.98096 | -0.36513 | 28.4277
66 | -0.073525 | -0.01857 | 0.073601 | 0.018619 | 7.6818e-05 | 4.8955e-05 | 0.11148 | 0.11148 | 0.11148 | 0.98188 | -0.34726 | 0.983 | -0.32548 | 30.6254
67 | 0.0025301 | 0.0006339 | -0.00253 | -0.00063407 | 1.0885e-07 | -1.7139e-07 | 0.0038682 | 0.0038683 | 0.0038683 | 0.97326 | -0.51631 | 0.97321 | -0.51721 | 1.0627
68 | -0.073601 | -0.018619 | 0.073733 | 0.018703 | 0.00013152 | 8.3816e-05 | 0.11148 | 0.11148 | 0.11148 | 0.983 | -0.32548 | 0.98491 | -0.28831 | 30.6254
69 | -0.011517 | -0.0028863 | 0.011519 | 0.0028874 | 1.9719e-06 | 1.0348e-06 | 0.017281 | 0.017281 | 0.017281 | 0.99166 | -0.15888 | 0.99184 | -0.15528 | 4.7476
70 | -0.021081 | -0.0052843 | 0.021091 | 0.0052903 | 9.9684e-06 | 6.0366e-06 | 0.031627 | 0.031627 | 0.031627 | 0.99184 | -0.15528 | 0.99235 | -0.14536 | 8.6886
71 | 0.009562 | 0.0023969 | -0.0095599 | -0.0023959 | 2.0544e-06 | 9.7133e-07 | 0.014346 | 0.014346 | 0.014346 | 0.99184 | -0.15528 | 0.99161 | -0.15979 | 3.9411
72 | 0.0061541 | 0.0015415 | -0.0061523 | -0.0015411 | 1.7875e-06 | 4.0928e-07 | 0.0091906 | 0.0091908 | 0.0091908 | 0.99636 | -0.069345 | 0.99604 | -0.075445 | 2.525
73 | 0.090491 | 0.023009 | -0.090282 | -0.022876 | 0.00020857 | 0.00013309 | 0.13526 | 0.13526 | 0.13526 | 0.99636 | -0.069345 | 0.99385 | -0.11731 | 37.1598
74 | -0.096645 | -0.02455 | 0.096843 | 0.024677 | 0.00019826 | 0.00012656 | 0.14445 | 0.14445 | 0.14445 | 0.99636 | -0.069345 | 0.99859 | -0.026823 | 39.6846
75 | -0.10389 | -0.026444 | 0.10403 | 0.02653 | 0.00013454 | 8.5911e-05 | 0.15496 | 0.15496 | 0.15496 | 0.99859 | -0.026823 | 1 | 0 | 42.5705
76 | 0.073893 | 0.018805 | -0.073733 | -0.018703 | 0.00015966 | 0.00010175 | 0.11148 | 0.11148 | 0.11148 | 0.98724 | -0.24338 | 0.98491 | -0.28831 | 30.6254
77 | -0.085325 | -0.02167 | 0.085493 | 0.021777 | 0.00016777 | 0.00010702 | 0.12871 | 0.12871 | 0.12871 | 0.98724 | -0.24338 | 0.98936 | -0.20261 | 35.3593
78 | -0.090984 | -0.023153 | 0.091202 | 0.023292 | 0.00021832 | 0.00013933 | 0.13697 | 0.13697 | 0.13697 | 0.98936 | -0.20261 | 0.99196 | -0.15296 | 37.6281
79 | 0.005491 | 0.0013762 | -0.0054909 | -0.0013762 | 4.5402e-08 | 6.2611e-09 | 0.0082585 | 0.0082585 | 0.0082585 | 0.98936 | -0.20261 | 0.98936 | -0.20279 | 2.2688
80 | -0.10076 | -0.025689 | 0.1008 | 0.025713 | 3.6986e-05 | 2.3615e-05 | 0.15131 | 0.15131 | 0.15131 | 0.99196 | -0.15296 | 0.99235 | -0.14536 | 41.5685
81 | 0.0095617 | 0.0023968 | -0.0095597 | -0.0023959 | 1.989e-06 | 9.4023e-07 | 0.014343 | 0.014344 | 0.014344 | 0.99196 | -0.15296 | 0.99173 | -0.15733 | 3.9405
82 | -0.12189 | -0.031003 | 0.12211 | 0.031144 | 0.00022041 | 0.00014084 | 0.18294 | 0.18294 | 0.18294 | 0.99235 | -0.14536 | 0.99431 | -0.10791 | 50.2571
83 | -0.13156 | -0.033513 | 0.13157 | 0.033515 | 2.6647e-06 | 1.703e-06 | 0.19708 | 0.19708 | 0.19708 | 0.99431 | -0.10791 | 0.99434 | -0.10749 | 54.1429
84 | -0.14078 | -0.035824 | 0.14101 | 0.035969 | 0.00022872 | 0.00014567 | 0.21087 | 0.21087 | 0.21087 | 0.99434 | -0.10749 | 0.9961 | -0.073844 | 28.9655
85 | -0.14566 | -0.037134 | 0.14575 | 0.037193 | 9.3072e-05 | 5.8953e-05 | 0.21781 | 0.21781 | 0.21781 | 0.9961 | -0.073844 | 0.9968 | -0.060616 | 19.946
86 | 0.15091 | 0.038644 | -0.15085 | -0.038609 | 5.5911e-05 | 3.5439e-05 | 0.22557 | 0.22557 | 0.22557 | 0.9968 | -0.060616 | 0.99639 | -0.068268 | 20.6562
87 | -0.29666 | -0.075837 | 0.29753 | 0.076394 | 0.0008727 | 0.00055713 | 0.44338 | 0.44338 | 0.44338 | 0.9968 | -0.060616 | 1 | 0 | 40.6022
88 | 0.15085 | 0.038609 | -0.15078 | -0.038567 | 6.5881e-05 | 4.1984e-05 | 0.22557 | 0.22557 | 0.22557 | 0.99639 | -0.068268 | 0.99592 | -0.077291 | 30.9843
89 | 0.14049 | 0.035987 | -0.14001 | -0.03568 | 0.00048049 | 0.00030714 | 0.21019 | 0.21019 | 0.21019 | 0.99592 | -0.077291 | 0.9922 | -0.14814 | 57.7439
90 | -0.0055356 | -0.0013874 | 0.005536 | 0.0013874 | 3.0838e-07 | 4.7721e-08 | 0.0083632 | 0.0083632 | 0.0083632 | 0.98492 | -0.28998 | 0.98498 | -0.28881 | 2.2976
91 | 0.0035287 | 0.00088438 | -0.0035287 | -0.00088439 | 1.041e-08 | -5.7678e-09 | 0.0053312 | 0.0053312 | 0.0053312 | 0.98492 | -0.28998 | 0.98492 | -0.29005 | 1.4646
92 | -0.0084275 | -0.0021121 | 0.0084279 | 0.0021123 | 3.8388e-07 | 1.6529e-07 | 0.012731 | 0.012731 | 0.012731 | 0.98498 | -0.28881 | 0.98503 | -0.28786 | 3.4976
93 | -0.010848 | -0.0027187 | 0.01085 | 0.0027199 | 2.4297e-06 | 1.2478e-06 | 0.016387 | 0.016386 | 0.016387 | 0.98503 | -0.28786 | 0.98527 | -0.28316 | 4.5018
94 | 0.012826 | 0.0032166 | -0.012819 | -0.0032131 | 6.4797e-06 | 3.5608e-06 | 0.019371 | 0.019371 | 0.019371 | 0.98527 | -0.28316 | 0.98473 | -0.29376 | 5.3217
95 | -0.023676 | -0.0059366 | 0.023679 | 0.0059387 | 3.5146e-06 | 2.156e-06 | 0.035757 | 0.035757 | 0.035757 | 0.98527 | -0.28316 | 0.98543 | -0.28004 | 9.8234
96 | 0.0081586 | 0.002045 | -0.008158 | -0.0020448 | 5.2932e-07 | 2.2063e-07 | 0.012328 | 0.012328 | 0.012328 | 0.98473 | -0.29376 | 0.98466 | -0.29512 | 3.3869
97 | 0.008158 | 0.0020448 | -0.0081567 | -0.0020443 | 1.3531e-06 | 5.6406e-07 | 0.012328 | 0.012329 | 0.012329 | 0.98466 | -0.29512 | 0.98448 | -0.29861 | 3.387
98 | -0.091839 | -0.023252 | 0.091859 | 0.023265 | 2.0142e-05 | 1.2856e-05 | 0.13899 | 0.13899 | 0.13899 | 0.98379 | -0.31009 | 0.98402 | -0.30552 | 38.1853
99 | 0.089628 | 0.022698 | -0.08947 | -0.022597 | 0.00015765 | 0.00010061 | 0.13565 | 0.13565 | 0.13565 | 0.98379 | -0.31009 | 0.9819 | -0.34679 | 37.2666
100 | -0.093918 | -0.023781 | 0.094027 | 0.023851 | 0.00010918 | 6.9695e-05 | 0.14211 | 0.14211 | 0.14211 | 0.98402 | -0.30552 | 0.98527 | -0.28134 | 39.0407
101 | 0.073037 | 0.018477 | -0.072976 | -0.018438 | 6.1313e-05 | 3.9072e-05 | 0.11075 | 0.11075 | 0.11075 | 0.9819 | -0.34679 | 0.981 | -0.3643 | 30.4248
102 | 0.016433 | 0.0041208 | -0.016426 | -0.0041168 | 6.782e-06 | 3.9718e-06 | 0.024904 | 0.024904 | 0.024904 | 0.9819 | -0.34679 | 0.98145 | -0.35545 | 6.8418
103 | -0.11203 | -0.028365 | 0.11236 | 0.028571 | 0.00032167 | 0.00020548 | 0.1693 | 0.1693 | 0.1693 | 0.98527 | -0.28134 | 0.98836 | -0.22173 | 46.5118
104 | 0.018007 | 0.0045144 | -0.018005 | -0.0045135 | 1.6177e-06 | 9.6108e-07 | 0.027195 | 0.027195 | 0.027195 | 0.98527 | -0.28134 | 0.98518 | -0.28323 | 7.4712
105 | 0.0018765 | 0.00046963 | -0.0018764 | -0.00046991 | 7.9764e-08 | -2.8044e-07 | 0.0028461 | 0.0028463 | 0.0028463 | 0.981 | -0.3643 | 0.98095 | -0.36519 | 0.78194
106 | 0.0711 | 0.017968 | -0.071021 | -0.017918 | 7.823e-05 | 4.9841e-05 | 0.1079 | 0.1079 | 0.1079 | 0.981 | -0.3643 | 0.97982 | -0.38728 | 29.6429
107 | -0.12879 | -0.032689 | 0.12924 | 0.032981 | 0.00045768 | 0.0002925 | 0.19404 | 0.19404 | 0.19404 | 0.98836 | -0.22173 | 0.9922 | -0.14814 | 53.3075
108 | 0.015239 | 0.0038202 | -0.015235 | -0.0038183 | 3.2109e-06 | 1.8492e-06 | 0.023017 | 0.023017 | 0.023017 | 0.98518 | -0.28323 | 0.98495 | -0.28765 | 6.3233
109 | 0.0018764 | 0.00046991 | -0.0018763 | -0.00047026 | 9.8164e-08 | -3.4505e-07 | 0.0028463 | 0.0028464 | 0.0028464 | 0.98095 | -0.36519 | 0.9809 | -0.36629 | 0.78198
110 | 0.067832 | 0.017119 | -0.067808 | -0.017103 | 2.3922e-05 | 1.5235e-05 | 0.10306 | 0.10306 | 0.10306 | 0.97982 | -0.38728 | 0.97944 | -0.39464 | 28.3121
111 | 0.010768 | 0.0026989 | -0.010767 | -0.0026984 | 1.0601e-06 | 5.3846e-07 | 0.016149 | 0.016149 | 0.016149 | 0.9922 | -0.14814 | 0.99209 | -0.15021 | 4.4365
112 | 0.0086965 | 0.0021795 | -0.0086956 | -0.0021791 | 8.827e-07 | 3.9139e-07 | 0.013138 | 0.013138 | 0.013138 | 0.98495 | -0.28765 | 0.98484 | -0.28978 | 3.6094
113 | 0.063161 | 0.015939 | -0.06309 | -0.015894 | 7.0912e-05 | 4.5126e-05 | 0.095997 | 0.095997 | 0.095997 | 0.97944 | -0.39464 | 0.97824 | -0.41812 | 26.3728
114 | -0.044149 | -0.011075 | 0.04419 | 0.011101 | 4.1192e-05 | 2.6061e-05 | 0.067427 | 0.067426 | 0.067427 | 0.97436 | -0.49426 | 0.97536 | -0.4747 | 18.5238
115 | 0.036083 | 0.0090534 | -0.036077 | -0.0090501 | 5.3039e-06 | 3.3365e-06 | 0.055108 | 0.055108 | 0.055108 | 0.97436 | -0.49426 | 0.97421 | -0.49734 | 15.1396
116 | -0.04635 | -0.011642 | 0.046358 | 0.011648 | 7.9111e-06 | 5.0105e-06 | 0.070722 | 0.070722 | 0.070722 | 0.97536 | -0.4747 | 0.97554 | -0.47113 | 19.4291
117 | 0.031729 | 0.0079602 | -0.031716 | -0.0079521 | 1.2904e-05 | 8.0761e-06 | 0.048466 | 0.048466 | 0.048466 | 0.97421 | -0.49734 | 0.97378 | -0.50587 | 13.3147
118 | -0.052143 | -0.013097 | 0.052209 | 0.013139 | 6.6211e-05 | 4.2026e-05 | 0.079545 | 0.079545 | 0.079545 | 0.97554 | -0.47113 | 0.97689 | -0.44456 | 21.8531
119 | 0.0227 | 0.0056925 | -0.022695 | -0.0056896 | 4.683e-06 | 2.868e-06 | 0.034688 | 0.034688 | 0.034688 | 0.97378 | -0.50587 | 0.97356 | -0.5102 | 9.5297
120 | -0.055681 | -0.014009 | 0.055737 | 0.014045 | 5.6801e-05 | 3.6089e-05 | 0.084833 | 0.084833 | 0.084833 | 0.97689 | -0.44456 | 0.97798 | -0.42323 | 23.3058
121 | 0.016476 | 0.004131 | -0.016471 | -0.004128 | 5.1363e-06 | 3.0188e-06 | 0.025183 | 0.025183 | 0.025183 | 0.97356 | -0.5102 | 0.97322 | -0.51675 | 6.9185
122 | -0.059253 | -0.014927 | 0.059268 | 0.014936 | 1.4496e-05 | 9.2181e-06 | 0.090182 | 0.090182 | 0.090182 | 0.97798 | -0.42323 | 0.97824 | -0.41812 | 24.7754
123 | 0.005192 | 0.0013012 | -0.0051919 | -0.0013012 | 1.1414e-07 | 1.3033e-08 | 0.0079383 | 0.0079383 | 0.0079383 | 0.97322 | -0.51675 | 0.9732 | -0.51721 | 2.1809
124 | -0.0036559 | -0.00091626 | 0.003656 | 0.00091623 | 4.7301e-08 | -2.3894e-08 | 0.0054835 | 0.0054835 | 0.0054835 | 0.99208 | -0.15048 | 0.99209 | -0.15021 | 1.5065
125 | 0.0026266 | 0.00065809 | -0.0026265 | -0.00065827 | 1.1681e-07 | -1.7689e-07 | 0.0039686 | 0.0039687 | 0.0039687 | 0.98484 | -0.28978 | 0.98479 | -0.29072 | 1.0903

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40321 | 0.10292

## res_load
| p_mw | q_mvar
0 | 0.0082605 | 0.0020703
1 | 0.0019271 | 0.00048297
2 | 0.0094899 | 0.0023784
3 | 0.0033767 | 0.00084628
4 | 0.0033781 | 0.00084663
5 | 0.0056457 | 0.001415
6 | 0.0014107 | 0.00035357
7 | 0.0070609 | 0.0017696
8 | 0.0012292 | 0.00030807
9 | 0.0023886 | 0.00059864
10 | 0.0024858 | 0.00062301
11 | 0.0031198 | 0.00078188
12 | 0.0014333 | 0.00035922
13 | 0.0021267 | 0.00053301
14 | 0.0022785 | 0.00057105
15 | 0.0033352 | 0.00083589
16 | 0.0015389 | 0.00038569
17 | 0.0028928 | 0.000725
18 | 0.0011815 | 0.0002961
19 | 0.0020145 | 0.00050488
20 | 0.001477 | 0.00037017
21 | 0.0021241 | 0.00053235
22 | 0.0012901 | 0.00032333
23 | 0.0012896 | 0.0003232
24 | 0.0012023 | 0.00030133
25 | 0.0031485 | 0.00078908
26 | 0.0045228 | 0.0011335
27 | 0.0042855 | 0.001074
28 | 0.0011814 | 0.0002961
29 | 0.0025289 | 0.00063379
30 | 0.0041691 | 0.0010449
31 | 0.0015389 | 0.00038569
32 | 0.003273 | 0.00082028
33 | 0.0012428 | 0.00031148
34 | 0.0073712 | 0.0018474
35 | 0.0066633 | 0.00167
36 | 0.0013636 | 0.00034174
37 | 0.0017449 | 0.00043732
38 | 0.0014304 | 0.0003585
39 | 0.0022182 | 0.00055593
40 | 0.0020737 | 0.00051972
41 | 0.00098545 | 0.00024698
42 | 0.0023881 | 0.00059853
43 | 0.00253 | 0.00063407
44 | 0.0027779 | 0.00069622
45 | 0.0031665 | 0.0007936
46 | 0.0016892 | 0.00042337
47 | 0.011517 | 0.0028863
48 | 0.0014475 | 0.00036279
49 | 0.0013916 | 0.00034876
50 | 0.0070498 | 0.0017668
51 | 0.011433 | 0.0028653
52 | 0.0054909 | 0.0013762
53 | 0.0095597 | 0.0023959
54 | 0.0094517 | 0.0023688
55 | 0.0095599 | 0.0023959
56 | 0.0092139 | 0.0023092
57 | 0.0046472 | 0.0011647
58 | 0.010292 | 0.0025795
59 | 0.0020069 | 0.00050298
60 | 0.0028915 | 0.00072468
61 | 0.0035287 | 0.00088439
62 | 0.0024197 | 0.00060643
63 | 0.0046605 | 0.001168
64 | 0.002602 | 0.00065213
65 | 0.0081567 | 0.0020443
66 | 0.0022111 | 0.00055416
67 | 0.0020589 | 0.00051601
68 | 0.016426 | 0.0041168
69 | 0.01643 | 0.0041178
70 | 0.0027663 | 0.00069329
71 | 0.0031898 | 0.00079944
72 | 0.006539 | 0.0016388
73 | 0.0018763 | 0.00047026
74 | 0.0046464 | 0.0011645
75 | 0.0080663 | 0.0020216
76 | 0.0021602 | 0.0005414
77 | 0.0043488 | 0.0010899
78 | 0.0057845 | 0.0014497
79 | 0.0090161 | 0.0022597
80 | 0.0034716 | 0.00087006
81 | 0.0062189 | 0.0015586
82 | 0.0035159 | 0.00088117
83 | 0.011279 | 0.0028267
84 | 0.0036559 | 0.00091626
85 | 0.0071109 | 0.0017822
86 | 0.0051919 | 0.0013012
87 | 0.0038227 | 0.00095805
88 | 0.0060689 | 0.001521
89 | 0.0026265 | 0.00065827
90 | 0.0035469 | 0.00088895

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1