## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-15_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-15_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1711-15_0_6_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1711-15_0_6_node_7 | 0.4 | n |  | TRUE
4 | bus_LV_1711-15_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1711-15_0_6_node_41 | 0.4 | n |  | TRUE
6 | bus_LV_1711-15_0_6_node_122 | 0.4 | n |  | TRUE
7 | bus_LV_1711-15_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1711-15_0_6_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1711-15_0_6_node_52 | 0.4 | n |  | TRUE
10 | bus_LV_1711-15_0_6_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_1711-15_0_6_node_42 | 0.4 | n |  | TRUE
12 | bus_LV_1711-15_0_6_node_123 | 0.4 | n |  | TRUE
13 | bus_LV_1711-15_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1711-15_0_6_node_51 | 0.4 | n |  | TRUE
15 | bus_LV_1711-15_0_6_node_19 | 0.4 | n |  | TRUE
16 | bus_LV_1711-15_0_6_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1711-15_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1711-15_0_6_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1711-15_0_6_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_1711-15_0_6_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_1711-15_0_6_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_1711-15_0_6_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1711-15_0_6_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1711-15_0_6_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1711-15_0_6_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1711-15_0_6_node_88 | 0.4 | n |  | TRUE
27 | bus_LV_1711-15_0_6_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1711-15_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1711-15_0_6_node_117 | 0.4 | n |  | TRUE
30 | bus_LV_1711-15_0_6_node_80 | 0.4 | n |  | TRUE
31 | bus_LV_1711-15_0_6_node_115 | 0.4 | n |  | TRUE
32 | bus_LV_1711-15_0_6_node_111 | 0.4 | n |  | TRUE
33 | bus_LV_1711-15_0_6_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1711-15_0_6_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_1711-15_0_6_node_83 | 0.4 | n |  | TRUE
36 | bus_LV_1711-15_0_6_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1711-15_0_6_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1711-15_0_6_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_1711-15_0_6_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_1711-15_0_6_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_1711-15_0_6_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_1711-15_0_6_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_1711-15_0_6_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_1711-15_0_6_node_34 | 0.4 | n |  | TRUE
45 | bus_LV_1711-15_0_6_node_31 | 0.4 | n |  | TRUE
46 | bus_LV_1711-15_0_6_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_1711-15_0_6_node_84 | 0.4 | n |  | TRUE
48 | bus_LV_1711-15_0_6_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_1711-15_0_6_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1711-15_0_6_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_1711-15_0_6_node_37 | 0.4 | n |  | TRUE
52 | bus_LV_1711-15_0_6_node_40 | 0.4 | n |  | TRUE
53 | bus_LV_1711-15_0_6_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_1711-15_0_6_node_43 | 0.4 | n |  | TRUE
55 | bus_LV_1711-15_0_6_node_95 | 0.4 | n |  | TRUE
56 | bus_LV_1711-15_0_6_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_1711-15_0_6_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_1711-15_0_6_node_96 | 0.4 | n |  | TRUE
59 | bus_LV_1711-15_0_6_node_97 | 0.4 | n |  | TRUE
60 | bus_LV_1711-15_0_6_node_119 | 0.4 | n |  | TRUE
61 | bus_LV_1711-15_0_6_node_94 | 0.4 | n |  | TRUE
62 | bus_LV_1711-15_0_6_node_118 | 0.4 | n |  | TRUE
63 | bus_LV_1711-15_0_6_node_114 | 0.4 | n |  | TRUE
64 | bus_LV_1711-15_0_6_node_47 | 0.4 | n |  | TRUE
65 | bus_LV_1711-15_0_6_node_48 | 0.4 | n |  | TRUE
66 | bus_LV_1711-15_0_6_node_49 | 0.4 | n |  | TRUE
67 | bus_LV_1711-15_0_6_node_53 | 0.4 | n |  | TRUE
68 | bus_LV_1711-15_0_6_node_54 | 0.4 | n |  | TRUE
69 | bus_LV_1711-15_0_6_node_55 | 0.4 | n |  | TRUE
70 | bus_LV_1711-15_0_6_node_56 | 0.4 | n |  | TRUE
71 | bus_LV_1711-15_0_6_node_57 | 0.4 | n |  | TRUE
72 | bus_LV_1711-15_0_6_node_87 | 0.4 | n |  | TRUE
73 | bus_LV_1711-15_0_6_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_1711-15_0_6_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_1711-15_0_6_node_89 | 0.4 | n |  | TRUE
76 | bus_LV_1711-15_0_6_node_81 | 0.4 | n |  | TRUE
77 | bus_LV_1711-15_0_6_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_1711-15_0_6_node_65 | 0.4 | n |  | TRUE
79 | bus_LV_1711-15_0_6_node_90 | 0.4 | n |  | TRUE
80 | bus_LV_1711-15_0_6_node_59 | 0.4 | n |  | TRUE
81 | bus_LV_1711-15_0_6_node_61 | 0.4 | n |  | TRUE
82 | bus_LV_1711-15_0_6_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_1711-15_0_6_node_70 | 0.4 | n |  | TRUE
84 | bus_LV_1711-15_0_6_node_71 | 0.4 | n |  | TRUE
85 | bus_LV_1711-15_0_6_node_91 | 0.4 | n |  | TRUE
86 | bus_LV_1711-15_0_6_node_64 | 0.4 | n |  | TRUE
87 | bus_LV_1711-15_0_6_node_66 | 0.4 | n |  | TRUE
88 | bus_LV_1711-15_0_6_node_68 | 0.4 | n |  | TRUE
89 | bus_LV_1711-15_0_6_node_69 | 0.4 | n |  | TRUE
90 | bus_LV_1711-15_0_6_node_92 | 0.4 | n |  | TRUE
91 | bus_LV_1711-15_0_6_node_102 | 0.4 | n |  | TRUE
92 | bus_LV_1711-15_0_6_node_101 | 0.4 | n |  | TRUE
93 | bus_LV_1711-15_0_6_node_72 | 0.4 | n |  | TRUE
94 | bus_LV_1711-15_0_6_node_73 | 0.4 | n |  | TRUE
95 | bus_LV_1711-15_0_6_node_74 | 0.4 | n |  | TRUE
96 | bus_LV_1711-15_0_6_node_121 | 0.4 | n |  | TRUE
97 | bus_LV_1711-15_0_6_node_75 | 0.4 | n |  | TRUE
98 | bus_LV_1711-15_0_6_node_120 | 0.4 | n |  | TRUE
99 | bus_LV_1711-15_0_6_node_113 | 0.4 | n |  | TRUE
100 | bus_LV_1711-15_0_6_node_112 | 0.4 | n |  | TRUE
101 | bus_LV_1711-15_0_6_node_76 | 0.4 | n |  | TRUE
102 | bus_LV_1711-15_0_6_node_77 | 0.4 | n |  | TRUE
103 | bus_LV_1711-15_0_6_node_79 | 0.4 | n |  | TRUE
104 | bus_LV_1711-15_0_6_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_1711-15_0_6_node_116 | 0.4 | n |  | TRUE
106 | bus_LV_1711-15_0_6_node_110 | 0.4 | n |  | TRUE
107 | bus_LV_1711-15_0_6_node_85 | 0.4 | n |  | TRUE
108 | bus_LV_1711-15_0_6_node_93 | 0.4 | n |  | TRUE
109 | bus_LV_1711-15_0_6_node_98 | 0.4 | n |  | TRUE
110 | bus_LV_1711-15_0_6_node_99 | 0.4 | n |  | TRUE
111 | bus_LV_1711-15_0_6_node_100 | 0.4 | n |  | TRUE
112 | bus_LV_1711-15_0_6_node_105 | 0.4 | n |  | TRUE
113 | bus_LV_1711-15_0_6_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_1711-15_0_6_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_1711-15_0_6_node_108 | 0.4 | n |  | TRUE
116 | bus_LV_1711-15_0_6_node_124 | 0.4 | n |  | TRUE
117 | bus_MV_228_0_node_18 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-15_0_6_load_0 | 0 | 0.0026029 | 0.00065234 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-15_0_6_load_7 | 3 | 0.0017275 | 0.00043295 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-15_0_6_load_122 | 6 | 0.0045421 | 0.0011383 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-15_0_6_load_11 | 8 | 0.0045609 | 0.0011431 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-15_0_6_load_52 | 9 | 0.005998 | 0.0015032 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-15_0_6_load_42 | 11 | 0.020874 | 0.0052314 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-15_0_6_load_123 | 12 | 0.012688 | 0.00318 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-15_0_6_load_9 | 13 | 0.0059629 | 0.0014944 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-15_0_6_load_51 | 14 | 0.015253 | 0.0038228 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-15_0_6_load_19 | 15 | 0.0019236 | 0.00048211 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-15_0_6_load_10 | 17 | 0.0045052 | 0.0011291 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-15_0_6_load_12 | 18 | 0.0026496 | 0.00066405 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-15_0_6_load_13 | 19 | 0.0055511 | 0.0013912 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-15_0_6_load_14 | 20 | 0.0056708 | 0.0014212 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-15_0_6_load_15 | 21 | 0.0022153 | 0.0005552 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-15_0_6_load_18 | 23 | 0.0040353 | 0.0010113 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-15_0_6_load_21 | 24 | 0.011855 | 0.0029712 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-15_0_6_load_88 | 26 | 0.0050111 | 0.0012559 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-15_0_6_load_30 | 27 | 0.0054824 | 0.001374 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-15_0_6_load_22 | 28 | 0.0018174 | 0.00045549 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-15_0_6_load_117 | 29 | 0.0043206 | 0.0010829 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-15_0_6_load_115 | 31 | 0.0073615 | 0.001845 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-15_0_6_load_111 | 32 | 0.0061595 | 0.0015437 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-15_0_6_load_58 | 34 | 0.0096825 | 0.0024267 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-15_0_6_load_83 | 35 | 0.0098752 | 0.002475 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-15_0_6_load_23 | 36 | 0.011324 | 0.0028382 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-15_0_6_load_24 | 37 | 0.011529 | 0.0028895 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1711-15_0_6_load_27 | 40 | 0.012259 | 0.0030724 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1711-15_0_6_load_28 | 41 | 0.012321 | 0.0030878 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1711-15_0_6_load_32 | 42 | 0.011751 | 0.002945 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1711-15_0_6_load_33 | 43 | 0.011781 | 0.0029526 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1711-15_0_6_load_34 | 44 | 0.011291 | 0.0028298 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1711-15_0_6_load_31 | 45 | 0.0069495 | 0.0017417 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1711-15_0_6_load_35 | 46 | 0.012164 | 0.0030485 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1711-15_0_6_load_50 | 48 | 0.012438 | 0.0031172 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1711-15_0_6_load_36 | 49 | 0.0025589 | 0.00064133 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1711-15_0_6_load_38 | 50 | 0.0025589 | 0.00064133 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1711-15_0_6_load_37 | 51 | 0.0088966 | 0.0022297 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1711-15_0_6_load_43 | 54 | 0.0077976 | 0.0019543 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1711-15_0_6_load_44 | 56 | 0.0037244 | 0.00093343 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1711-15_0_6_load_45 | 57 | 0.0041252 | 0.0010339 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1711-15_0_6_load_96 | 58 | 0.0060937 | 0.0015272 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1711-15_0_6_load_97 | 59 | 0.0044657 | 0.0011192 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1711-15_0_6_load_119 | 60 | 0.006346 | 0.0015905 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1711-15_0_6_load_94 | 61 | 0.0049084 | 0.0012302 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1711-15_0_6_load_118 | 62 | 0.0078737 | 0.0019733 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1711-15_0_6_load_114 | 63 | 0.0023456 | 0.00058786 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1711-15_0_6_load_47 | 64 | 0.012794 | 0.0032066 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1711-15_0_6_load_48 | 65 | 0.0057557 | 0.0014425 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1711-15_0_6_load_49 | 66 | 0.0083285 | 0.0020873 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1711-15_0_6_load_53 | 67 | 0.0068955 | 0.0017282 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1711-15_0_6_load_54 | 68 | 0.0079648 | 0.0019962 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1711-15_0_6_load_55 | 69 | 0.012657 | 0.0031721 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1711-15_0_6_load_63 | 73 | 0.0037016 | 0.0009277 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1711-15_0_6_load_60 | 74 | 0.003491 | 0.00087492 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1711-15_0_6_load_89 | 75 | 0.0083257 | 0.0020866 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1711-15_0_6_load_67 | 77 | 0.0043346 | 0.0010863 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1711-15_0_6_load_65 | 78 | 0.0053535 | 0.0013417 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1711-15_0_6_load_90 | 79 | 0.0063389 | 0.0015887 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1711-15_0_6_load_59 | 80 | 0.0057597 | 0.0014435 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1711-15_0_6_load_61 | 81 | 0.0025948 | 0.00065031 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1711-15_0_6_load_62 | 82 | 0.0061826 | 0.0015495 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1711-15_0_6_load_70 | 83 | 0.002492 | 0.00062454 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1711-15_0_6_load_64 | 86 | 0.016923 | 0.0042414 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1711-15_0_6_load_68 | 88 | 0.0084279 | 0.0021122 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1711-15_0_6_load_69 | 89 | 0.0018727 | 0.00046933 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1711-15_0_6_load_92 | 90 | 0.0071487 | 0.0017916 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1711-15_0_6_load_102 | 91 | 0.0030014 | 0.00075222 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1711-15_0_6_load_101 | 92 | 0.0022889 | 0.00057366 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1711-15_0_6_load_72 | 93 | 0.0077164 | 0.0019339 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1711-15_0_6_load_73 | 94 | 0.0016071 | 0.00040277 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1711-15_0_6_load_74 | 95 | 0.0038826 | 0.00097308 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1711-15_0_6_load_121 | 96 | 0.0031327 | 0.00078512 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1711-15_0_6_load_75 | 97 | 0.002177 | 0.0005456 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1711-15_0_6_load_120 | 98 | 0.0056437 | 0.0014144 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1711-15_0_6_load_113 | 99 | 0.00286 | 0.00071678 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1711-15_0_6_load_76 | 101 | 0.004923 | 0.0012338 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1711-15_0_6_load_77 | 102 | 0.0096599 | 0.002421 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1711-15_0_6_load_86 | 104 | 0.0056106 | 0.0014062 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1711-15_0_6_load_116 | 105 | 0.012171 | 0.0030504 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1711-15_0_6_load_110 | 106 | 0.0022192 | 0.00055619 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1711-15_0_6_load_85 | 107 | 0.0071293 | 0.0017868 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1711-15_0_6_load_93 | 108 | 0.0061093 | 0.0015311 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1711-15_0_6_load_98 | 109 | 0.002286 | 0.00057292 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1711-15_0_6_load_99 | 110 | 0.0022878 | 0.00057339 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1711-15_0_6_load_100 | 111 | 0.0038028 | 0.00095308 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1711-15_0_6_load_105 | 112 | 0.0071698 | 0.0017969 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1711-15_0_6_load_103 | 113 | 0.0022887 | 0.0005736 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1711-15_0_6_load_104 | 114 | 0.0087961 | 0.0022045 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1711-15_0_6_load_108 | 115 | 0.0045863 | 0.0011494 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1711-15_0_6_load_124 | 116 | 0.0050088 | 0.0012553 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 63 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-15_0_6_line_0 |  | 0 | 1 | 0.0062384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-15_0_6_line_1 |  | 1 | 2 | 0.00462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-15_0_6_line_2 |  | 2 | 3 | 0.0029891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-15_0_6_line_3 |  | 3 | 10 | 0.011915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-15_0_6_line_4 |  | 4 | 5 | 0.063987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-15_0_6_line_5 |  | 4 | 6 | 0.062083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1711-15_0_6_line_6 |  | 5 | 11 | 0.063668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-15_0_6_line_7 |  | 6 | 12 | 0.013001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-15_0_6_line_8 |  | 7 | 8 | 0.011582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-15_0_6_line_9 |  | 7 | 9 | 0.043739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-15_0_6_line_10 |  | 8 | 13 | 0.026167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1711-15_0_6_line_11 |  | 9 | 14 | 0.0098185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-15_0_6_line_12 |  | 10 | 13 | 0.015728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-15_0_6_line_13 |  | 10 | 17 | 0.030098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-15_0_6_line_14 |  | 11 | 43 | 0.022829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-15_0_6_line_15 |  | 12 | 116 | 0.012498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-15_0_6_line_16 |  | 14 | 66 | 0.0094372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-15_0_6_line_17 |  | 15 | 16 | 0.015568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-15_0_6_line_18 |  | 16 | 22 | 0.011988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-15_0_6_line_19 |  | 17 | 18 | 0.018483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-15_0_6_line_20 |  | 18 | 19 | 0.032202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-15_0_6_line_21 |  | 20 | 21 | 0.011142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-15_0_6_line_22 |  | 21 | 22 | 0.011255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1711-15_0_6_line_23 |  | 22 | 23 | 0.031253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1711-15_0_6_line_24 |  | 23 | 24 | 0.014319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-15_0_6_line_25 |  | 24 | 28 | 0.0085577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-15_0_6_line_26 |  | 25 | 26 | 0.0045369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
27 | LV_1711-15_0_6_line_27 |  | 25 | 27 | 0.014896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_1711-15_0_6_line_28 |  | 26 | 29 | 0.013274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
29 | LV_1711-15_0_6_line_29 |  | 27 | 33 | 0.018001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
30 | LV_1711-15_0_6_line_30 |  | 28 | 34 | 0.0092409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1711-15_0_6_line_31 |  | 29 | 105 | 0.023378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_1711-15_0_6_line_32 |  | 30 | 31 | 0.010187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
33 | LV_1711-15_0_6_line_33 |  | 30 | 32 | 0.015687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
34 | LV_1711-15_0_6_line_34 |  | 31 | 105 | 0.023154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_1711-15_0_6_line_35 |  | 32 | 106 | 0.027167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_1711-15_0_6_line_36 |  | 33 | 45 | 0.036199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_1711-15_0_6_line_37 |  | 33 | 40 | 0.022914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
38 | LV_1711-15_0_6_line_38 |  | 34 | 35 | 0.017794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1711-15_0_6_line_39 |  | 35 | 47 | 0.013917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1711-15_0_6_line_40 |  | 36 | 37 | 0.018305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1711-15_0_6_line_41 |  | 36 | 38 | 0.016558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1711-15_0_6_line_42 |  | 37 | 39 | 0.019501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1711-15_0_6_line_43 |  | 38 | 40 | 0.022243 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1711-15_0_6_line_44 |  | 38 | 41 | 0.038864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1711-15_0_6_line_45 |  | 39 | 42 | 0.018832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1711-15_0_6_line_46 |  | 39 | 43 | 0.0090429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1711-15_0_6_line_47 |  | 41 | 44 | 0.00057527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1711-15_0_6_line_48 |  | 44 | 46 | 0.02703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1711-15_0_6_line_49 |  | 45 | 47 | 0.0049947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1711-15_0_6_line_50 |  | 46 | 49 | 0.0030543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1711-15_0_6_line_51 |  | 47 | 48 | 0.030826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1711-15_0_6_line_52 |  | 48 | 65 | 0.035939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1711-15_0_6_line_53 |  | 49 | 50 | 0.00043717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1711-15_0_6_line_54 |  | 50 | 51 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1711-15_0_6_line_55 |  | 52 | 53 | 0.040499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1711-15_0_6_line_56 |  | 52 | 54 | 0.081233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1711-15_0_6_line_57 |  | 53 | 55 | 0.008002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1711-15_0_6_line_58 |  | 54 | 56 | 0.016643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1711-15_0_6_line_59 |  | 55 | 60 | 0.022673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1711-15_0_6_line_60 |  | 55 | 61 | 0.022223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1711-15_0_6_line_61 |  | 56 | 57 | 0.0069633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1711-15_0_6_line_62 |  | 57 | 58 | 0.015369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1711-15_0_6_line_63 |  | 58 | 59 | 0.013319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1711-15_0_6_line_64 |  | 59 | 109 | 0.019178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1711-15_0_6_line_65 |  | 60 | 98 | 0.0047809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1711-15_0_6_line_66 |  | 62 | 63 | 0.044317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1711-15_0_6_line_67 |  | 63 | 100 | 0.013446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_1711-15_0_6_line_68 |  | 64 | 65 | 0.0062206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1711-15_0_6_line_69 |  | 64 | 66 | 0.015503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1711-15_0_6_line_70 |  | 67 | 68 | 0.035707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1711-15_0_6_line_71 |  | 67 | 69 | 0.001146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1711-15_0_6_line_72 |  | 68 | 70 | 0.028269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1711-15_0_6_line_73 |  | 69 | 71 | 0.015514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1711-15_0_6_line_74 |  | 70 | 72 | 0.011028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1711-15_0_6_line_75 |  | 71 | 73 | 0.030516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1711-15_0_6_line_76 |  | 71 | 74 | 0.018506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_1711-15_0_6_line_77 |  | 72 | 75 | 0.040098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1711-15_0_6_line_78 |  | 72 | 76 | 0.013085 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1711-15_0_6_line_79 |  | 73 | 79 | 0.0029806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1711-15_0_6_line_80 |  | 74 | 80 | 0.019384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
81 | LV_1711-15_0_6_line_81 |  | 75 | 103 | 0.019408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1711-15_0_6_line_82 |  | 76 | 104 | 0.031103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1711-15_0_6_line_83 |  | 77 | 78 | 0.016467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1711-15_0_6_line_84 |  | 78 | 86 | 0.012268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1711-15_0_6_line_85 |  | 79 | 85 | 0.021943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1711-15_0_6_line_86 |  | 80 | 81 | 0.0043473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
87 | LV_1711-15_0_6_line_87 |  | 81 | 82 | 0.019751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
88 | LV_1711-15_0_6_line_88 |  | 82 | 83 | 0.0097886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_1711-15_0_6_line_89 |  | 83 | 84 | 0.013694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
90 | LV_1711-15_0_6_line_90 |  | 84 | 93 | 0.010611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
91 | LV_1711-15_0_6_line_91 |  | 84 | 94 | 0.014253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1711-15_0_6_line_92 |  | 85 | 108 | 0.019027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1711-15_0_6_line_93 |  | 85 | 90 | 0.01921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1711-15_0_6_line_94 |  | 86 | 87 | 0.021931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1711-15_0_6_line_95 |  | 87 | 88 | 0.019367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1711-15_0_6_line_96 |  | 87 | 89 | 0.013674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1711-15_0_6_line_97 |  | 88 | 90 | 0.027423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1711-15_0_6_line_98 |  | 89 | 91 | 0.018323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1711-15_0_6_line_99 |  | 91 | 92 | 0.01008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1711-15_0_6_line_100 |  | 92 | 113 | 0.0027749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1711-15_0_6_line_101 |  | 93 | 95 | 0.018987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
102 | LV_1711-15_0_6_line_102 |  | 94 | 96 | 0.019077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1711-15_0_6_line_103 |  | 95 | 97 | 0.024496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
104 | LV_1711-15_0_6_line_104 |  | 96 | 98 | 0.020114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1711-15_0_6_line_105 |  | 97 | 99 | 0.018741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
106 | LV_1711-15_0_6_line_106 |  | 99 | 100 | 0.012897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
107 | LV_1711-15_0_6_line_107 |  | 100 | 106 | 0.012134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
108 | LV_1711-15_0_6_line_108 |  | 101 | 102 | 0.032293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1711-15_0_6_line_109 |  | 102 | 103 | 0.040836 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1711-15_0_6_line_110 |  | 104 | 107 | 0.032738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1711-15_0_6_line_111 |  | 109 | 110 | 7.973e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1711-15_0_6_line_112 |  | 110 | 111 | 0.028012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1711-15_0_6_line_113 |  | 111 | 112 | 0.034335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1711-15_0_6_line_114 |  | 113 | 114 | 0.012084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1711-15_0_6_line_115 |  | 114 | 115 | 0.012373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-15_0_6_trafo_114 | 0.63 MVA 20/0.4 kV | 117 | 63 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682140.7008 | 1224922.4024 | 2682144.6665 | 1224927.218
1 | 2682137.755 | 1224918.8371 | 2682140.7008 | 1224922.4024
2 | 2682137.755 | 1224918.8371 | 2682140.0233 | 1224916.8905
3 | 2682149.0653 | 1224909.131 | 2682140.0233 | 1224916.8905
4 | 2682035.7702 | 1224824.5114 | 2682030.3562 | 1224808.0256 | 2682022.8914 | 1224782.4499 | 2682016.9751 | 1224763.3443
5 | 2682035.7702 | 1224824.5114 | 2682041.4775 | 1224823.0223 | 2682052.8009 | 1224820.0653 | 2682075.7089 | 1224812.7984 | 2682079.1512 | 1224811.7118 | 2682095.3113 | 1224806.9795
6 | 2682016.9751 | 1224763.3443 | 2682052.9022 | 1224752.7989 | 2682076.6855 | 1224741.7493
7 | 2682095.3113 | 1224806.9795 | 2682107.7881 | 1224803.3258
8 | 2682114.7391 | 1224870.22 | 2682121.97 | 1224879.2673
9 | 2682114.7391 | 1224870.22 | 2682115.3375 | 1224867.5153 | 2682117.1832 | 1224865.6394 | 2682113.8733 | 1224852.7406 | 2682122.5452 | 1224849.6137 | 2682137.7467 | 1224845.2983 | 2682137.7467 | 1224845.2983
10 | 2682138.8489 | 1224897.1733 | 2682135.8282 | 1224893.6379 | 2682134.2376 | 1224894.6166 | 2682121.97 | 1224879.2673
11 | 2682144.4358 | 1224838.1108 | 2682137.7467 | 1224845.2983
12 | 2682149.0653 | 1224909.131 | 2682138.8489 | 1224897.1733
13 | 2682149.0653 | 1224909.131 | 2682165.4043 | 1224893.268 | 2682170.5827 | 1224888.0873
14 | 2682096.0912 | 1224749.0043 | 2682089.8902 | 1224743.4025 | 2682084.4335 | 1224739.9138 | 2682077.9102 | 1224741.1802 | 2682076.6855 | 1224741.7493
15 | 2682107.7881 | 1224803.3258 | 2682109.5734 | 1224802.803 | 2682119.8104 | 1224799.9109
16 | 2682144.4358 | 1224838.1108 | 2682149.23 | 1224832.9595 | 2682150.6406 | 1224831.0177
17 | 2682273.9526 | 1224852.6841 | 2682285.2841 | 1224863.3591
18 | 2682273.9526 | 1224852.6841 | 2682265.0948 | 1224844.5784
19 | 2682170.5827 | 1224888.0873 | 2682182.396 | 1224876.2688 | 2682183.9996 | 1224875.5122
20 | 2682211.9948 | 1224859.7335 | 2682206.3472 | 1224862.6458 | 2682193.6609 | 1224870.954 | 2682183.9996 | 1224875.5122
21 | 2682249.1437 | 1224855.3876 | 2682254.2837 | 1224849.966 | 2682257.0174 | 1224852.4166
22 | 2682265.0948 | 1224844.5784 | 2682257.0174 | 1224852.4166 | 2682257.0174 | 1224852.4166
23 | 2682265.0948 | 1224844.5784 | 2682252.7026 | 1224833.2551 | 2682242.3648 | 1224823.1357
24 | 2682232.1324 | 1224813.1195 | 2682242.3648 | 1224823.1357
25 | 2682232.1324 | 1224813.1195 | 2682230.2591 | 1224811.2857 | 2682226.2597 | 1224806.899
26 | 2682180.5187 | 1224715.7675 | 2682181.0382 | 1224711.2604
27 | 2682180.5187 | 1224715.7675 | 2682178.0719 | 1224727.6751 | 2682177.3523 | 1224730.3186
28 | 2682181.1657 | 1224698.0853 | 2682181.7386 | 1224700.4629 | 2682181.518 | 1224707.0976 | 2682181.0382 | 1224711.2604
29 | 2682170.4241 | 1224746.6713 | 2682174.5412 | 1224740.6463 | 2682177.3523 | 1224730.3186
30 | 2682220.0338 | 1224800.0702 | 2682220.0338 | 1224800.0702 | 2682226.2597 | 1224806.899
31 | 2682172.3515 | 1224676.5661 | 2682179.4509 | 1224690.9693 | 2682181.1657 | 1224698.0853
32 | 2682157.6109 | 1224646.6601 | 2682162.1148 | 1224655.7976
33 | 2682157.6109 | 1224646.6601 | 2682150.0023 | 1224632.9417
34 | 2682162.1148 | 1224655.7976 | 2682172.3515 | 1224676.5661
35 | 2682136.8258 | 1224609.1842 | 2682150.0023 | 1224632.9417
36 | 2682170.4241 | 1224746.6713 | 2682186.8466 | 1224765.4218 | 2682194.5781 | 1224773.6266
37 | 2682170.4241 | 1224746.6713 | 2682163.7451 | 1224739.452 | 2682155.4905 | 1224730.4653 | 2682154.8601 | 1224729.8556
38 | 2682207.6718 | 1224787.2714 | 2682220.0338 | 1224800.0702
39 | 2682198.0036 | 1224777.2616 | 2682207.6718 | 1224787.2714
40 | 2682115.7404 | 1224740.4757 | 2682127.8859 | 1224726.7799
41 | 2682138.8717 | 1224714.3918 | 2682127.8859 | 1224726.7799
42 | 2682102.8014 | 1224755.0662 | 2682115.7404 | 1224740.4757
43 | 2682138.8717 | 1224714.3918 | 2682154.8601 | 1224729.8556
44 | 2682138.8717 | 1224714.3918 | 2682126.0172 | 1224703.5627 | 2682108.3699 | 1224690.3322
45 | 2682102.8014 | 1224755.0662 | 2682107.4428 | 1224759.9446 | 2682115.9781 | 1224768.5186
46 | 2682102.8014 | 1224755.0662 | 2682096.0912 | 1224749.0043
47 | 2682108.3699 | 1224690.3322 | 2682107.9096 | 1224689.9871
48 | 2682107.9096 | 1224689.9871 | 2682103.0673 | 1224686.3567 | 2682086.0904 | 1224674.0341
49 | 2682198.0036 | 1224777.2616 | 2682194.5781 | 1224773.6266
50 | 2682086.0904 | 1224674.0341 | 2682083.6186 | 1224672.24
51 | 2682198.0036 | 1224777.2616 | 2682195.3645 | 1224779.4823 | 2682194.6435 | 1224780.0838 | 2682181.113 | 1224783.0768 | 2682178.353 | 1224783.0721 | 2682169.2876 | 1224786.849
52 | 2682163.4087 | 1224813.442 | 2682166.7756 | 1224808.8075 | 2682167.1755 | 1224804.5545 | 2682159.1438 | 1224794.8149 | 2682163.6037 | 1224789.2171 | 2682169.2876 | 1224786.849
53 | 2682083.6186 | 1224672.24 | 2682083.2648 | 1224671.9832
54 | 2682064.5167 | 1224658.3749 | 2682083.2648 | 1224671.9832
55 | 2682028.4586 | 1224583.2473 | 2682044.0812 | 1224568.2413 | 2682049.8188 | 1224560.7264 | 2682054.3083 | 1224552.4383
56 | 2682028.4586 | 1224583.2473 | 2682022.6411 | 1224576.218 | 2682014.1492 | 1224565.1602 | 2682002.7323 | 1224546.8127 | 2681990.8398 | 1224523.9112 | 2681985.3786 | 1224514.6506
57 | 2682054.3083 | 1224552.4383 | 2682055.7892 | 1224544.5756
58 | 2681985.3786 | 1224514.6506 | 2681976.9245 | 1224500.3147
59 | 2682055.7892 | 1224544.5756 | 2682075.9442 | 1224534.1904
60 | 2682055.7892 | 1224544.5756 | 2682056.3283 | 1224534.6318 | 2682055.7505 | 1224522.3812
61 | 2681972.5734 | 1224494.8782 | 2681976.9245 | 1224500.3147 | 2681976.9245 | 1224500.3147
62 | 2681972.5734 | 1224494.8782 | 2681962.97 | 1224482.8791
63 | 2681962.97 | 1224482.8791 | 2681954.6476 | 1224472.4806
64 | 2681954.6476 | 1224472.4806 | 2681942.6639 | 1224457.5073
65 | 2682075.9442 | 1224534.1904 | 2682080.1942 | 1224532.0006
66 | 2682085.59 | 1224588.3689 | 2682093.8835 | 1224599.0821 | 2682105.6803 | 1224610.7527 | 2682117.8656 | 1224603.5119
67 | 2682129.9581 | 1224599.3465 | 2682125.887 | 1224598.7455 | 2682117.8656 | 1224603.5119
68 | 2682159.7526 | 1224818.4748 | 2682163.4087 | 1224813.442
69 | 2682159.7526 | 1224818.4748 | 2682150.6406 | 1224831.0177
70 | 2682106.9618 | 1224429.685 | 2682110.9565 | 1224425.1443 | 2682126.5129 | 1224412.2279 | 2682134.7361 | 1224407.5923
71 | 2682106.9618 | 1224429.685 | 2682106.2048 | 1224430.5454
72 | 2682157.3439 | 1224391.4392 | 2682154.1839 | 1224396.2322 | 2682147.6518 | 1224400.3115 | 2682134.7361 | 1224407.5923
73 | 2682095.9574 | 1224442.1934 | 2682106.2048 | 1224430.5454
74 | 2682157.3439 | 1224391.4392 | 2682162.3479 | 1224391.4972 | 2682167.9739 | 1224393.7319
75 | 2682095.9574 | 1224442.1934 | 2682080.1081 | 1224462.055 | 2682075.7966 | 1224464.7904
76 | 2682095.9574 | 1224442.1934 | 2682107.2673 | 1224451.8003 | 2682109.465 | 1224454.7348
77 | 2682167.9739 | 1224393.7319 | 2682171.9956 | 1224399.5692 | 2682180.6992 | 1224414.5105 | 2682186.9623 | 1224424.4148 | 2682189.9841 | 1224427.0353
78 | 2682167.9739 | 1224393.7319 | 2682172.2318 | 1224385.7631 | 2682174.3648 | 1224382.3124
79 | 2682075.7966 | 1224464.7904 | 2682073.2798 | 1224466.3872
80 | 2682119.2955 | 1224471.2544 | 2682116.3882 | 1224463.9788 | 2682109.465 | 1224454.7348
81 | 2682207.2001 | 1224435.4572 | 2682200.0401 | 1224433.3903 | 2682192.747 | 1224429.4314 | 2682189.9841 | 1224427.0353
82 | 2682174.3648 | 1224382.3124 | 2682173.8444 | 1224376.0677 | 2682167.8549 | 1224371.0483 | 2682160.1059 | 1224369.8961 | 2682150.9584 | 1224369.0363
83 | 2682074.544 | 1224398.2933 | 2682065.1665 | 1224397.4386 | 2682058.1178 | 1224397.6091
84 | 2682045.9482 | 1224398.432 | 2682047.5986 | 1224397.8635 | 2682058.1178 | 1224397.6091
85 | 2682051.9223 | 1224470.8835 | 2682061.0703 | 1224469.0084 | 2682071.8923 | 1224467.2675 | 2682073.2798 | 1224466.3872
86 | 2682119.2955 | 1224471.2544 | 2682120.9087 | 1224475.2914
87 | 2682126.0136 | 1224494.3324 | 2682122.4865 | 1224479.2399 | 2682120.9087 | 1224475.2914
88 | 2682128.2412 | 1224503.8641 | 2682126.0136 | 1224494.3324
89 | 2682131.3576 | 1224517.1991 | 2682128.2412 | 1224503.8641
90 | 2682131.3576 | 1224517.1991 | 2682132.5388 | 1224522.2633 | 2682133.6451 | 1224527.56
91 | 2682131.3576 | 1224517.1991 | 2682117.4614 | 1224520.3697
92 | 2682051.9223 | 1224470.8835 | 2682053.615 | 1224483.4042 | 2682053.9876 | 1224489.7854
93 | 2682051.9223 | 1224470.8835 | 2682044.8035 | 1224453.0417
94 | 2682027.4636 | 1224409.5828 | 2682037.3585 | 1224401.3914 | 2682045.9482 | 1224398.432
95 | 2682027.4636 | 1224409.5828 | 2682034.6408 | 1224427.5711
96 | 2682027.4636 | 1224409.5828 | 2682018.9738 | 1224413.7576 | 2682014.9559 | 1224415.0255
97 | 2682034.6408 | 1224427.5711 | 2682044.8035 | 1224453.0417
98 | 2682014.9559 | 1224415.0255 | 2682010.2306 | 1224416.5168 | 2682001.1273 | 1224417.3475 | 2681996.9393 | 1224416.7774
99 | 2681986.9511 | 1224415.4176 | 2681996.9393 | 1224416.7774
100 | 2681986.9511 | 1224415.4176 | 2681986.9511 | 1224415.4176 | 2681984.5299 | 1224414.062
101 | 2682133.6451 | 1224527.56 | 2682137.5269 | 1224546.1456
102 | 2682117.4614 | 1224520.3697 | 2682113.3905 | 1224521.2985 | 2682099.0066 | 1224525.1925
103 | 2682141.2639 | 1224570.296 | 2682140.7041 | 1224561.3579 | 2682137.5269 | 1224546.1456
104 | 2682099.0066 | 1224525.1925 | 2682087.208 | 1224528.3866 | 2682080.1942 | 1224532.0006
105 | 2682135.592 | 1224587.7791 | 2682138.8592 | 1224582.3912 | 2682141.4248 | 1224572.8645 | 2682141.2639 | 1224570.296
106 | 2682129.9581 | 1224599.3465 | 2682133.2027 | 1224591.7194 | 2682135.592 | 1224587.7791
107 | 2682129.9581 | 1224599.3465 | 2682132.8408 | 1224601.9992 | 2682136.8258 | 1224609.1842
108 | 2682197.2684 | 1224503.5898 | 2682190.7747 | 1224476.6917 | 2682190.9449 | 1224472.073
109 | 2682207.2001 | 1224435.4572 | 2682201.912 | 1224445.5466 | 2682197.5115 | 1224451.2119 | 2682193.7145 | 1224458.1975 | 2682191.1993 | 1224465.1675 | 2682190.9449 | 1224472.073
110 | 2682118.4668 | 1224365.5502 | 2682121.1477 | 1224366.3785 | 2682135.588 | 1224367.8564 | 2682147.0725 | 1224368.671 | 2682150.9584 | 1224369.0363
111 | 2681942.6639 | 1224457.5073 | 2681942.6141 | 1224457.445
112 | 2681926.0245 | 1224434.9234 | 2681931.4221 | 1224443.461 | 2681942.6141 | 1224457.445
113 | 2681926.0245 | 1224434.9234 | 2681922.4943 | 1224429.3397 | 2681915.9715 | 1224416.7859 | 2681911.627 | 1224403.9173
114 | 2681974.5968 | 1224407.2597 | 2681979.4789 | 1224411.2341 | 2681984.5299 | 1224414.062
115 | 2681965.3795 | 1224399.02 | 2681970.5179 | 1224403.9391 | 2681974.5968 | 1224407.2597

## bus_geodata
| x | y | coords
0 | 2682144.6665 | 1224927.218
1 | 2682140.7008 | 1224922.4024
2 | 2682137.755 | 1224918.8371
3 | 2682140.0233 | 1224916.8905
4 | 2682035.7702 | 1224824.5114
5 | 2682016.9751 | 1224763.3443
6 | 2682095.3113 | 1224806.9795
7 | 2682114.7391 | 1224870.22
8 | 2682121.97 | 1224879.2673
9 | 2682137.7467 | 1224845.2983
10 | 2682149.0653 | 1224909.131
11 | 2682076.6855 | 1224741.7493
12 | 2682107.7881 | 1224803.3258
13 | 2682138.8489 | 1224897.1733
14 | 2682144.4358 | 1224838.1108
15 | 2682285.2841 | 1224863.3591
16 | 2682273.9526 | 1224852.6841
17 | 2682170.5827 | 1224888.0873
18 | 2682183.9996 | 1224875.5122
19 | 2682211.9948 | 1224859.7335
20 | 2682249.1437 | 1224855.3876
21 | 2682257.0174 | 1224852.4166
22 | 2682265.0948 | 1224844.5784
23 | 2682242.3648 | 1224823.1357
24 | 2682232.1324 | 1224813.1195
25 | 2682180.5187 | 1224715.7675
26 | 2682181.0382 | 1224711.2604
27 | 2682177.3523 | 1224730.3186
28 | 2682226.2597 | 1224806.899
29 | 2682181.1657 | 1224698.0853
30 | 2682157.6109 | 1224646.6601
31 | 2682162.1148 | 1224655.7976
32 | 2682150.0023 | 1224632.9417
33 | 2682170.4241 | 1224746.6713
34 | 2682220.0338 | 1224800.0702
35 | 2682207.6718 | 1224787.2714
36 | 2682127.8859 | 1224726.7799
37 | 2682115.7404 | 1224740.4757
38 | 2682138.8717 | 1224714.3918
39 | 2682102.8014 | 1224755.0662
40 | 2682154.8601 | 1224729.8556
41 | 2682108.3699 | 1224690.3322
42 | 2682115.9781 | 1224768.5186
43 | 2682096.0912 | 1224749.0043
44 | 2682107.9096 | 1224689.9871
45 | 2682194.5781 | 1224773.6266
46 | 2682086.0904 | 1224674.0341
47 | 2682198.0036 | 1224777.2616
48 | 2682169.2876 | 1224786.849
49 | 2682083.6186 | 1224672.24
50 | 2682083.2648 | 1224671.9832
51 | 2682064.5167 | 1224658.3749
52 | 2682028.4586 | 1224583.2473
53 | 2682054.3083 | 1224552.4383
54 | 2681985.3786 | 1224514.6506
55 | 2682055.7892 | 1224544.5756
56 | 2681976.9245 | 1224500.3147
57 | 2681972.5734 | 1224494.8782
58 | 2681962.97 | 1224482.8791
59 | 2681954.6476 | 1224472.4806
60 | 2682075.9442 | 1224534.1904
61 | 2682055.7505 | 1224522.3812
62 | 2682085.59 | 1224588.3689
63 | 2682117.8656 | 1224603.5119
64 | 2682159.7526 | 1224818.4748
65 | 2682163.4087 | 1224813.442
66 | 2682150.6407 | 1224831.0177
67 | 2682106.9618 | 1224429.685
68 | 2682134.7361 | 1224407.5923
69 | 2682106.2048 | 1224430.5454
70 | 2682157.3439 | 1224391.4392
71 | 2682095.9574 | 1224442.1934
72 | 2682167.9739 | 1224393.7319
73 | 2682075.7966 | 1224464.7904
74 | 2682109.465 | 1224454.7348
75 | 2682189.984 | 1224427.0353
76 | 2682174.3648 | 1224382.3124
77 | 2682074.544 | 1224398.2933
78 | 2682058.1178 | 1224397.6091
79 | 2682073.2798 | 1224466.3872
80 | 2682119.2955 | 1224471.2544
81 | 2682120.9087 | 1224475.2914
82 | 2682126.0136 | 1224494.3324
83 | 2682128.2412 | 1224503.8641
84 | 2682131.3576 | 1224517.1991
85 | 2682051.9223 | 1224470.8835
86 | 2682045.9482 | 1224398.432
87 | 2682027.4636 | 1224409.5828
88 | 2682034.6408 | 1224427.5711
89 | 2682014.9559 | 1224415.0255
90 | 2682044.8035 | 1224453.0417
91 | 2681996.9393 | 1224416.7774
92 | 2681986.9511 | 1224415.4176
93 | 2682133.6451 | 1224527.56
94 | 2682117.4614 | 1224520.3697
95 | 2682137.5269 | 1224546.1456
96 | 2682099.0066 | 1224525.1925
97 | 2682141.2639 | 1224570.296
98 | 2682080.1942 | 1224532.0006
99 | 2682135.592 | 1224587.7791
100 | 2682129.9581 | 1224599.3465
101 | 2682197.2684 | 1224503.5898
102 | 2682190.9449 | 1224472.073
103 | 2682207.2001 | 1224435.4572
104 | 2682150.9584 | 1224369.0363
105 | 2682172.3515 | 1224676.5661
106 | 2682136.8258 | 1224609.1842
107 | 2682118.4668 | 1224365.5502
108 | 2682053.9876 | 1224489.7854
109 | 2681942.6639 | 1224457.5073
110 | 2681942.6141 | 1224457.445
111 | 2681926.0245 | 1224434.9234
112 | 2681911.627 | 1224403.9173
113 | 2681984.5299 | 1224414.062
114 | 2681974.5968 | 1224407.2597
115 | 2681965.3795 | 1224399.02
116 | 2682119.8104 | 1224799.9109
117 | 2682129.9581 | 1224599.3465

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97675 | -0.44842 | 0.0026029 | 0.00065234
1 | 0.97677 | -0.44812 | 0 | 0
2 | 0.97678 | -0.4479 | 0 | 0
3 | 0.97679 | -0.44776 | 0.0017275 | 0.00043295
4 | 0.97666 | -0.45004 | 0 | 0
5 | 0.97799 | -0.42406 | 0 | 0
6 | 0.97538 | -0.4753 | 0.0045421 | 0.0011383
7 | 0.97794 | -0.42512 | 0 | 0
8 | 0.97764 | -0.43094 | 0.0045609 | 0.0011431
9 | 0.97906 | -0.40317 | 0.005998 | 0.0015032
10 | 0.97683 | -0.44682 | 0 | 0
11 | 0.9793 | -0.39829 | 0.020874 | 0.0052314
12 | 0.97517 | -0.47952 | 0.012688 | 0.00318
13 | 0.97708 | -0.44192 | 0.0059629 | 0.0014944
14 | 0.97936 | -0.39718 | 0.015253 | 0.0038228
15 | 0.98389 | -0.30909 | 0.0019236 | 0.00048211
16 | 0.98391 | -0.30855 | 0 | 0
17 | 0.97648 | -0.45381 | 0.0045052 | 0.0011291
18 | 0.97634 | -0.45658 | 0.0026496 | 0.00066405
19 | 0.97617 | -0.45985 | 0.0055511 | 0.0013912
20 | 0.98379 | -0.31087 | 0.0056708 | 0.0014212
21 | 0.98385 | -0.30974 | 0.0022153 | 0.0005552
22 | 0.98393 | -0.30814 | 0 | 0
23 | 0.98422 | -0.30262 | 0.0040353 | 0.0010113
24 | 0.9844 | -0.29905 | 0.011855 | 0.0029712
25 | 0.99085 | -0.17417 | 0 | 0
26 | 0.9911 | -0.16935 | 0.0050111 | 0.0012559
27 | 0.99003 | -0.19 | 0.0054824 | 0.001374
28 | 0.9846 | -0.2951 | 0.0018174 | 0.00045549
29 | 0.99185 | -0.15503 | 0.0043206 | 0.0010829
30 | 0.99518 | -0.091522 | 0 | 0
31 | 0.99456 | -0.10329 | 0.0073615 | 0.001845
32 | 0.99613 | -0.073423 | 0.0061595 | 0.0015437
33 | 0.98905 | -0.20883 | 0 | 0
34 | 0.98484 | -0.29053 | 0.0096825 | 0.0024267
35 | 0.98545 | -0.27864 | 0.0098752 | 0.002475
36 | 0.98321 | -0.32205 | 0.011324 | 0.0028382
37 | 0.98188 | -0.34789 | 0.011529 | 0.0028895
38 | 0.98458 | -0.29537 | 0 | 0
39 | 0.98068 | -0.37142 | 0 | 0
40 | 0.98745 | -0.23982 | 0.012259 | 0.0030724
41 | 0.98279 | -0.33022 | 0.012321 | 0.0030878
42 | 0.98047 | -0.37543 | 0.011751 | 0.002945
43 | 0.98022 | -0.38042 | 0.011781 | 0.0029526
44 | 0.98277 | -0.33061 | 0.011291 | 0.0028298
45 | 0.98667 | -0.25479 | 0.0069495 | 0.0017417
46 | 0.98212 | -0.34339 | 0.012164 | 0.0030485
47 | 0.98605 | -0.26688 | 0 | 0
48 | 0.98353 | -0.31571 | 0.012438 | 0.0031172
49 | 0.98208 | -0.34416 | 0.0025589 | 0.00064133
50 | 0.98208 | -0.34425 | 0.0025589 | 0.00064133
51 | 0.98189 | -0.34798 | 0.0088966 | 0.0022297
52 | 0.98872 | -0.21609 | 0 | 0
53 | 0.99028 | -0.18598 | 0 | 0
54 | 0.9856 | -0.27676 | 0.0077976 | 0.0019543
55 | 0.99059 | -0.18005 | 0 | 0
56 | 0.98508 | -0.28691 | 0.0037244 | 0.00093343
57 | 0.98489 | -0.29069 | 0.0041252 | 0.0010339
58 | 0.98452 | -0.2979 | 0.0060937 | 0.0015272
59 | 0.98427 | -0.3027 | 0.0044657 | 0.0011192
60 | 0.99156 | -0.16127 | 0.006346 | 0.0015905
61 | 0.99049 | -0.18198 | 0.0049084 | 0.0012302
62 | 0.99968 | -0.0060843 | 0.0078737 | 0.0019733
63 | 1 | 0 | -0.599 | -0.15284
64 | 0.98061 | -0.37274 | 0.012794 | 0.0032066
65 | 0.98101 | -0.36486 | 0.0057557 | 0.0014425
66 | 0.97979 | -0.38881 | 0.0083285 | 0.0020873
67 | 0.99069 | -0.17814 | 0.0068955 | 0.0017282
68 | 0.98926 | -0.20585 | 0.0079648 | 0.0019962
69 | 0.99075 | -0.17712 | 0.012657 | 0.0031721
70 | 0.98834 | -0.22381 | 0 | 0
71 | 0.99164 | -0.15973 | 0 | 0
72 | 0.98798 | -0.23083 | 0 | 0
73 | 0.98936 | -0.20374 | 0.0037016 | 0.0009277
74 | 0.99287 | -0.13608 | 0.003491 | 0.00087492
75 | 0.98713 | -0.24725 | 0.0083257 | 0.0020866
76 | 0.98782 | -0.23381 | 0 | 0
77 | 0.9835 | -0.31766 | 0.0043346 | 0.0010863
78 | 0.98357 | -0.31637 | 0.0053535 | 0.0013417
79 | 0.98915 | -0.20785 | 0.0063389 | 0.0015887
80 | 0.9934 | -0.12595 | 0.0057597 | 0.0014435
81 | 0.99352 | -0.1236 | 0.0025948 | 0.00065031
82 | 0.99409 | -0.11271 | 0.0061826 | 0.0015495
83 | 0.99438 | -0.1071 | 0.002492 | 0.00062454
84 | 0.9948 | -0.099144 | 0 | 0
85 | 0.98771 | -0.2357 | 0 | 0
86 | 0.98368 | -0.31423 | 0.016923 | 0.0042414
87 | 0.98422 | -0.30372 | 0 | 0
88 | 0.9851 | -0.28651 | 0.0084279 | 0.0021122
89 | 0.98393 | -0.30934 | 0.0018727 | 0.00046933
90 | 0.98656 | -0.25804 | 0.0071487 | 0.0017916
91 | 0.98357 | -0.31626 | 0.0030014 | 0.00075222
92 | 0.98341 | -0.31952 | 0.0022889 | 0.00057366
93 | 0.99524 | -0.090615 | 0.0077164 | 0.0019339
94 | 0.99397 | -0.11507 | 0.0016071 | 0.00040277
95 | 0.99607 | -0.074858 | 0.0038826 | 0.00097308
96 | 0.99288 | -0.13589 | 0.0031327 | 0.00078512
97 | 0.99714 | -0.054233 | 0.002177 | 0.0005456
98 | 0.9918 | -0.15678 | 0.0056437 | 0.0014144
99 | 0.99798 | -0.038341 | 0.00286 | 0.00071678
100 | 0.99856 | -0.027291 | 0 | 0
101 | 0.98618 | -0.26583 | 0.004923 | 0.0012338
102 | 0.98632 | -0.26298 | 0.0096599 | 0.002421
103 | 0.98687 | -0.25232 | 0 | 0
104 | 0.98746 | -0.24089 | 0.0056106 | 0.0014062
105 | 0.99319 | -0.1295 | 0.012171 | 0.0030504
106 | 0.9978 | -0.041575 | 0.0022192 | 0.00055619
107 | 0.98724 | -0.24506 | 0.0071293 | 0.0017868
108 | 0.98761 | -0.23778 | 0.0061093 | 0.0015311
109 | 0.984 | -0.30807 | 0.002286 | 0.00057292
110 | 0.98399 | -0.30808 | 0.0022878 | 0.00057339
111 | 0.98371 | -0.31362 | 0.0038028 | 0.00095308
112 | 0.98348 | -0.31805 | 0.0071698 | 0.0017969
113 | 0.98337 | -0.32031 | 0.0022887 | 0.0005736
114 | 0.98322 | -0.32322 | 0.0087961 | 0.0022045
115 | 0.98317 | -0.32425 | 0.0045863 | 0.0011494
116 | 0.97511 | -0.48066 | 0.0050088 | 0.0012553
117 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0026029 | -0.00065234 | 0.0026029 | 0.00065229 | 3.6784e-08 | -5.4542e-08 | 0.0039653 | 0.0039653 | 0.0039653 | 0.97675 | -0.44842 | 0.97677 | -0.44812 | 1.0894
1 | -0.0026029 | -0.00065229 | 0.0026029 | 0.00065225 | 2.7241e-08 | -4.0394e-08 | 0.0039653 | 0.0039652 | 0.0039653 | 0.97677 | -0.44812 | 0.97678 | -0.4479 | 1.0894
2 | -0.0026029 | -0.00065225 | 0.0026029 | 0.00065222 | 1.7624e-08 | -2.6135e-08 | 0.0039652 | 0.0039652 | 0.0039652 | 0.97678 | -0.4479 | 0.97679 | -0.44776 | 1.0894
3 | -0.0043304 | -0.0010852 | 0.0043306 | 0.0010851 | 1.9444e-07 | -2.4707e-08 | 0.0065968 | 0.0065968 | 0.0065968 | 0.97679 | -0.44776 | 0.97683 | -0.44682 | 1.8123
4 | -0.02227 | -0.0055922 | 0.022297 | 0.0056091 | 2.763e-05 | 1.6881e-05 | 0.033934 | 0.033933 | 0.033934 | 0.97666 | -0.45004 | 0.97799 | -0.42406 | 9.3224
5 | 0.02227 | 0.0055922 | -0.022243 | -0.0055758 | 2.6808e-05 | 1.6381e-05 | 0.033934 | 0.033934 | 0.033934 | 0.97666 | -0.45004 | 0.97538 | -0.4753 | 9.3225
6 | -0.022297 | -0.0056091 | 0.022325 | 0.0056259 | 2.7491e-05 | 1.6795e-05 | 0.033933 | 0.033933 | 0.033933 | 0.97799 | -0.42406 | 0.9793 | -0.39829 | 9.3223
7 | 0.017701 | 0.0044375 | -0.017697 | -0.0044353 | 3.5553e-06 | 2.1132e-06 | 0.027005 | 0.027005 | 0.027005 | 0.97538 | -0.4753 | 0.97517 | -0.47952 | 7.4189
8 | 0.02759 | 0.0069245 | -0.027583 | -0.0069197 | 7.6558e-06 | 4.7544e-06 | 0.041984 | 0.041984 | 0.041984 | 0.97794 | -0.42512 | 0.97764 | -0.43094 | 11.5342
9 | -0.02759 | -0.0069245 | 0.027619 | 0.0069424 | 2.8912e-05 | 1.7954e-05 | 0.041984 | 0.041984 | 0.041984 | 0.97794 | -0.42512 | 0.97906 | -0.40317 | 11.5342
10 | 0.023022 | 0.0057767 | -0.02301 | -0.0057693 | 1.205e-05 | 7.3839e-06 | 0.035043 | 0.035043 | 0.035043 | 0.97764 | -0.43094 | 0.97708 | -0.44192 | 9.6271
11 | -0.033617 | -0.0084457 | 0.033627 | 0.0084517 | 9.6144e-06 | 6.0297e-06 | 0.0511 | 0.0511 | 0.0511 | 0.97906 | -0.40317 | 0.97936 | -0.39718 | 14.0385
12 | -0.017043 | -0.0042725 | 0.017047 | 0.0042748 | 3.9752e-06 | 2.3472e-06 | 0.025962 | 0.025962 | 0.025962 | 0.97683 | -0.44682 | 0.97708 | -0.44192 | 7.1323
13 | 0.012712 | 0.0031874 | -0.012708 | -0.003185 | 4.2325e-06 | 2.3322e-06 | 0.019365 | 0.019365 | 0.019365 | 0.97683 | -0.44682 | 0.97648 | -0.45381 | 5.3201
14 | -0.043199 | -0.010857 | 0.043235 | 0.010881 | 3.6896e-05 | 2.3326e-05 | 0.06565 | 0.06565 | 0.06565 | 0.9793 | -0.39829 | 0.98022 | -0.38042 | 18.0356
15 | 0.005009 | 0.0012553 | -0.0050088 | -0.0012553 | 2.738e-07 | 1.9321e-08 | 0.0076433 | 0.0076434 | 0.0076434 | 0.97517 | -0.47952 | 0.97511 | -0.48066 | 2.0998
16 | -0.04888 | -0.012274 | 0.048899 | 0.012287 | 1.9524e-05 | 1.2376e-05 | 0.074275 | 0.074275 | 0.074275 | 0.97936 | -0.39718 | 0.97979 | -0.38881 | 20.4053
17 | -0.0019236 | -0.00048211 | 0.0019237 | 0.00048194 | 4.9411e-08 | -1.6609e-07 | 0.0029093 | 0.0029092 | 0.0029093 | 0.98389 | -0.30909 | 0.98391 | -0.30855 | 0.79926
18 | -0.0019237 | -0.00048194 | 0.0019237 | 0.00048182 | 3.8047e-08 | -1.2791e-07 | 0.0029092 | 0.0029092 | 0.0029092 | 0.98391 | -0.30855 | 0.98393 | -0.30814 | 0.79924
19 | 0.0082027 | 0.0020559 | -0.0082016 | -0.0020554 | 1.083e-06 | 4.6192e-07 | 0.0125 | 0.0125 | 0.0125 | 0.97648 | -0.45381 | 0.97634 | -0.45658 | 3.434
20 | 0.005552 | 0.0013914 | -0.0055511 | -0.0013912 | 8.6462e-07 | 1.5072e-07 | 0.0084616 | 0.0084618 | 0.0084618 | 0.97634 | -0.45658 | 0.97617 | -0.45985 | 2.3247
21 | -0.0056708 | -0.0014212 | 0.0056711 | 0.0014213 | 3.0739e-07 | 5.5244e-08 | 0.0085772 | 0.0085772 | 0.0085772 | 0.98379 | -0.31087 | 0.98385 | -0.30974 | 2.3564
22 | -0.0078864 | -0.0019765 | 0.007887 | 0.0019767 | 6.0048e-07 | 2.4136e-07 | 0.011928 | 0.011928 | 0.011928 | 0.98385 | -0.30974 | 0.98393 | -0.30814 | 3.2768
23 | -0.0098107 | -0.0024585 | 0.0098133 | 0.0024598 | 2.5798e-06 | 1.254e-06 | 0.014837 | 0.014837 | 0.014837 | 0.98393 | -0.30814 | 0.98422 | -0.30262 | 4.076
24 | -0.013849 | -0.0034711 | 0.013851 | 0.0034725 | 2.3539e-06 | 1.3245e-06 | 0.020938 | 0.020937 | 0.020938 | 0.98422 | -0.30262 | 0.9844 | -0.29905 | 5.7521
25 | -0.025706 | -0.0064436 | 0.025711 | 0.0064466 | 4.8455e-06 | 2.9923e-06 | 0.038858 | 0.038858 | 0.038858 | 0.9844 | -0.29905 | 0.9846 | -0.2951 | 10.6752
26 | -0.30182 | -0.076655 | 0.30189 | 0.076699 | 7.0017e-05 | 4.4518e-05 | 0.45362 | 0.45362 | 0.45362 | 0.99085 | -0.17417 | 0.9911 | -0.16935 | 24.924
27 | 0.30182 | 0.076655 | -0.30159 | -0.076509 | 0.00022989 | 0.00014617 | 0.45362 | 0.45362 | 0.45362 | 0.99085 | -0.17417 | 0.99003 | -0.19 | 24.924
28 | -0.3069 | -0.077955 | 0.30711 | 0.07809 | 0.00021171 | 0.00013464 | 0.46114 | 0.46114 | 0.46114 | 0.9911 | -0.16935 | 0.99185 | -0.15503 | 25.3374
29 | 0.29611 | 0.075135 | -0.29584 | -0.074964 | 0.0002678 | 0.00017024 | 0.44538 | 0.44538 | 0.44538 | 0.99003 | -0.19 | 0.98905 | -0.20883 | 24.4713
30 | -0.027528 | -0.0069021 | 0.027534 | 0.0069058 | 5.9982e-06 | 3.7213e-06 | 0.041604 | 0.041604 | 0.041604 | 0.9846 | -0.2951 | 0.98484 | -0.29053 | 11.4297
31 | -0.31143 | -0.079173 | 0.31182 | 0.079417 | 0.0003834 | 0.00024386 | 0.46762 | 0.46762 | 0.46762 | 0.99185 | -0.15503 | 0.99319 | -0.1295 | 25.6935
32 | 0.33195 | 0.084693 | -0.33176 | -0.084573 | 0.00018863 | 0.00012006 | 0.49687 | 0.49687 | 0.49687 | 0.99518 | -0.091522 | 0.99456 | -0.10329 | 27.3006
33 | -0.33195 | -0.084693 | 0.33224 | 0.084878 | 0.00029046 | 0.00018487 | 0.49687 | 0.49687 | 0.49687 | 0.99518 | -0.091522 | 0.99613 | -0.073423 | 27.3006
34 | 0.3244 | 0.082728 | -0.32399 | -0.082467 | 0.00040993 | 0.00026085 | 0.48586 | 0.48586 | 0.48586 | 0.99456 | -0.10329 | 0.99319 | -0.1295 | 26.6954
35 | -0.3384 | -0.086421 | 0.33892 | 0.086754 | 0.00052182 | 0.0003322 | 0.50607 | 0.50607 | 0.50607 | 0.99613 | -0.073423 | 0.9978 | -0.041575 | 27.8061
36 | 0.14315 | 0.036262 | -0.14284 | -0.036061 | 0.00031524 | 0.00020083 | 0.21551 | 0.21551 | 0.21551 | 0.98905 | -0.20883 | 0.98667 | -0.25479 | 29.6033
37 | 0.15268 | 0.038703 | -0.15246 | -0.038558 | 0.00022702 | 0.0001447 | 0.22987 | 0.22987 | 0.22987 | 0.98905 | -0.20883 | 0.98745 | -0.23982 | 31.5751
38 | -0.037217 | -0.0093325 | 0.037238 | 0.0093458 | 2.1101e-05 | 1.3278e-05 | 0.056234 | 0.056234 | 0.056234 | 0.98484 | -0.29053 | 0.98545 | -0.27864 | 15.4488
39 | -0.047113 | -0.011821 | 0.04714 | 0.011837 | 2.6415e-05 | 1.6728e-05 | 0.071145 | 0.071145 | 0.071145 | 0.98545 | -0.27864 | 0.98605 | -0.26688 | 19.5454
40 | 0.078494 | 0.019794 | -0.078397 | -0.019732 | 9.6945e-05 | 6.1813e-05 | 0.11884 | 0.11884 | 0.11884 | 0.98321 | -0.32205 | 0.98188 | -0.34789 | 32.648
41 | -0.089819 | -0.022632 | 0.089933 | 0.022705 | 0.00011481 | 7.3265e-05 | 0.13598 | 0.13598 | 0.13598 | 0.98321 | -0.32205 | 0.98458 | -0.29537 | 37.3565
42 | 0.066868 | 0.016842 | -0.066793 | -0.016794 | 7.5142e-05 | 4.7845e-05 | 0.10137 | 0.10137 | 0.10137 | 0.98188 | -0.34789 | 0.98068 | -0.37142 | 27.848
43 | -0.13983 | -0.035247 | 0.1402 | 0.035486 | 0.00037274 | 0.00023827 | 0.21139 | 0.21139 | 0.21139 | 0.98458 | -0.29537 | 0.98745 | -0.23982 | 58.0751
44 | 0.049892 | 0.012542 | -0.049809 | -0.01249 | 8.2891e-05 | 5.2557e-05 | 0.075416 | 0.075416 | 0.075416 | 0.98458 | -0.29537 | 0.98279 | -0.33022 | 20.7187
45 | 0.011753 | 0.0029462 | -0.011751 | -0.002945 | 2.2458e-06 | 1.1998e-06 | 0.017833 | 0.017833 | 0.017833 | 0.98068 | -0.37142 | 0.98047 | -0.37543 | 4.8992
46 | 0.05504 | 0.013848 | -0.055016 | -0.013833 | 2.3663e-05 | 1.503e-05 | 0.083534 | 0.083534 | 0.083534 | 0.98068 | -0.37142 | 0.98022 | -0.38042 | 22.9488
47 | 0.037488 | 0.009402 | -0.037487 | -0.0094016 | 6.9505e-07 | 4.3754e-07 | 0.056762 | 0.056762 | 0.056762 | 0.98279 | -0.33022 | 0.98277 | -0.33061 | 15.5939
48 | 0.026196 | 0.0065718 | -0.02618 | -0.0065619 | 1.5948e-05 | 9.8646e-06 | 0.039666 | 0.039666 | 0.039666 | 0.98277 | -0.33061 | 0.98212 | -0.34339 | 10.8973
49 | 0.13589 | 0.034319 | -0.13581 | -0.034269 | 7.8738e-05 | 5.0329e-05 | 0.20503 | 0.20503 | 0.20503 | 0.98667 | -0.25479 | 0.98605 | -0.26688 | 56.3273
50 | 0.014017 | 0.0035134 | -0.014016 | -0.0035131 | 5.1656e-07 | 2.9195e-07 | 0.021237 | 0.021237 | 0.021237 | 0.98212 | -0.34339 | 0.98208 | -0.34416 | 5.8343
51 | 0.088672 | 0.022431 | -0.088465 | -0.022299 | 0.00020722 | 0.00013223 | 0.13389 | 0.13389 | 0.13389 | 0.98605 | -0.26688 | 0.98353 | -0.31571 | 36.782
52 | 0.076027 | 0.019182 | -0.075848 | -0.019068 | 0.00017845 | 0.00011375 | 0.11507 | 0.11507 | 0.11507 | 0.98353 | -0.31571 | 0.98101 | -0.36486 | 31.6123
53 | 0.011457 | 0.0028718 | -0.011457 | -0.0028717 | 4.9404e-08 | 2.6087e-08 | 0.01736 | 0.01736 | 0.01736 | 0.98208 | -0.34416 | 0.98208 | -0.34425 | 4.7691
54 | 0.0088982 | 0.0022304 | -0.0088966 | -0.0022297 | 1.5792e-06 | 7.176e-07 | 0.013482 | 0.013483 | 0.013483 | 0.98208 | -0.34425 | 0.98189 | -0.34798 | 3.704
55 | -0.041918 | -0.010567 | 0.041979 | 0.010606 | 6.0485e-05 | 3.819e-05 | 0.063108 | 0.063108 | 0.063108 | 0.98872 | -0.21609 | 0.99028 | -0.18598 | 17.3375
56 | 0.041918 | 0.010567 | -0.041797 | -0.010491 | 0.00012132 | 7.6607e-05 | 0.063108 | 0.063109 | 0.063109 | 0.98872 | -0.21609 | 0.9856 | -0.27676 | 17.3376
57 | -0.041979 | -0.010606 | 0.041991 | 0.010613 | 1.1951e-05 | 7.5456e-06 | 0.063108 | 0.063108 | 0.063108 | 0.99028 | -0.18598 | 0.99059 | -0.18005 | 17.3374
58 | 0.033999 | 0.0085364 | -0.033983 | -0.0085261 | 1.6448e-05 | 1.0315e-05 | 0.051336 | 0.051336 | 0.051336 | 0.9856 | -0.27676 | 0.98508 | -0.28691 | 14.1034
59 | -0.0469 | -0.011843 | 0.046942 | 0.01187 | 4.2238e-05 | 2.674e-05 | 0.070482 | 0.070482 | 0.070482 | 0.99059 | -0.18005 | 0.99156 | -0.16127 | 19.3632
60 | 0.0049088 | 0.0012302 | -0.0049084 | -0.0012302 | 4.5312e-07 | 3.9399e-09 | 0.0073738 | 0.0073739 | 0.0073739 | 0.99059 | -0.18005 | 0.99049 | -0.18198 | 2.0258
61 | 0.030259 | 0.0075927 | -0.030253 | -0.0075893 | 5.4561e-06 | 3.4033e-06 | 0.04571 | 0.04571 | 0.04571 | 0.98508 | -0.28691 | 0.98489 | -0.29069 | 12.5578
62 | 0.026128 | 0.0065554 | -0.026119 | -0.0065499 | 8.9822e-06 | 5.5531e-06 | 0.039478 | 0.039478 | 0.039478 | 0.98489 | -0.29069 | 0.98452 | -0.2979 | 10.8456
63 | 0.020025 | 0.0050226 | -0.020021 | -0.0050199 | 4.5758e-06 | 2.7592e-06 | 0.030268 | 0.030268 | 0.030268 | 0.98452 | -0.2979 | 0.98427 | -0.3027 | 8.3154
64 | 0.015555 | 0.0039007 | -0.015551 | -0.0038984 | 3.9773e-06 | 2.3018e-06 | 0.023517 | 0.023517 | 0.023517 | 0.98427 | -0.3027 | 0.984 | -0.30807 | 6.4606
65 | -0.053288 | -0.01346 | 0.053299 | 0.013468 | 1.1476e-05 | 7.2828e-06 | 0.080005 | 0.080005 | 0.080005 | 0.99156 | -0.16127 | 0.9918 | -0.15678 | 21.9794
66 | -0.0078737 | -0.0019733 | 0.007876 | 0.0019742 | 2.2827e-06 | 8.7969e-07 | 0.01172 | 0.01172 | 0.01172 | 0.99968 | -0.0060843 | 1 | 0 | 3.2198
67 | 0.58947 | 0.15087 | -0.58869 | -0.15037 | 0.00077785 | 0.00049694 | 0.87825 | 0.87826 | 0.87826 | 1 | 0 | 0.99856 | -0.027291 | 48.2558
68 | -0.070066 | -0.017609 | 0.070092 | 0.017625 | 2.6378e-05 | 1.6804e-05 | 0.10634 | 0.10634 | 0.10634 | 0.98061 | -0.37274 | 0.98101 | -0.36486 | 29.2138
69 | 0.057272 | 0.014402 | -0.057228 | -0.014374 | 4.3927e-05 | 2.7918e-05 | 0.086924 | 0.086924 | 0.086924 | 0.98061 | -0.37274 | 0.97979 | -0.38881 | 23.8801
70 | 0.043751 | 0.011015 | -0.043693 | -0.010978 | 5.7854e-05 | 3.6567e-05 | 0.065731 | 0.065731 | 0.065731 | 0.99069 | -0.17814 | 0.98926 | -0.20585 | 18.058
71 | -0.050646 | -0.012743 | 0.050649 | 0.012745 | 2.4879e-06 | 1.5775e-06 | 0.076088 | 0.076088 | 0.076088 | 0.99069 | -0.17814 | 0.99075 | -0.17712 | 20.9033
72 | 0.035728 | 0.0089821 | -0.035697 | -0.0089629 | 3.0627e-05 | 1.9239e-05 | 0.053751 | 0.053751 | 0.053751 | 0.98926 | -0.20585 | 0.98834 | -0.22381 | 14.7668
73 | -0.063306 | -0.015917 | 0.063358 | 0.01595 | 5.2614e-05 | 3.3473e-05 | 0.095098 | 0.095098 | 0.095098 | 0.99075 | -0.17712 | 0.99164 | -0.15973 | 26.1258
74 | 0.035697 | 0.0089629 | -0.035686 | -0.0089554 | 1.1948e-05 | 7.5056e-06 | 0.053751 | 0.053751 | 0.053751 | 0.98834 | -0.22381 | 0.98798 | -0.23083 | 14.7668
75 | 0.081677 | 0.020664 | -0.081505 | -0.020554 | 0.00017209 | 0.00010974 | 0.12263 | 0.12263 | 0.12263 | 0.99164 | -0.15973 | 0.98936 | -0.20374 | 33.6895
76 | -0.14504 | -0.036614 | 0.1452 | 0.036719 | 0.00016449 | 0.00010479 | 0.21773 | 0.21773 | 0.21773 | 0.99164 | -0.15973 | 0.99287 | -0.13608 | 29.9076
77 | 0.022938 | 0.0057586 | -0.02292 | -0.0057477 | 1.7951e-05 | 1.0975e-05 | 0.034551 | 0.034551 | 0.034551 | 0.98798 | -0.23083 | 0.98713 | -0.24725 | 9.4921
78 | 0.012747 | 0.0031967 | -0.012746 | -0.0031958 | 1.8089e-06 | 9.9013e-07 | 0.0192 | 0.0192 | 0.0192 | 0.98798 | -0.23083 | 0.98782 | -0.23381 | 5.2747
79 | 0.077804 | 0.019626 | -0.077788 | -0.019616 | 1.5317e-05 | 9.7646e-06 | 0.11706 | 0.11706 | 0.11706 | 0.98936 | -0.20374 | 0.98915 | -0.20785 | 32.1601
80 | -0.14869 | -0.037594 | 0.14876 | 0.037639 | 7.227e-05 | 4.4999e-05 | 0.22296 | 0.22296 | 0.22296 | 0.99287 | -0.13608 | 0.9934 | -0.12595 | 12.2505
81 | 0.014594 | 0.0036611 | -0.014591 | -0.0036591 | 3.5229e-06 | 2.0066e-06 | 0.022001 | 0.022001 | 0.022001 | 0.98713 | -0.24725 | 0.98687 | -0.25232 | 6.0443
82 | 0.012746 | 0.0031958 | -0.012741 | -0.0031934 | 4.2997e-06 | 2.3538e-06 | 0.0192 | 0.0192 | 0.0192 | 0.98782 | -0.23381 | 0.98746 | -0.24089 | 5.2748
83 | -0.0043346 | -0.0010863 | 0.0043348 | 0.0010863 | 2.6558e-07 | -3.9009e-08 | 0.0065581 | 0.006558 | 0.0065581 | 0.9835 | -0.31766 | 0.98357 | -0.31637 | 1.8017
84 | -0.0096884 | -0.002428 | 0.0096894 | 0.0024285 | 9.8833e-07 | 4.7681e-07 | 0.014657 | 0.014657 | 0.014657 | 0.98357 | -0.31637 | 0.98368 | -0.31423 | 4.0267
85 | 0.071449 | 0.018028 | -0.071354 | -0.017967 | 9.5138e-05 | 6.0607e-05 | 0.10753 | 0.10753 | 0.10753 | 0.98915 | -0.20785 | 0.98771 | -0.2357 | 29.5404
86 | -0.15452 | -0.039082 | 0.15454 | 0.039093 | 1.7487e-05 | 1.091e-05 | 0.23159 | 0.23159 | 0.23159 | 0.9934 | -0.12595 | 0.99352 | -0.1236 | 12.7245
87 | -0.15714 | -0.039743 | 0.15722 | 0.039795 | 8.2136e-05 | 5.1287e-05 | 0.23547 | 0.23547 | 0.23547 | 0.99352 | -0.1236 | 0.99409 | -0.11271 | 12.938
88 | -0.1634 | -0.041344 | 0.16344 | 0.041372 | 4.3969e-05 | 2.7505e-05 | 0.24473 | 0.24473 | 0.24473 | 0.99409 | -0.11271 | 0.99438 | -0.1071 | 13.4465
89 | -0.16594 | -0.041996 | 0.166 | 0.042036 | 6.3401e-05 | 3.9688e-05 | 0.24846 | 0.24845 | 0.24846 | 0.99438 | -0.1071 | 0.9948 | -0.099144 | 13.6514
90 | -0.22985 | -0.058214 | 0.22995 | 0.058274 | 9.4191e-05 | 5.9593e-05 | 0.34403 | 0.34403 | 0.34403 | 0.9948 | -0.099144 | 0.99524 | -0.090615 | 18.9026
91 | 0.063853 | 0.016178 | -0.063804 | -0.016147 | 4.8822e-05 | 3.1061e-05 | 0.095573 | 0.095573 | 0.095573 | 0.9948 | -0.099144 | 0.99397 | -0.11507 | 26.2563
92 | 0.0061099 | 0.0015313 | -0.0061093 | -0.0015311 | 6.0453e-07 | 1.434e-07 | 0.0092047 | 0.0092048 | 0.0092048 | 0.98771 | -0.2357 | 0.98761 | -0.23778 | 2.5288
93 | 0.065244 | 0.016436 | -0.065175 | -0.016392 | 6.9639e-05 | 4.4324e-05 | 0.098322 | 0.098322 | 0.098322 | 0.98771 | -0.2357 | 0.98656 | -0.25804 | 27.0116
94 | -0.026613 | -0.0066699 | 0.026626 | 0.0066782 | 1.3328e-05 | 8.2516e-06 | 0.040257 | 0.040257 | 0.040257 | 0.98368 | -0.31423 | 0.98422 | -0.30372 | 11.0597
95 | -0.049479 | -0.012412 | 0.049519 | 0.012438 | 4.0646e-05 | 2.5767e-05 | 0.07481 | 0.07481 | 0.07481 | 0.98422 | -0.30372 | 0.9851 | -0.28651 | 20.5521
96 | 0.022853 | 0.0057337 | -0.022846 | -0.00573 | 6.1219e-06 | 3.7443e-06 | 0.034552 | 0.034553 | 0.034553 | 0.98422 | -0.30372 | 0.98393 | -0.30934 | 9.4925
97 | -0.057947 | -0.01455 | 0.058026 | 0.0146 | 7.8807e-05 | 5.0087e-05 | 0.08754 | 0.08754 | 0.08754 | 0.9851 | -0.28651 | 0.98656 | -0.25804 | 24.0495
98 | 0.020974 | 0.0052606 | -0.020967 | -0.0052564 | 6.9136e-06 | 4.1921e-06 | 0.03172 | 0.031721 | 0.031721 | 0.98393 | -0.30934 | 0.98357 | -0.31626 | 8.7144
99 | 0.017965 | 0.0045042 | -0.017963 | -0.0045026 | 2.7926e-06 | 1.6593e-06 | 0.02718 | 0.02718 | 0.02718 | 0.98357 | -0.31626 | 0.98341 | -0.31952 | 7.467
100 | 0.015674 | 0.0039289 | -0.015673 | -0.0039286 | 5.853e-07 | 3.3939e-07 | 0.023717 | 0.023717 | 0.023717 | 0.98341 | -0.31952 | 0.98337 | -0.32031 | 6.5155
101 | -0.23766 | -0.060208 | 0.23784 | 0.060321 | 0.00018003 | 0.00011398 | 0.35556 | 0.35556 | 0.35556 | 0.99524 | -0.090615 | 0.99607 | -0.074858 | 19.5365
102 | 0.062197 | 0.015744 | -0.062135 | -0.015705 | 6.2097e-05 | 3.9495e-05 | 0.093167 | 0.093167 | 0.093167 | 0.99397 | -0.11507 | 0.99288 | -0.13589 | 25.5954
103 | -0.24173 | -0.061295 | 0.24197 | 0.061447 | 0.00023991 | 0.00015195 | 0.36136 | 0.36136 | 0.36136 | 0.99607 | -0.074858 | 0.99714 | -0.054233 | 19.8552
104 | 0.059002 | 0.01492 | -0.058943 | -0.014882 | 5.9039e-05 | 3.7525e-05 | 0.088472 | 0.088473 | 0.088473 | 0.99288 | -0.13589 | 0.9918 | -0.15678 | 24.3056
105 | -0.24414 | -0.061992 | 0.24433 | 0.06211 | 0.00018686 | 0.00011837 | 0.36461 | 0.36461 | 0.36461 | 0.99714 | -0.054233 | 0.99798 | -0.038341 | 20.0337
106 | -0.24719 | -0.062827 | 0.24732 | 0.062911 | 0.00013161 | 8.339e-05 | 0.36888 | 0.36888 | 0.36888 | 0.99798 | -0.038341 | 0.99856 | -0.027291 | 20.2679
107 | 0.34137 | 0.08746 | -0.34114 | -0.08731 | 0.00023612 | 0.00015032 | 0.50938 | 0.50938 | 0.50938 | 0.99856 | -0.027291 | 0.9978 | -0.041575 | 27.9879
108 | -0.004923 | -0.0012338 | 0.0049237 | 0.0012338 | 6.6817e-07 | 1.5544e-08 | 0.0074282 | 0.007428 | 0.0074282 | 0.98618 | -0.26583 | 0.98632 | -0.26298 | 2.0407
109 | -0.014584 | -0.0036548 | 0.014591 | 0.0036591 | 7.4126e-06 | 4.2226e-06 | 0.022001 | 0.022001 | 0.022001 | 0.98632 | -0.26298 | 0.98687 | -0.25232 | 6.0443
110 | 0.0071307 | 0.0017873 | -0.0071293 | -0.0017868 | 1.4175e-06 | 4.8852e-07 | 0.010745 | 0.010746 | 0.010746 | 0.98746 | -0.24089 | 0.98724 | -0.24506 | 2.9521
111 | 0.013265 | 0.0033254 | -0.013265 | -0.0033254 | 1.2031e-08 | 6.6868e-09 | 0.02006 | 0.02006 | 0.02006 | 0.984 | -0.30807 | 0.98399 | -0.30808 | 5.5109
112 | 0.010977 | 0.002752 | -0.010974 | -0.0027505 | 2.8947e-06 | 1.4969e-06 | 0.0166 | 0.0166 | 0.0166 | 0.98399 | -0.30808 | 0.98371 | -0.31362 | 4.5605
113 | 0.0071713 | 0.0017975 | -0.0071698 | -0.0017969 | 1.5152e-06 | 5.3391e-07 | 0.010848 | 0.010848 | 0.010848 | 0.98371 | -0.31362 | 0.98348 | -0.31805 | 2.9802
114 | 0.013384 | 0.003355 | -0.013383 | -0.0033539 | 1.8588e-06 | 1.0364e-06 | 0.020253 | 0.020253 | 0.020253 | 0.98337 | -0.32031 | 0.98322 | -0.32322 | 5.5641
115 | 0.0045865 | 0.0011494 | -0.0045863 | -0.0011494 | 2.2356e-07 | -1.3838e-08 | 0.0069413 | 0.0069413 | 0.0069413 | 0.98322 | -0.32322 | 0.98317 | -0.32425 | 1.907

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60134 | 0.15343

## res_load
| p_mw | q_mvar
0 | 0.0026029 | 0.00065234
1 | 0.0017275 | 0.00043295
2 | 0.0045421 | 0.0011383
3 | 0.0045609 | 0.0011431
4 | 0.005998 | 0.0015032
5 | 0.020874 | 0.0052314
6 | 0.012688 | 0.00318
7 | 0.0059629 | 0.0014944
8 | 0.015253 | 0.0038228
9 | 0.0019236 | 0.00048211
10 | 0.0045052 | 0.0011291
11 | 0.0026496 | 0.00066405
12 | 0.0055511 | 0.0013912
13 | 0.0056708 | 0.0014212
14 | 0.0022153 | 0.0005552
15 | 0.0040353 | 0.0010113
16 | 0.011855 | 0.0029712
17 | 0.0050111 | 0.0012559
18 | 0.0054824 | 0.001374
19 | 0.0018174 | 0.00045549
20 | 0.0043206 | 0.0010829
21 | 0.0073615 | 0.001845
22 | 0.0061595 | 0.0015437
23 | 0.0096825 | 0.0024267
24 | 0.0098752 | 0.002475
25 | 0.011324 | 0.0028382
26 | 0.011529 | 0.0028895
27 | 0.012259 | 0.0030724
28 | 0.012321 | 0.0030878
29 | 0.011751 | 0.002945
30 | 0.011781 | 0.0029526
31 | 0.011291 | 0.0028298
32 | 0.0069495 | 0.0017417
33 | 0.012164 | 0.0030485
34 | 0.012438 | 0.0031172
35 | 0.0025589 | 0.00064133
36 | 0.0025589 | 0.00064133
37 | 0.0088966 | 0.0022297
38 | 0.0077976 | 0.0019543
39 | 0.0037244 | 0.00093343
40 | 0.0041252 | 0.0010339
41 | 0.0060937 | 0.0015272
42 | 0.0044657 | 0.0011192
43 | 0.006346 | 0.0015905
44 | 0.0049084 | 0.0012302
45 | 0.0078737 | 0.0019733
46 | 0.0023456 | 0.00058786
47 | 0.012794 | 0.0032066
48 | 0.0057557 | 0.0014425
49 | 0.0083285 | 0.0020873
50 | 0.0068955 | 0.0017282
51 | 0.0079648 | 0.0019962
52 | 0.012657 | 0.0031721
53 | 0.0037016 | 0.0009277
54 | 0.003491 | 0.00087492
55 | 0.0083257 | 0.0020866
56 | 0.0043346 | 0.0010863
57 | 0.0053535 | 0.0013417
58 | 0.0063389 | 0.0015887
59 | 0.0057597 | 0.0014435
60 | 0.0025948 | 0.00065031
61 | 0.0061826 | 0.0015495
62 | 0.002492 | 0.00062454
63 | 0.016923 | 0.0042414
64 | 0.0084279 | 0.0021122
65 | 0.0018727 | 0.00046933
66 | 0.0071487 | 0.0017916
67 | 0.0030014 | 0.00075222
68 | 0.0022889 | 0.00057366
69 | 0.0077164 | 0.0019339
70 | 0.0016071 | 0.00040277
71 | 0.0038826 | 0.00097308
72 | 0.0031327 | 0.00078512
73 | 0.002177 | 0.0005456
74 | 0.0056437 | 0.0014144
75 | 0.00286 | 0.00071678
76 | 0.004923 | 0.0012338
77 | 0.0096599 | 0.002421
78 | 0.0056106 | 0.0014062
79 | 0.012171 | 0.0030504
80 | 0.0022192 | 0.00055619
81 | 0.0071293 | 0.0017868
82 | 0.0061093 | 0.0015311
83 | 0.002286 | 0.00057292
84 | 0.0022878 | 0.00057339
85 | 0.0038028 | 0.00095308
86 | 0.0071698 | 0.0017969
87 | 0.0022887 | 0.0005736
88 | 0.0087961 | 0.0022045
89 | 0.0045863 | 0.0011494
90 | 0.0050088 | 0.0012553

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1