## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-16_0_8_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-16_0_8_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-16_0_8_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1711-16_0_8_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1711-16_0_8_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1711-16_0_8_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1711-16_0_8_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1711-16_0_8_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1711-16_0_8_node_13 | 0.4 | n |  | TRUE
9 | bus_LV_1711-16_0_8_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_1711-16_0_8_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1711-16_0_8_node_101 | 0.4 | n |  | TRUE
12 | bus_LV_1711-16_0_8_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_1711-16_0_8_node_7 | 0.4 | n |  | TRUE
14 | bus_LV_1711-16_0_8_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_1711-16_0_8_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_1711-16_0_8_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1711-16_0_8_node_15 | 0.4 | n |  | TRUE
18 | bus_LV_1711-16_0_8_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_1711-16_0_8_node_100 | 0.4 | n |  | TRUE
20 | bus_LV_1711-16_0_8_node_67 | 0.4 | n |  | TRUE
21 | bus_LV_1711-16_0_8_node_102 | 0.4 | n |  | TRUE
22 | bus_LV_1711-16_0_8_node_21 | 0.4 | n |  | TRUE
23 | bus_LV_1711-16_0_8_node_22 | 0.4 | n |  | TRUE
24 | bus_LV_1711-16_0_8_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_1711-16_0_8_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1711-16_0_8_node_105 | 0.4 | n |  | TRUE
27 | bus_LV_1711-16_0_8_node_106 | 0.4 | n |  | TRUE
28 | bus_LV_1711-16_0_8_node_104 | 0.4 | n |  | TRUE
29 | bus_LV_1711-16_0_8_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1711-16_0_8_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_1711-16_0_8_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1711-16_0_8_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_1711-16_0_8_node_29 | 0.4 | n |  | TRUE
34 | bus_LV_1711-16_0_8_node_43 | 0.4 | n |  | TRUE
35 | bus_LV_1711-16_0_8_node_74 | 0.4 | n |  | TRUE
36 | bus_LV_1711-16_0_8_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_1711-16_0_8_node_60 | 0.4 | n |  | TRUE
38 | bus_LV_1711-16_0_8_node_44 | 0.4 | n |  | TRUE
39 | bus_LV_1711-16_0_8_node_66 | 0.4 | n |  | TRUE
40 | bus_LV_1711-16_0_8_node_62 | 0.4 | n |  | TRUE
41 | bus_LV_1711-16_0_8_node_50 | 0.4 | n |  | TRUE
42 | bus_LV_1711-16_0_8_node_58 | 0.4 | n |  | TRUE
43 | bus_LV_1711-16_0_8_node_30 | 0.4 | n |  | TRUE
44 | bus_LV_1711-16_0_8_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_1711-16_0_8_node_32 | 0.4 | n |  | TRUE
46 | bus_LV_1711-16_0_8_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_1711-16_0_8_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_1711-16_0_8_node_53 | 0.4 | n |  | TRUE
49 | bus_LV_1711-16_0_8_node_103 | 0.4 | n |  | TRUE
50 | bus_LV_1711-16_0_8_node_54 | 0.4 | n |  | TRUE
51 | bus_LV_1711-16_0_8_node_35 | 0.4 | n |  | TRUE
52 | bus_LV_1711-16_0_8_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_1711-16_0_8_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_1711-16_0_8_node_38 | 0.4 | n |  | TRUE
55 | bus_LV_1711-16_0_8_node_39 | 0.4 | n |  | TRUE
56 | bus_LV_1711-16_0_8_node_41 | 0.4 | n |  | TRUE
57 | bus_LV_1711-16_0_8_node_42 | 0.4 | n |  | TRUE
58 | bus_LV_1711-16_0_8_node_55 | 0.4 | n |  | TRUE
59 | bus_LV_1711-16_0_8_node_75 | 0.4 | n |  | TRUE
60 | bus_LV_1711-16_0_8_node_76 | 0.4 | n |  | TRUE
61 | bus_LV_1711-16_0_8_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_1711-16_0_8_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_1711-16_0_8_node_47 | 0.4 | n |  | TRUE
64 | bus_LV_1711-16_0_8_node_48 | 0.4 | n |  | TRUE
65 | bus_LV_1711-16_0_8_node_49 | 0.4 | n |  | TRUE
66 | bus_LV_1711-16_0_8_node_51 | 0.4 | n |  | TRUE
67 | bus_LV_1711-16_0_8_node_87 | 0.4 | n |  | TRUE
68 | bus_LV_1711-16_0_8_node_88 | 0.4 | n |  | TRUE
69 | bus_LV_1711-16_0_8_node_89 | 0.4 | n |  | TRUE
70 | bus_LV_1711-16_0_8_node_80 | 0.4 | n |  | TRUE
71 | bus_LV_1711-16_0_8_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_1711-16_0_8_node_69 | 0.4 | n |  | TRUE
73 | bus_LV_1711-16_0_8_node_57 | 0.4 | n |  | TRUE
74 | bus_LV_1711-16_0_8_node_93 | 0.4 | n |  | TRUE
75 | bus_LV_1711-16_0_8_node_92 | 0.4 | n |  | TRUE
76 | bus_LV_1711-16_0_8_node_59 | 0.4 | n |  | TRUE
77 | bus_LV_1711-16_0_8_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_1711-16_0_8_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_1711-16_0_8_node_91 | 0.4 | n |  | TRUE
80 | bus_LV_1711-16_0_8_node_71 | 0.4 | n |  | TRUE
81 | bus_LV_1711-16_0_8_node_63 | 0.4 | n |  | TRUE
82 | bus_LV_1711-16_0_8_node_64 | 0.4 | n |  | TRUE
83 | bus_LV_1711-16_0_8_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_1711-16_0_8_node_72 | 0.4 | n |  | TRUE
85 | bus_LV_1711-16_0_8_node_73 | 0.4 | n |  | TRUE
86 | bus_LV_1711-16_0_8_node_96 | 0.4 | n |  | TRUE
87 | bus_LV_1711-16_0_8_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_1711-16_0_8_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_1711-16_0_8_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_1711-16_0_8_node_79 | 0.4 | n |  | TRUE
91 | bus_LV_1711-16_0_8_node_98 | 0.4 | n |  | TRUE
92 | bus_LV_1711-16_0_8_node_99 | 0.4 | n |  | TRUE
93 | bus_LV_1711-16_0_8_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_1711-16_0_8_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_1711-16_0_8_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_1711-16_0_8_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_1711-16_0_8_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_1711-16_0_8_node_107 | 0.4 | n |  | TRUE
99 | bus_LV_1711-16_0_8_node_97 | 0.4 | n |  | TRUE
100 | bus_LV_1711-16_0_8_node_109 | 0.4 | n |  | TRUE
101 | bus_LV_1711-16_0_8_node_108 | 0.4 | n |  | TRUE
102 | bus_LV_1711-16_0_8_node_112 | 0.4 | n |  | TRUE
103 | bus_LV_1711-16_0_8_node_110 | 0.4 | n |  | TRUE
104 | bus_LV_1711-16_0_8_node_94 | 0.4 | n |  | TRUE
105 | bus_LV_1711-16_0_8_node_95 | 0.4 | n |  | TRUE
106 | bus_LV_1711-16_0_8_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_1711-16_0_8_node_126 | 0.4 | n |  | TRUE
108 | bus_LV_1711-16_0_8_node_111 | 0.4 | n |  | TRUE
109 | bus_LV_1711-16_0_8_node_117 | 0.4 | n |  | TRUE
110 | bus_LV_1711-16_0_8_node_118 | 0.4 | n |  | TRUE
111 | bus_LV_1711-16_0_8_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_1711-16_0_8_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_1711-16_0_8_node_115 | 0.4 | n |  | TRUE
114 | bus_LV_1711-16_0_8_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_1711-16_0_8_node_124 | 0.4 | n |  | TRUE
116 | bus_LV_1711-16_0_8_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_1711-16_0_8_node_119 | 0.4 | n |  | TRUE
118 | bus_LV_1711-16_0_8_node_121 | 0.4 | n |  | TRUE
119 | bus_LV_1711-16_0_8_node_122 | 0.4 | n |  | TRUE
120 | bus_LV_1711-16_0_8_node_127 | 0.4 | n |  | TRUE
121 | bus_LV_1711-16_0_8_node_123 | 0.4 | n |  | TRUE
122 | bus_MV_228_0_node_25 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-16_0_8_load_0 | 0 | 0.0022278 | 0.00055835 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-16_0_8_load_1 | 1 | 0.0058138 | 0.0014571 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-16_0_8_load_2 | 2 | 0.0028142 | 0.00070531 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-16_0_8_load_3 | 3 | 0.00048173 | 0.00012073 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-16_0_8_load_5 | 5 | 0.0062509 | 0.0015666 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-16_0_8_load_14 | 6 | 0.0033516 | 0.00083999 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-16_0_8_load_13 | 8 | 0.0037796 | 0.00094726 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-16_0_8_load_17 | 9 | 0.0043203 | 0.0010828 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-16_0_8_load_10 | 10 | 0.0057331 | 0.0014368 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-16_0_8_load_101 | 11 | 0.0044422 | 0.0011133 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-16_0_8_load_9 | 12 | 0.012631 | 0.0031656 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-16_0_8_load_7 | 13 | 0.00086191 | 0.00021601 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-16_0_8_load_12 | 15 | 0.013921 | 0.0034889 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-16_0_8_load_18 | 16 | 0.014199 | 0.0035587 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-16_0_8_load_15 | 17 | 0.0043344 | 0.0010863 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-16_0_8_load_16 | 18 | 0.0029673 | 0.00074368 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-16_0_8_load_100 | 19 | 0.0048324 | 0.0012111 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-16_0_8_load_67 | 20 | 0.0038623 | 0.00096797 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-16_0_8_load_102 | 21 | 0.0041874 | 0.0010495 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-16_0_8_load_21 | 22 | 0.0031755 | 0.00079587 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-16_0_8_load_105 | 26 | 0.0032695 | 0.00081942 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-16_0_8_load_106 | 27 | 0.0020012 | 0.00050156 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-16_0_8_load_104 | 28 | 0.0034994 | 0.00087703 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-16_0_8_load_25 | 29 | 0.0038991 | 0.00097721 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-16_0_8_load_26 | 30 | 0.0052 | 0.0013032 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-16_0_8_load_27 | 31 | 0.0043228 | 0.0010834 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-16_0_8_load_28 | 32 | 0.0030879 | 0.0007739 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1711-16_0_8_load_43 | 34 | 0.0030557 | 0.00076584 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1711-16_0_8_load_74 | 35 | 0.0028307 | 0.00070945 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1711-16_0_8_load_40 | 36 | 0.0036069 | 0.00090397 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1711-16_0_8_load_44 | 38 | 0.002972 | 0.00074486 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1711-16_0_8_load_66 | 39 | 0.0022719 | 0.00056938 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1711-16_0_8_load_62 | 40 | 0.0041163 | 0.0010316 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1711-16_0_8_load_50 | 41 | 0.0050797 | 0.0012731 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1711-16_0_8_load_58 | 42 | 0.00413 | 0.0010351 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1711-16_0_8_load_30 | 43 | 0.006331 | 0.0015867 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1711-16_0_8_load_31 | 44 | 0.0044521 | 0.0011158 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1711-16_0_8_load_32 | 45 | 0.0033594 | 0.00084195 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1711-16_0_8_load_33 | 46 | 0.0053124 | 0.0013314 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1711-16_0_8_load_34 | 47 | 0.0086277 | 0.0021623 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1711-16_0_8_load_53 | 48 | 0.0056151 | 0.0014073 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1711-16_0_8_load_103 | 49 | 0.0049767 | 0.0012473 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1711-16_0_8_load_54 | 50 | 0.0074882 | 0.0018767 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1711-16_0_8_load_35 | 51 | 0.0096021 | 0.0024065 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1711-16_0_8_load_38 | 54 | 0.012272 | 0.0030756 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1711-16_0_8_load_39 | 55 | 0.0053196 | 0.0013332 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1711-16_0_8_load_41 | 56 | 0.012195 | 0.0030563 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1711-16_0_8_load_42 | 57 | 0.006679 | 0.0016739 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1711-16_0_8_load_55 | 58 | 0.013557 | 0.0033976 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1711-16_0_8_load_75 | 59 | 0.010456 | 0.0026205 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1711-16_0_8_load_76 | 60 | 0.0070767 | 0.0017736 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1711-16_0_8_load_52 | 62 | 0.0029742 | 0.00074542 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1711-16_0_8_load_47 | 63 | 0.0036315 | 0.00091013 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1711-16_0_8_load_48 | 64 | 0.0057962 | 0.0014527 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1711-16_0_8_load_49 | 65 | 0.0050383 | 0.0012627 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1711-16_0_8_load_87 | 67 | 0.0033749 | 0.00084582 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1711-16_0_8_load_88 | 68 | 0.0080631 | 0.0020208 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1711-16_0_8_load_89 | 69 | 0.0051588 | 0.0012929 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1711-16_0_8_load_80 | 70 | 0.0042139 | 0.0010561 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1711-16_0_8_load_68 | 71 | 0.0079102 | 0.0019825 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1711-16_0_8_load_57 | 73 | 0.0056754 | 0.0014224 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1711-16_0_8_load_93 | 74 | 0.004351 | 0.0010905 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1711-16_0_8_load_92 | 75 | 0.0095346 | 0.0023896 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1711-16_0_8_load_59 | 76 | 0.0035494 | 0.00088956 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1711-16_0_8_load_61 | 77 | 0.0053136 | 0.0013317 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1711-16_0_8_load_91 | 79 | 0.0039749 | 0.0009962 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1711-16_0_8_load_71 | 80 | 0.0048088 | 0.0012052 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1711-16_0_8_load_63 | 81 | 0.0069022 | 0.0017299 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1711-16_0_8_load_64 | 82 | 0.0048 | 0.001203 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1711-16_0_8_load_65 | 83 | 0.0042825 | 0.0010733 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1711-16_0_8_load_72 | 84 | 0.011034 | 0.0027654 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1711-16_0_8_load_73 | 85 | 0.0023361 | 0.00058549 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1711-16_0_8_load_96 | 86 | 0.010005 | 0.0025076 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1711-16_0_8_load_77 | 87 | 0.0075628 | 0.0018954 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1711-16_0_8_load_79 | 90 | 0.0043134 | 0.001081 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1711-16_0_8_load_99 | 92 | 0.0010153 | 0.00025445 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1711-16_0_8_load_81 | 93 | 0.0077543 | 0.0019434 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1711-16_0_8_load_82 | 94 | 0.0064826 | 0.0016247 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_1711-16_0_8_load_84 | 96 | 0.0049931 | 0.0012514 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_1711-16_0_8_load_86 | 97 | 0.0035804 | 0.00089732 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_1711-16_0_8_load_107 | 98 | 0.0068468 | 0.001716 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_1711-16_0_8_load_97 | 99 | 0.0033763 | 0.00084619 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_1711-16_0_8_load_109 | 100 | 0.0030067 | 0.00075355 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_1711-16_0_8_load_108 | 101 | 0.0031521 | 0.00078998 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_1711-16_0_8_load_112 | 102 | 0.0052779 | 0.0013228 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_1711-16_0_8_load_110 | 103 | 0.0054982 | 0.001378 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_1711-16_0_8_load_94 | 104 | 0.0097087 | 0.0024332 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_1711-16_0_8_load_95 | 105 | 0.0090227 | 0.0022613 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_1711-16_0_8_load_120 | 106 | 0.0032583 | 0.00081661 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_1711-16_0_8_load_126 | 107 | 0.0034969 | 0.00087641 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_1711-16_0_8_load_111 | 108 | 0.0062097 | 0.0015563 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_1711-16_0_8_load_117 | 109 | 0.0043735 | 0.0010961 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_1711-16_0_8_load_118 | 110 | 0.003524 | 0.0008832 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_1711-16_0_8_load_113 | 111 | 0.0060061 | 0.0015053 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_1711-16_0_8_load_114 | 112 | 0.014221 | 0.003564 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_1711-16_0_8_load_115 | 113 | 0.0053352 | 0.0013371 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_1711-16_0_8_load_116 | 114 | 0.0092135 | 0.0023091 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_1711-16_0_8_load_124 | 115 | 0.012789 | 0.0032052 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_1711-16_0_8_load_125 | 116 | 0.016912 | 0.0042387 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_1711-16_0_8_load_119 | 117 | 0.0074496 | 0.001867 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_1711-16_0_8_load_121 | 118 | 0.004507 | 0.0011296 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_1711-16_0_8_load_122 | 119 | 0.0078696 | 0.0019723 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_1711-16_0_8_load_127 | 120 | 0.0032893 | 0.00082439 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-16_0_8_line_0 |  | 0 | 1 | 0.0071701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1711-16_0_8_line_1 |  | 0 | 2 | 0.018079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1711-16_0_8_line_2 |  | 1 | 3 | 0.010024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1711-16_0_8_line_3 |  | 2 | 4 | 0.017811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_1711-16_0_8_line_4 |  | 3 | 5 | 0.014545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1711-16_0_8_line_5 |  | 4 | 6 | 0.029916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1711-16_0_8_line_6 |  | 5 | 7 | 0.013281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1711-16_0_8_line_7 |  | 6 | 8 | 0.0016812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1711-16_0_8_line_8 |  | 7 | 9 | 0.011057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1711-16_0_8_line_9 |  | 7 | 10 | 0.015611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-16_0_8_line_10 |  | 8 | 17 | 0.021926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1711-16_0_8_line_11 |  | 9 | 11 | 0.031439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1711-16_0_8_line_12 |  | 10 | 12 | 0.0060734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-16_0_8_line_13 |  | 11 | 21 | 0.027863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1711-16_0_8_line_14 |  | 12 | 14 | 0.012576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-16_0_8_line_15 |  | 13 | 14 | 0.035147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-16_0_8_line_16 |  | 14 | 15 | 0.029049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-16_0_8_line_17 |  | 15 | 16 | 0.017581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-16_0_8_line_18 |  | 17 | 18 | 0.0018928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1711-16_0_8_line_19 |  | 18 | 19 | 0.01873 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1711-16_0_8_line_20 |  | 19 | 20 | 0.011017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1711-16_0_8_line_21 |  | 20 | 83 | 0.006498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1711-16_0_8_line_22 |  | 21 | 25 | 0.01139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1711-16_0_8_line_23 |  | 22 | 23 | 0.023354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1711-16_0_8_line_24 |  | 23 | 24 | 0.014543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-16_0_8_line_25 |  | 24 | 27 | 0.033365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_1711-16_0_8_line_26 |  | 24 | 26 | 0.012998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_1711-16_0_8_line_27 |  | 25 | 26 | 0.011853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
28 | LV_1711-16_0_8_line_28 |  | 27 | 28 | 0.013348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_1711-16_0_8_line_29 |  | 28 | 49 | 0.024683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1711-16_0_8_line_30 |  | 29 | 30 | 0.024477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1711-16_0_8_line_31 |  | 29 | 31 | 0.0031502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-16_0_8_line_32 |  | 30 | 32 | 0.0051817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1711-16_0_8_line_33 |  | 31 | 33 | 0.010305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1711-16_0_8_line_34 |  | 32 | 34 | 0.016984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1711-16_0_8_line_35 |  | 33 | 35 | 0.010916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_1711-16_0_8_line_36 |  | 33 | 36 | 0.015219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1711-16_0_8_line_37 |  | 33 | 37 | 0.030912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_1711-16_0_8_line_38 |  | 34 | 38 | 0.012718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1711-16_0_8_line_39 |  | 35 | 39 | 0.019566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_1711-16_0_8_line_40 |  | 37 | 40 | 0.012064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1711-16_0_8_line_41 |  | 37 | 41 | 0.026497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_1711-16_0_8_line_42 |  | 37 | 42 | 0.0098753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1711-16_0_8_line_43 |  | 38 | 61 | 0.0036981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1711-16_0_8_line_44 |  | 39 | 82 | 0.017463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_1711-16_0_8_line_45 |  | 40 | 79 | 0.019278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1711-16_0_8_line_46 |  | 41 | 64 | 0.0064542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_1711-16_0_8_line_47 |  | 42 | 76 | 0.01899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1711-16_0_8_line_48 |  | 43 | 44 | 0.025738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_1711-16_0_8_line_49 |  | 43 | 45 | 0.022931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_1711-16_0_8_line_50 |  | 44 | 46 | 0.018273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_1711-16_0_8_line_51 |  | 45 | 47 | 0.032817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_1711-16_0_8_line_52 |  | 46 | 48 | 0.0021532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_1711-16_0_8_line_53 |  | 47 | 49 | 0.010305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_1711-16_0_8_line_54 |  | 48 | 50 | 0.022519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_1711-16_0_8_line_55 |  | 50 | 71 | 0.023839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_1711-16_0_8_line_56 |  | 51 | 52 | 0.016219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1711-16_0_8_line_57 |  | 51 | 53 | 0.014939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1711-16_0_8_line_58 |  | 52 | 54 | 0.019668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1711-16_0_8_line_59 |  | 52 | 55 | 0.017311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1711-16_0_8_line_60 |  | 53 | 56 | 0.0172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1711-16_0_8_line_61 |  | 53 | 57 | 0.013348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1711-16_0_8_line_62 |  | 54 | 58 | 0.027206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1711-16_0_8_line_63 |  | 55 | 59 | 0.01579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1711-16_0_8_line_64 |  | 59 | 60 | 0.0068786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1711-16_0_8_line_65 |  | 60 | 85 | 0.024333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1711-16_0_8_line_66 |  | 61 | 62 | 0.0060101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1711-16_0_8_line_67 |  | 63 | 64 | 0.014758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_1711-16_0_8_line_68 |  | 63 | 65 | 0.0092198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_1711-16_0_8_line_69 |  | 65 | 66 | 0.019555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_1711-16_0_8_line_70 |  | 66 | 67 | 0.017396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1711-16_0_8_line_71 |  | 66 | 68 | 0.0044637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1711-16_0_8_line_72 |  | 67 | 69 | 0.00036999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1711-16_0_8_line_73 |  | 68 | 70 | 0.021806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1711-16_0_8_line_74 |  | 70 | 88 | 0.015963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1711-16_0_8_line_75 |  | 71 | 72 | 0.019599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_1711-16_0_8_line_76 |  | 72 | 84 | 0.013315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_1711-16_0_8_line_77 |  | 72 | 85 | 0.0078294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1711-16_0_8_line_78 |  | 73 | 74 | 0.00057985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1711-16_0_8_line_79 |  | 74 | 75 | 0.006195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1711-16_0_8_line_80 |  | 75 | 104 | 0.027618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1711-16_0_8_line_81 |  | 76 | 77 | 0.0005515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1711-16_0_8_line_82 |  | 77 | 78 | 0.025899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1711-16_0_8_line_83 |  | 78 | 80 | 0.027872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1711-16_0_8_line_84 |  | 81 | 82 | 0.0048615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_1711-16_0_8_line_85 |  | 81 | 83 | 0.021984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_1711-16_0_8_line_86 |  | 84 | 86 | 0.032499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_1711-16_0_8_line_87 |  | 86 | 89 | 0.046371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_1711-16_0_8_line_88 |  | 87 | 88 | 0.017892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1711-16_0_8_line_89 |  | 88 | 90 | 0.022316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1711-16_0_8_line_90 |  | 89 | 99 | 0.021067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1711-16_0_8_line_91 |  | 89 | 95 | 0.008927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
92 | LV_1711-16_0_8_line_92 |  | 90 | 91 | 0.032671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1711-16_0_8_line_93 |  | 91 | 92 | 0.019198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1711-16_0_8_line_94 |  | 93 | 94 | 0.030366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1711-16_0_8_line_95 |  | 93 | 95 | 0.019781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1711-16_0_8_line_96 |  | 94 | 96 | 0.027192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1711-16_0_8_line_97 |  | 95 | 97 | 0.0094688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_1711-16_0_8_line_98 |  | 96 | 98 | 0.022401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1711-16_0_8_line_99 |  | 97 | 100 | 0.026876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_1711-16_0_8_line_100 |  | 98 | 101 | 0.023518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1711-16_0_8_line_101 |  | 99 | 102 | 0.010218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1711-16_0_8_line_102 |  | 100 | 103 | 0.022394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1711-16_0_8_line_103 |  | 101 | 106 | 0.00063367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1711-16_0_8_line_104 |  | 102 | 105 | 0.018476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1711-16_0_8_line_105 |  | 103 | 108 | 0.0072387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1711-16_0_8_line_106 |  | 104 | 105 | 0.0076687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1711-16_0_8_line_107 |  | 106 | 107 | 0.0058724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1711-16_0_8_line_108 |  | 107 | 120 | 0.022442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1711-16_0_8_line_109 |  | 108 | 109 | 0.0098824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1711-16_0_8_line_110 |  | 109 | 110 | 0.014284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1711-16_0_8_line_111 |  | 110 | 117 | 0.012893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1711-16_0_8_line_112 |  | 111 | 112 | 0.0036886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_1711-16_0_8_line_113 |  | 111 | 113 | 0.0081451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_1711-16_0_8_line_114 |  | 112 | 114 | 0.026542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_1711-16_0_8_line_115 |  | 114 | 115 | 0.033504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_1711-16_0_8_line_116 |  | 115 | 116 | 0.032271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_1711-16_0_8_line_117 |  | 116 | 121 | 0.046207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_1711-16_0_8_line_118 |  | 117 | 118 | 0.016331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_1711-16_0_8_line_119 |  | 118 | 119 | 0.010698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_1711-16_0_8_line_120 |  | 119 | 121 | 0.058432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-16_0_8_trafo_54 | 0.63 MVA 20/0.4 kV | 122 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2682300.0508 | 1224877.3216 | 2682305.2441 | 1224882.2653
1 | 2682300.0508 | 1224877.3216 | 2682294.8427 | 1224872.364 | 2682286.917 | 1224864.8974
2 | 2682312.5043 | 1224889.1765 | 2682305.2441 | 1224882.2653
3 | 2682273.9526 | 1224852.6841 | 2682286.917 | 1224864.8974
4 | 2682312.5043 | 1224889.1765 | 2682313.6644 | 1224890.2808 | 2682323.1037 | 1224899.1371
5 | 2682273.9526 | 1224852.6841 | 2682279.1856 | 1224846.5745 | 2682284.521 | 1224837.9869 | 2682286.6631 | 1224826.4225
6 | 2682332.7888 | 1224908.2241 | 2682323.1037 | 1224899.1371
7 | 2682286.6631 | 1224826.4225 | 2682286.7498 | 1224825.954 | 2682286.7964 | 1224824.7502
8 | 2682332.7888 | 1224908.2241 | 2682340.8162 | 1224915.828
9 | 2682332.7888 | 1224908.2241 | 2682329.6916 | 1224913.4181 | 2682322.3655 | 1224919.5654 | 2682322.3655 | 1224919.5654
10 | 2682287.6443 | 1224802.8402 | 2682286.7964 | 1224824.7502
11 | 2682340.8162 | 1224915.828 | 2682353.5274 | 1224927.8687 | 2682363.6143 | 1224937.4762
12 | 2682318.1979 | 1224923.9833 | 2682322.3655 | 1224919.5654
13 | 2682363.6143 | 1224937.4762 | 2682383.79 | 1224956.693
14 | 2682309.5685 | 1224933.131 | 2682318.1979 | 1224923.9833
15 | 2682309.5685 | 1224933.131 | 2682277.901 | 1224917.8833
16 | 2682309.5685 | 1224933.131 | 2682328.1899 | 1224955.4267
17 | 2682328.1899 | 1224955.4267 | 2682339.46 | 1224968.9206
18 | 2682287.6443 | 1224802.8402 | 2682287.7175 | 1224800.9488
19 | 2682287.7175 | 1224800.9488 | 2682287.8 | 1224798.8168 | 2682287.4121 | 1224782.2252
20 | 2682285.4444 | 1224771.4042 | 2682287.3808 | 1224780.8877 | 2682287.4121 | 1224782.2252
21 | 2682285.4444 | 1224771.4042 | 2682284.7604 | 1224768.0539 | 2682283.7717 | 1224765.1384
22 | 2682392.0377 | 1224964.5487 | 2682383.79 | 1224956.693
23 | 2682406.9451 | 1224991.8625 | 2682399.8593 | 1224994.3438 | 2682394.3858 | 1224996.4695 | 2682386.3131 | 1225002.3284
24 | 2682406.9451 | 1224991.8625 | 2682404.0171 | 1224982.649 | 2682408.7279 | 1224981.3911
25 | 2682408.7279 | 1224981.3911 | 2682410.151 | 1224981.0106 | 2682416.2826 | 1224975.7141 | 2682418.1809 | 1224970.0365 | 2682418.4316 | 1224962.8907 | 2682416.4001 | 1224955.1907 | 2682415.8318 | 1224952.5619
26 | 2682408.7279 | 1224981.3911 | 2682407.9206 | 1224979.4564 | 2682402.5116 | 1224969.9916
27 | 2682392.0377 | 1224964.5487 | 2682402.3611 | 1224969.7284 | 2682402.5116 | 1224969.9916
28 | 2682413.0113 | 1224939.5151 | 2682415.8318 | 1224952.5619
29 | 2682413.0113 | 1224939.5151 | 2682412.0677 | 1224935.1505 | 2682409.0397 | 1224915.1605
30 | 2682260.755 | 1224680.4771 | 2682260.7364 | 1224679.9622 | 2682259.688 | 1224666.9501 | 2682258.2755 | 1224656.1343 | 2682258.2755 | 1224656.1343
31 | 2682260.755 | 1224680.4771 | 2682260.8688 | 1224683.6252
32 | 2682256.8272 | 1224651.1591 | 2682258.2755 | 1224656.1343
33 | 2682261.241 | 1224693.9231 | 2682260.8688 | 1224683.6252
34 | 2682251.491 | 1224635.066 | 2682253.44 | 1224639.5229 | 2682256.8272 | 1224651.1591
35 | 2682261.241 | 1224693.9231 | 2682263.3961 | 1224704.6247
36 | 2682261.241 | 1224693.9231 | 2682276.3683 | 1224692.2559
37 | 2682261.241 | 1224693.9231 | 2682258.8765 | 1224694.3796 | 2682235.0129 | 1224697.7634 | 2682230.8192 | 1224696.1599
38 | 2682251.491 | 1224635.066 | 2682246.3954 | 1224623.4136
39 | 2682263.3961 | 1224704.6247 | 2682263.9017 | 1224707.1355 | 2682269.5135 | 1224723.1874
40 | 2682230.8192 | 1224696.1599 | 2682236.4564 | 1224706.8258
41 | 2682230.8192 | 1224696.1599 | 2682219.1056 | 1224672.3923
42 | 2682230.8192 | 1224696.1599 | 2682222.1151 | 1224700.8247
43 | 2682244.9137 | 1224620.0253 | 2682246.3954 | 1224623.4136
44 | 2682269.5135 | 1224723.1874 | 2682270.6122 | 1224726.3301 | 2682275.1509 | 1224739.7151
45 | 2682245.4647 | 1224723.8699 | 2682236.4564 | 1224706.8258
46 | 2682216.2524 | 1224666.603 | 2682219.1056 | 1224672.3923
47 | 2682222.1151 | 1224700.8247 | 2682205.3774 | 1224709.7949
48 | 2682383.1027 | 1224854.7534 | 2682377.5103 | 1224844.0771 | 2682370.8444 | 1224832.1244
49 | 2682383.1027 | 1224854.7534 | 2682393.743 | 1224875.0666
50 | 2682361.9442 | 1224816.1655 | 2682370.8444 | 1224832.1244
51 | 2682393.743 | 1224875.0666 | 2682400.9124 | 1224888.7535 | 2682406.3568 | 1224905.244
52 | 2682361.9442 | 1224816.1655 | 2682360.8954 | 1224814.285
53 | 2682406.3568 | 1224905.244 | 2682408.5387 | 1224911.8525 | 2682409.0397 | 1224915.1605
54 | 2682351.464 | 1224793.8931 | 2682355.9948 | 1224805.4977 | 2682360.8954 | 1224814.285
55 | 2682351.464 | 1224793.8931 | 2682346.0651 | 1224780.0653 | 2682343.5076 | 1224771.4422
56 | 2682319.0156 | 1224684.3819 | 2682314.9899 | 1224668.6707
57 | 2682311.2819 | 1224654.199 | 2682314.9899 | 1224668.6707
58 | 2682319.0156 | 1224684.3819 | 2682338.0201 | 1224679.3148
59 | 2682319.0156 | 1224684.3819 | 2682323.8708 | 1224700.9981
60 | 2682311.2819 | 1224654.199 | 2682327.5007 | 1224648.4718
61 | 2682311.2819 | 1224654.199 | 2682307.9711 | 1224641.2679
62 | 2682364.3078 | 1224672.3058 | 2682338.0201 | 1224679.3148
63 | 2682323.8708 | 1224700.9981 | 2682324.6263 | 1224703.5836 | 2682328.2767 | 1224716.1613
64 | 2682328.2767 | 1224716.1613 | 2682330.1939 | 1224722.7673
65 | 2682330.1939 | 1224722.7673 | 2682336.9762 | 1224746.1362
66 | 2682244.9137 | 1224620.0253 | 2682242.3291 | 1224614.5993
67 | 2682209.7284 | 1224653.3655 | 2682216.2524 | 1224666.603
68 | 2682209.7284 | 1224653.3655 | 2682205.6527 | 1224645.0955
69 | 2682195.4148 | 1224628.7587 | 2682199.3542 | 1224632.3155 | 2682205.6527 | 1224645.0955
70 | 2682195.4148 | 1224628.7587 | 2682197.9357 | 1224624.1237 | 2682208.8431 | 1224618.8395
71 | 2682195.4148 | 1224628.7587 | 2682190.954 | 1224628.9194 | 2682190.954 | 1224628.9194
72 | 2682208.8431 | 1224618.8395 | 2682209.1761 | 1224618.6781
73 | 2682171.7031 | 1224639.1621 | 2682190.954 | 1224628.9194
74 | 2682157.6109 | 1224646.6601 | 2682171.7031 | 1224639.1621
75 | 2682340.8111 | 1224752.6296 | 2682339.4252 | 1224756.8911 | 2682340.3565 | 1224760.8177 | 2682343.5076 | 1224771.4422
76 | 2682340.8111 | 1224752.6296 | 2682344.2791 | 1224749.6867 | 2682351.7149 | 1224747.6882 | 2682352.7793 | 1224747.7598
77 | 2682340.8111 | 1224752.6296 | 2682338.1531 | 1224750.1912 | 2682336.9762 | 1224746.1362
78 | 2682388.3054 | 1224711.6437 | 2682388.2298 | 1224711.0688
79 | 2682389.1138 | 1224717.7857 | 2682388.3054 | 1224711.6437
80 | 2682389.1138 | 1224717.7857 | 2682389.3425 | 1224719.5231 | 2682392.4847 | 1224745.197
81 | 2682204.8913 | 1224710.0555 | 2682205.3774 | 1224709.7949
82 | 2682180.5187 | 1224715.7675 | 2682185.8828 | 1224716.631 | 2682194.4952 | 1224715.627 | 2682204.8913 | 1224710.0555
83 | 2682180.5187 | 1224715.7675 | 2682181.518 | 1224707.0976 | 2682181.7386 | 1224700.4629 | 2682179.4509 | 1224690.9693 | 2682178.2392 | 1224688.511
84 | 2682276.7121 | 1224744.3191 | 2682275.1509 | 1224739.7151
85 | 2682276.7121 | 1224744.3191 | 2682283.7717 | 1224765.1384
86 | 2682352.7793 | 1224747.7598 | 2682357.5404 | 1224748.0801 | 2682365.0291 | 1224751.0191 | 2682370.1916 | 1224759.8632 | 2682373.6143 | 1224768.663
87 | 2682399.4878 | 1224802.1973 | 2682393.0005 | 1224802.5077 | 2682387.7606 | 1224798.7104 | 2682382.192 | 1224790.7168 | 2682373.6143 | 1224768.663
88 | 2682157.6109 | 1224646.6601 | 2682165.5209 | 1224662.708
89 | 2682157.6109 | 1224646.6601 | 2682146.787 | 1224627.1444
90 | 2682399.4878 | 1224802.1973 | 2682397.2529 | 1224783.4425 | 2682396.9804 | 1224781.2798
91 | 2682399.4878 | 1224802.1973 | 2682400.8973 | 1224811.0117
92 | 2682129.9581 | 1224599.3465 | 2682132.8408 | 1224601.9992 | 2682146.787 | 1224627.1444
93 | 2682129.9581 | 1224599.3465 | 2682133.2027 | 1224591.7194 | 2682138.8592 | 1224582.3912
94 | 2682404.7947 | 1224830.3961 | 2682405.0424 | 1224831.4496 | 2682406.1263 | 1224834.7557 | 2682409.3281 | 1224843.3725 | 2682416.4156 | 1224857.7471 | 2682416.7237 | 1224858.2447
95 | 2682400.8973 | 1224811.0117 | 2682402.7009 | 1224821.4882 | 2682404.7947 | 1224830.3961
96 | 2682416.7237 | 1224858.2447 | 2682431.0396 | 1224881.3626
97 | 2682400.8973 | 1224811.0117 | 2682406.6638 | 1224810.7357 | 2682409.7056 | 1224812.8348
98 | 2682431.0396 | 1224881.3626 | 2682442.8335 | 1224900.4079
99 | 2682429.5663 | 1224830.1888 | 2682413.5857 | 1224819.0038 | 2682411.4575 | 1224816.6394 | 2682409.7056 | 1224812.8348 | 2682409.7056 | 1224812.8348
100 | 2682442.8335 | 1224900.4079 | 2682449.5148 | 1224911.1972 | 2682454.3039 | 1224920.9083
101 | 2682396.9804 | 1224781.2798 | 2682395.7029 | 1224771.1424
102 | 2682429.5663 | 1224830.1888 | 2682439.5162 | 1224837.153 | 2682447.9916 | 1224842.9151
103 | 2682454.3039 | 1224920.9083 | 2682454.5842 | 1224921.4766
104 | 2682393.4163 | 1224752.809 | 2682394.2197 | 1224759.3731 | 2682395.7029 | 1224771.1424
105 | 2682447.9916 | 1224842.9151 | 2682453.9779 | 1224846.9849
106 | 2682393.4163 | 1224752.809 | 2682392.4847 | 1224745.197
107 | 2682457.0634 | 1224926.7956 | 2682456.4989 | 1224925.3591 | 2682454.5842 | 1224921.4766
108 | 2682457.0634 | 1224926.7956 | 2682460.8127 | 1224936.3374 | 2682462.1141 | 1224943.6493 | 2682462.4948 | 1224948.3968
109 | 2682453.9779 | 1224846.9849 | 2682460.0003 | 1224851.0794 | 2682462.1893 | 1224852.4822
110 | 2682462.1893 | 1224852.4822 | 2682474.2157 | 1224860.1891
111 | 2682485.5451 | 1224866.3255 | 2682476.4219 | 1224861.6029 | 2682474.2157 | 1224860.1891
112 | 2682461.6317 | 1224808.3601 | 2682463.7291 | 1224811.3944
113 | 2682457.0003 | 1224801.6599 | 2682461.6317 | 1224808.3601
114 | 2682463.7291 | 1224811.3944 | 2682468.128 | 1224817.7583 | 2682475.7424 | 1224821.4663 | 2682481.0154 | 1224830.3567
115 | 2682481.0154 | 1224830.3567 | 2682483.5221 | 1224834.583 | 2682507.2929 | 1224850.469
116 | 2682507.2929 | 1224850.469 | 2682519.4555 | 1224858.5973 | 2682531.7014 | 1224871.2975
117 | 2682561.532 | 1224905.4347 | 2682561.6057 | 1224902.3114 | 2682531.7014 | 1224871.2975
118 | 2682485.5451 | 1224866.3255 | 2682500.0482 | 1224873.8328
119 | 2682500.0482 | 1224873.8328 | 2682509.549 | 1224878.7507
120 | 2682561.532 | 1224905.4347 | 2682510.367 | 1224879.1741 | 2682509.549 | 1224878.7507

## bus_geodata
| x | y | coords
0 | 2682300.0508 | 1224877.3216
1 | 2682305.2441 | 1224882.2653
2 | 2682286.917 | 1224864.8974
3 | 2682312.5043 | 1224889.1765
4 | 2682273.9526 | 1224852.6841
5 | 2682323.1037 | 1224899.1371
6 | 2682286.6631 | 1224826.4225
7 | 2682332.7888 | 1224908.2241
8 | 2682286.7964 | 1224824.7502
9 | 2682340.8162 | 1224915.828
10 | 2682322.3655 | 1224919.5654
11 | 2682363.6143 | 1224937.4762
12 | 2682318.1979 | 1224923.9833
13 | 2682277.901 | 1224917.8833
14 | 2682309.5685 | 1224933.131
15 | 2682328.1899 | 1224955.4267
16 | 2682339.46 | 1224968.9206
17 | 2682287.6443 | 1224802.8402
18 | 2682287.7175 | 1224800.9488
19 | 2682287.4121 | 1224782.2252
20 | 2682285.4444 | 1224771.4042
21 | 2682383.79 | 1224956.693
22 | 2682386.3131 | 1225002.3284
23 | 2682406.9451 | 1224991.8625
24 | 2682408.7279 | 1224981.3911
25 | 2682392.0377 | 1224964.5487
26 | 2682402.5116 | 1224969.9916
27 | 2682415.8318 | 1224952.5619
28 | 2682413.0113 | 1224939.5151
29 | 2682260.755 | 1224680.4771
30 | 2682258.2755 | 1224656.1343
31 | 2682260.8688 | 1224683.6252
32 | 2682256.8272 | 1224651.1591
33 | 2682261.241 | 1224693.9231
34 | 2682251.491 | 1224635.066
35 | 2682263.3961 | 1224704.6247
36 | 2682276.3683 | 1224692.2559
37 | 2682230.8192 | 1224696.1599
38 | 2682246.3954 | 1224623.4136
39 | 2682269.5135 | 1224723.1874
40 | 2682236.4564 | 1224706.8258
41 | 2682219.1056 | 1224672.3923
42 | 2682222.1151 | 1224700.8247
43 | 2682383.1027 | 1224854.7534
44 | 2682370.8444 | 1224832.1244
45 | 2682393.743 | 1224875.0666
46 | 2682361.9442 | 1224816.1655
47 | 2682406.3568 | 1224905.244
48 | 2682360.8954 | 1224814.285
49 | 2682409.0397 | 1224915.1605
50 | 2682351.464 | 1224793.8931
51 | 2682314.9899 | 1224668.6707
52 | 2682319.0156 | 1224684.3819
53 | 2682311.2819 | 1224654.199
54 | 2682338.0201 | 1224679.3148
55 | 2682323.8708 | 1224700.9981
56 | 2682327.5007 | 1224648.4718
57 | 2682307.9711 | 1224641.2679
58 | 2682364.3078 | 1224672.3058
59 | 2682328.2767 | 1224716.1613
60 | 2682330.1939 | 1224722.7673
61 | 2682244.9137 | 1224620.0253
62 | 2682242.3291 | 1224614.5993
63 | 2682209.7284 | 1224653.3655
64 | 2682216.2524 | 1224666.603
65 | 2682205.6527 | 1224645.0955
66 | 2682195.4148 | 1224628.7587
67 | 2682208.8431 | 1224618.8395
68 | 2682190.954 | 1224628.9194
69 | 2682209.1761 | 1224618.6781
70 | 2682171.7031 | 1224639.1621
71 | 2682343.5076 | 1224771.4422
72 | 2682340.8111 | 1224752.6296
73 | 2682388.2298 | 1224711.0688
74 | 2682388.3054 | 1224711.6437
75 | 2682389.1138 | 1224717.7857
76 | 2682205.3774 | 1224709.7949
77 | 2682204.8913 | 1224710.0555
78 | 2682180.5187 | 1224715.7675
79 | 2682245.4647 | 1224723.8699
80 | 2682178.2392 | 1224688.511
81 | 2682276.7121 | 1224744.3191
82 | 2682275.1509 | 1224739.7151
83 | 2682283.7717 | 1224765.1384
84 | 2682352.7793 | 1224747.7598
85 | 2682336.9762 | 1224746.1362
86 | 2682373.6143 | 1224768.663
87 | 2682165.5209 | 1224662.708
88 | 2682157.6109 | 1224646.6601
89 | 2682399.4878 | 1224802.1973
90 | 2682146.787 | 1224627.1444
91 | 2682129.9581 | 1224599.3465
92 | 2682138.8592 | 1224582.3912
93 | 2682404.7947 | 1224830.3961
94 | 2682416.7237 | 1224858.2447
95 | 2682400.8973 | 1224811.0117
96 | 2682431.0396 | 1224881.3626
97 | 2682409.7056 | 1224812.8348
98 | 2682442.8335 | 1224900.4079
99 | 2682396.9804 | 1224781.2798
100 | 2682429.5663 | 1224830.1888
101 | 2682454.3039 | 1224920.9083
102 | 2682395.7029 | 1224771.1424
103 | 2682447.9916 | 1224842.9151
104 | 2682392.4847 | 1224745.197
105 | 2682393.4163 | 1224752.809
106 | 2682454.5842 | 1224921.4766
107 | 2682457.0634 | 1224926.7956
108 | 2682453.9779 | 1224846.9849
109 | 2682462.1893 | 1224852.4822
110 | 2682474.2157 | 1224860.1891
111 | 2682461.6317 | 1224808.3601
112 | 2682463.7291 | 1224811.3944
113 | 2682457.0003 | 1224801.6599
114 | 2682481.0154 | 1224830.3567
115 | 2682507.2929 | 1224850.469
116 | 2682531.7014 | 1224871.2975
117 | 2682485.5451 | 1224866.3255
118 | 2682500.0482 | 1224873.8328
119 | 2682509.549 | 1224878.7507
120 | 2682462.4948 | 1224948.3968
121 | 2682561.532 | 1224905.4347
122 | 2682340.8111 | 1224752.6296

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98046 | -0.374 | 0.0022278 | 0.00055835
1 | 0.98072 | -0.36888 | 0.0058138 | 0.0014571
2 | 0.9798 | -0.38674 | 0.0028142 | 0.00070531
3 | 0.9811 | -0.36146 | 0.00048173 | 0.00012073
4 | 0.97917 | -0.39908 | 0 | 0
5 | 0.98166 | -0.35068 | 0.0062509 | 0.0015666
6 | 0.97811 | -0.41983 | 0.0033516 | 0.00083999
7 | 0.98218 | -0.34047 | 0 | 0
8 | 0.97805 | -0.42098 | 0.0037796 | 0.00094726
9 | 0.98274 | -0.32962 | 0.0043203 | 0.0010828
10 | 0.9815 | -0.35383 | 0.0057331 | 0.0014368
11 | 0.98436 | -0.29821 | 0.0044422 | 0.0011133
12 | 0.98127 | -0.35841 | 0.012631 | 0.0031656
13 | 0.9809 | -0.36556 | 0.00086191 | 0.00021601
14 | 0.98093 | -0.36501 | 0 | 0
15 | 0.98017 | -0.37982 | 0.013921 | 0.0034889
16 | 0.97994 | -0.38435 | 0.014199 | 0.0035587
17 | 0.97731 | -0.43551 | 0.0043344 | 0.0010863
18 | 0.97725 | -0.43673 | 0.0029673 | 0.00074368
19 | 0.97665 | -0.44853 | 0.0048324 | 0.0012111
20 | 0.9763 | -0.45524 | 0.0038623 | 0.00096797
21 | 0.98583 | -0.2699 | 0.0041874 | 0.0010495
22 | 0.98766 | -0.23449 | 0.0031755 | 0.00079587
23 | 0.98773 | -0.23317 | 0 | 0
24 | 0.98778 | -0.23234 | 0 | 0
25 | 0.98644 | -0.25814 | 0 | 0
26 | 0.98707 | -0.24592 | 0.0032695 | 0.00081942
27 | 0.98961 | -0.19711 | 0.0020012 | 0.00050156
28 | 0.99035 | -0.18294 | 0.0034994 | 0.00087703
29 | 0.97378 | -0.50483 | 0.0038991 | 0.00097721
30 | 0.97339 | -0.51262 | 0.0052 | 0.0013032
31 | 0.97385 | -0.50361 | 0.0043228 | 0.0010834
32 | 0.97333 | -0.51377 | 0.0030879 | 0.0007739
33 | 0.97409 | -0.49878 | 0 | 0
34 | 0.97319 | -0.51658 | 0.0030557 | 0.00076584
35 | 0.97437 | -0.49335 | 0.0028307 | 0.00070945
36 | 0.97404 | -0.49978 | 0.0036069 | 0.00090397
37 | 0.97352 | -0.51002 | 0 | 0
38 | 0.97312 | -0.51797 | 0.002972 | 0.00074486
39 | 0.97487 | -0.48338 | 0.0022719 | 0.00056938
40 | 0.97343 | -0.51182 | 0.0041163 | 0.0010316
41 | 0.97319 | -0.51651 | 0.0050797 | 0.0012731
42 | 0.97336 | -0.51325 | 0.00413 | 0.0010351
43 | 0.99566 | -0.081827 | 0.006331 | 0.0015867
44 | 0.99725 | -0.051817 | 0.0044521 | 0.0011158
45 | 0.99428 | -0.108 | 0.0033594 | 0.00084195
46 | 0.9984 | -0.030214 | 0.0053124 | 0.0013314
47 | 0.99233 | -0.14511 | 0.0086277 | 0.0021623
48 | 0.99853 | -0.027621 | 0.0056151 | 0.0014073
49 | 0.99174 | -0.15639 | 0.0049767 | 0.0012473
50 | 1 | 0 | -0.59667 | -0.15253
51 | 0.99212 | -0.15111 | 0.0096021 | 0.0024065
52 | 0.99255 | -0.14293 | 0 | 0
53 | 0.99187 | -0.1561 | 0 | 0
54 | 0.99208 | -0.15192 | 0.012272 | 0.0030756
55 | 0.9934 | -0.12631 | 0.0053196 | 0.0013332
56 | 0.99167 | -0.15982 | 0.012195 | 0.0030563
57 | 0.99178 | -0.15768 | 0.006679 | 0.0016739
58 | 0.99174 | -0.15846 | 0.013557 | 0.0033976
59 | 0.99427 | -0.1097 | 0.010456 | 0.0026205
60 | 0.99471 | -0.1012 | 0.0070767 | 0.0017736
61 | 0.97311 | -0.51818 | 0 | 0
62 | 0.97309 | -0.51851 | 0.0029742 | 0.00074542
63 | 0.97297 | -0.52082 | 0.0036315 | 0.00091013
64 | 0.97312 | -0.51794 | 0.0057962 | 0.0014527
65 | 0.97289 | -0.52246 | 0.0050383 | 0.0012627
66 | 0.97258 | -0.52853 | 0 | 0
67 | 0.97244 | -0.53127 | 0.0033749 | 0.00084582
68 | 0.97248 | -0.53061 | 0.0080631 | 0.0020208
69 | 0.97244 | -0.53131 | 0.0051588 | 0.0012929
70 | 0.97213 | -0.53748 | 0.0042139 | 0.0010561
71 | 0.99833 | -0.031756 | 0.0079102 | 0.0019825
72 | 0.99699 | -0.057263 | 0 | 0
73 | 0.98995 | -0.19249 | 0.0056754 | 0.0014224
74 | 0.98995 | -0.19243 | 0.004351 | 0.0010905
75 | 0.99001 | -0.19133 | 0.0095346 | 0.0023896
76 | 0.97312 | -0.51803 | 0.0035494 | 0.00088956
77 | 0.97311 | -0.51813 | 0.0053136 | 0.0013317
78 | 0.97299 | -0.52043 | 0 | 0
79 | 0.97336 | -0.51323 | 0.0039749 | 0.0009962
80 | 0.97287 | -0.5229 | 0.0048088 | 0.0012052
81 | 0.97547 | -0.47167 | 0.0069022 | 0.0017299
82 | 0.97533 | -0.4743 | 0.0048 | 0.001203
83 | 0.97611 | -0.45909 | 0.0042825 | 0.0010733
84 | 0.99632 | -0.069983 | 0.011034 | 0.0027654
85 | 0.99642 | -0.068183 | 0.0023361 | 0.00058549
86 | 0.99477 | -0.099524 | 0.010005 | 0.0025076
87 | 0.97181 | -0.54378 | 0.0075628 | 0.0018954
88 | 0.97194 | -0.54128 | 0 | 0
89 | 0.99267 | -0.13978 | 0 | 0
90 | 0.97183 | -0.54348 | 0.0043134 | 0.001081
91 | 0.9718 | -0.54409 | 0 | 0
92 | 0.97178 | -0.54445 | 0.0010153 | 0.00025445
93 | 0.99165 | -0.15946 | 0.0077543 | 0.0019434
94 | 0.99078 | -0.17644 | 0.0064826 | 0.0016247
95 | 0.99236 | -0.14569 | 0 | 0
96 | 0.99015 | -0.18853 | 0.0049931 | 0.0012514
97 | 0.99212 | -0.15033 | 0.0035804 | 0.00089732
98 | 0.98974 | -0.19652 | 0.0068468 | 0.001716
99 | 0.99177 | -0.15729 | 0.0033763 | 0.00084619
100 | 0.99079 | -0.1758 | 0.0030067 | 0.00075355
101 | 0.98946 | -0.20204 | 0.0031521 | 0.00078998
102 | 0.99136 | -0.16518 | 0.0052779 | 0.0013228
103 | 0.98863 | -0.21721 | 0.0054982 | 0.001378
104 | 0.99051 | -0.18173 | 0.0097087 | 0.0024332
105 | 0.99071 | -0.17774 | 0.0090227 | 0.0022613
106 | 0.98945 | -0.20216 | 0.0032583 | 0.00081661
107 | 0.98941 | -0.20287 | 0.0034969 | 0.00087641
108 | 0.98797 | -0.22992 | 0.0062097 | 0.0015563
109 | 0.98713 | -0.24621 | 0.0043735 | 0.0010961
110 | 0.98596 | -0.26868 | 0.003524 | 0.0008832
111 | 0.9736 | -0.50987 | 0.0060061 | 0.0015053
112 | 0.97364 | -0.5091 | 0.014221 | 0.003564
113 | 0.97356 | -0.51067 | 0.0053352 | 0.0013371
114 | 0.97427 | -0.49664 | 0.0092135 | 0.0023091
115 | 0.97536 | -0.47527 | 0.012789 | 0.0032052
116 | 0.97679 | -0.44718 | 0.016912 | 0.0042387
117 | 0.98495 | -0.28819 | 0.0074496 | 0.001867
118 | 0.98378 | -0.31076 | 0.004507 | 0.0011296
119 | 0.98306 | -0.32471 | 0.0078696 | 0.0019723
120 | 0.98935 | -0.20418 | 0.0032893 | 0.00082439
121 | 0.97956 | -0.39291 | 0 | 0
122 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.15846 | -0.040059 | 0.15849 | 0.040083 | 3.8915e-05 | 2.4544e-05 | 0.24061 | 0.24061 | 0.24061 | 0.98046 | -0.374 | 0.98072 | -0.36888 | 16.5253
1 | 0.15623 | 0.039501 | -0.15613 | -0.03944 | 9.5385e-05 | 6.0135e-05 | 0.23723 | 0.23723 | 0.23723 | 0.98046 | -0.374 | 0.9798 | -0.38674 | 16.2931
2 | -0.16431 | -0.041541 | 0.16437 | 0.041577 | 5.8465e-05 | 3.6912e-05 | 0.24943 | 0.24943 | 0.24943 | 0.98072 | -0.36888 | 0.9811 | -0.36146 | 17.1311
3 | 0.15332 | 0.038735 | -0.15323 | -0.038678 | 9.0616e-05 | 5.7097e-05 | 0.23295 | 0.23295 | 0.23295 | 0.9798 | -0.38674 | 0.97917 | -0.39908 | 15.9996
4 | -0.16485 | -0.041698 | 0.16493 | 0.041752 | 8.5335e-05 | 5.3879e-05 | 0.25016 | 0.25016 | 0.25016 | 0.9811 | -0.36146 | 0.98166 | -0.35068 | 17.1813
5 | 0.15323 | 0.038678 | -0.15308 | -0.038582 | 0.0001522 | 9.5903e-05 | 0.23295 | 0.23295 | 0.23295 | 0.97917 | -0.39908 | 0.97811 | -0.41983 | 15.9996
6 | -0.17118 | -0.043319 | 0.17127 | 0.043372 | 8.3929e-05 | 5.3043e-05 | 0.25963 | 0.25963 | 0.25963 | 0.98166 | -0.35068 | 0.98218 | -0.34047 | 17.8321
7 | 0.14972 | 0.037742 | -0.14972 | -0.037737 | 8.183e-06 | 5.1527e-06 | 0.22786 | 0.22786 | 0.22786 | 0.97811 | -0.41983 | 0.97805 | -0.42098 | 15.6494
8 | -0.21869 | -0.055282 | 0.2188 | 0.055354 | 0.0001139 | 7.2337e-05 | 0.33148 | 0.33148 | 0.33148 | 0.98218 | -0.34047 | 0.98274 | -0.32962 | 22.7666
9 | 0.047418 | 0.01191 | -0.047387 | -0.011891 | 3.0219e-05 | 1.9143e-05 | 0.071847 | 0.071848 | 0.071848 | 0.98218 | -0.34047 | 0.9815 | -0.35383 | 19.7383
10 | 0.14594 | 0.03679 | -0.14583 | -0.036726 | 0.0001014 | 6.3799e-05 | 0.22211 | 0.22211 | 0.22211 | 0.97805 | -0.42098 | 0.97731 | -0.43551 | 15.2545
11 | -0.22312 | -0.056437 | 0.22346 | 0.056651 | 0.00033677 | 0.00021394 | 0.33802 | 0.33802 | 0.33802 | 0.98274 | -0.32962 | 0.98436 | -0.29821 | 23.2159
12 | 0.041654 | 0.010454 | -0.041645 | -0.010449 | 9.0842e-06 | 5.7372e-06 | 0.063156 | 0.063156 | 0.063156 | 0.9815 | -0.35383 | 0.98127 | -0.35841 | 17.3505
13 | -0.2279 | -0.057764 | 0.22821 | 0.057962 | 0.00031044 | 0.00019726 | 0.34474 | 0.34474 | 0.34474 | 0.98436 | -0.29821 | 0.98583 | -0.2699 | 23.677
14 | 0.029014 | 0.0072829 | -0.029005 | -0.0072772 | 9.1307e-06 | 5.6849e-06 | 0.044002 | 0.044002 | 0.044002 | 0.98127 | -0.35841 | 0.98093 | -0.36501 | 12.0884
15 | -0.00086191 | -0.00021601 | 0.00086193 | 0.00021558 | 2.253e-08 | -4.2925e-07 | 0.0013075 | 0.0013073 | 0.0013075 | 0.9809 | -0.36556 | 0.98093 | -0.36501 | 0.3592
16 | 0.028143 | 0.0070617 | -0.028123 | -0.0070493 | 1.9857e-05 | 1.2342e-05 | 0.042695 | 0.042695 | 0.042695 | 0.98093 | -0.36501 | 0.98017 | -0.37982 | 11.7293
17 | 0.014202 | 0.0035604 | -0.014199 | -0.0035587 | 3.065e-06 | 1.7401e-06 | 0.021561 | 0.021561 | 0.021561 | 0.98017 | -0.37982 | 0.97994 | -0.38435 | 5.9235
18 | 0.1415 | 0.03564 | -0.14149 | -0.035634 | 8.2415e-06 | 5.1797e-06 | 0.21551 | 0.21551 | 0.21551 | 0.97731 | -0.43551 | 0.97725 | -0.43673 | 14.8013
19 | 0.13852 | 0.034891 | -0.13845 | -0.034842 | 7.8166e-05 | 4.9088e-05 | 0.21099 | 0.21099 | 0.21099 | 0.97725 | -0.43673 | 0.97665 | -0.44853 | 14.491
20 | 0.13361 | 0.033631 | -0.13357 | -0.033604 | 4.2825e-05 | 2.6857e-05 | 0.20363 | 0.20363 | 0.20363 | 0.97665 | -0.44853 | 0.9763 | -0.45524 | 13.9853
21 | 0.12971 | 0.032636 | -0.12969 | -0.032621 | 2.382e-05 | 1.492e-05 | 0.19774 | 0.19774 | 0.19774 | 0.9763 | -0.45524 | 0.97611 | -0.45909 | 13.581
22 | -0.2324 | -0.059011 | 0.23253 | 0.059095 | 0.0001316 | 8.3643e-05 | 0.35106 | 0.35106 | 0.35106 | 0.98583 | -0.2699 | 0.98644 | -0.25814 | 24.1111
23 | -0.0031755 | -0.00079587 | 0.0031757 | 0.0007957 | 2.0046e-07 | -1.7061e-07 | 0.0047843 | 0.0047842 | 0.0047843 | 0.98766 | -0.23449 | 0.98773 | -0.23317 | 1.3144
24 | -0.0031757 | -0.0007957 | 0.0031759 | 0.00079559 | 1.2483e-07 | -1.0627e-07 | 0.0047842 | 0.0047841 | 0.0047842 | 0.98773 | -0.23317 | 0.98778 | -0.23234 | 1.3143
25 | -0.23927 | -0.060895 | 0.23967 | 0.061154 | 0.00040712 | 0.00025885 | 0.36077 | 0.36077 | 0.36077 | 0.98778 | -0.23234 | 0.98961 | -0.19711 | 24.7781
26 | 0.23609 | 0.060099 | -0.23594 | -0.060001 | 0.00015442 | 9.8164e-05 | 0.35599 | 0.35599 | 0.35599 | 0.98778 | -0.23234 | 0.98707 | -0.24592 | 24.4496
27 | -0.23253 | -0.059095 | 0.23267 | 0.059182 | 0.00013695 | 8.7042e-05 | 0.35106 | 0.35106 | 0.35106 | 0.98644 | -0.25814 | 0.98707 | -0.24592 | 24.1111
28 | -0.24167 | -0.061655 | 0.24184 | 0.061761 | 0.0001656 | 0.0001053 | 0.36378 | 0.36378 | 0.36378 | 0.98961 | -0.19711 | 0.99035 | -0.18294 | 24.9848
29 | -0.24534 | -0.062638 | 0.24565 | 0.062838 | 0.00031515 | 0.00020042 | 0.36904 | 0.36904 | 0.36904 | 0.99035 | -0.18294 | 0.99174 | -0.15639 | 25.3459
30 | 0.017299 | 0.004338 | -0.017292 | -0.0043342 | 6.4141e-06 | 3.8007e-06 | 0.026435 | 0.026435 | 0.026435 | 0.97378 | -0.50483 | 0.97339 | -0.51262 | 7.2623
31 | -0.021198 | -0.0053152 | 0.021199 | 0.005316 | 1.2395e-06 | 7.5411e-07 | 0.032393 | 0.032393 | 0.032393 | 0.97378 | -0.50483 | 0.97385 | -0.50361 | 8.8991
32 | 0.012092 | 0.003031 | -0.012092 | -0.0030306 | 6.64e-07 | 3.6055e-07 | 0.018485 | 0.018485 | 0.018485 | 0.97339 | -0.51262 | 0.97333 | -0.51377 | 5.0784
33 | -0.025522 | -0.0063994 | 0.025528 | 0.006403 | 5.8768e-06 | 3.6329e-06 | 0.038998 | 0.038998 | 0.038998 | 0.97385 | -0.50361 | 0.97409 | -0.49878 | 10.7137
34 | 0.0090037 | 0.0022567 | -0.0090025 | -0.0022561 | 1.2067e-06 | 5.6124e-07 | 0.013765 | 0.013765 | 0.013765 | 0.97333 | -0.51377 | 0.97319 | -0.51658 | 3.7816
35 | -0.10838 | -0.027198 | 0.10841 | 0.027216 | 2.8055e-05 | 1.7412e-05 | 0.16557 | 0.16557 | 0.16557 | 0.97409 | -0.49878 | 0.97437 | -0.49335 | 11.3716
36 | 0.003607 | 0.00090389 | -0.0036069 | -0.00090397 | 1.7327e-07 | -7.8544e-08 | 0.0055101 | 0.0055101 | 0.0055101 | 0.97409 | -0.49878 | 0.97404 | -0.49978 | 1.5138
37 | 0.079243 | 0.019892 | -0.0792 | -0.019866 | 4.2473e-05 | 2.5645e-05 | 0.12106 | 0.12106 | 0.12106 | 0.97409 | -0.49878 | 0.97352 | -0.51002 | 8.3147
38 | 0.0059467 | 0.0014903 | -0.0059463 | -0.0014902 | 3.943e-07 | 9.434e-08 | 0.0090926 | 0.0090927 | 0.0090927 | 0.97319 | -0.51658 | 0.97312 | -0.51797 | 2.498
39 | -0.11124 | -0.027925 | 0.11129 | 0.027958 | 5.2944e-05 | 3.2909e-05 | 0.16989 | 0.16989 | 0.16989 | 0.97437 | -0.49335 | 0.97487 | -0.48338 | 11.6685
40 | 0.0080921 | 0.0020281 | -0.0080914 | -0.0020278 | 6.921e-07 | 2.9296e-07 | 0.012369 | 0.012369 | 0.012369 | 0.97352 | -0.51002 | 0.97343 | -0.51182 | 3.398
41 | 0.053299 | 0.013373 | -0.053283 | -0.013364 | 1.6489e-05 | 9.2357e-06 | 0.081473 | 0.081473 | 0.081473 | 0.97352 | -0.51002 | 0.97319 | -0.51651 | 5.5957
42 | 0.017809 | 0.004465 | -0.017806 | -0.0044634 | 2.7441e-06 | 1.6334e-06 | 0.027221 | 0.027221 | 0.027221 | 0.97352 | -0.51002 | 0.97336 | -0.51325 | 7.4783
43 | 0.0029743 | 0.00074534 | -0.0029743 | -0.00074537 | 2.8686e-08 | -2.7584e-08 | 0.0045481 | 0.0045481 | 0.0045481 | 0.97312 | -0.51797 | 0.97311 | -0.51818 | 1.2495
44 | -0.11356 | -0.028528 | 0.11361 | 0.028558 | 4.9202e-05 | 3.0618e-05 | 0.17336 | 0.17336 | 0.17336 | 0.97487 | -0.48338 | 0.97533 | -0.4743 | 11.9066
45 | 0.0039751 | 0.00099613 | -0.0039749 | -0.0009962 | 2.6694e-07 | -6.8798e-08 | 0.0060765 | 0.0060766 | 0.0060766 | 0.97343 | -0.51182 | 0.97336 | -0.51323 | 1.6694
46 | 0.048203 | 0.012091 | -0.0482 | -0.012089 | 3.2872e-06 | 1.7831e-06 | 0.073706 | 0.073706 | 0.073706 | 0.97319 | -0.51651 | 0.97312 | -0.51794 | 5.0623
47 | 0.013676 | 0.0034283 | -0.013673 | -0.0034265 | 3.1129e-06 | 1.7563e-06 | 0.020907 | 0.020908 | 0.020908 | 0.97336 | -0.51325 | 0.97312 | -0.51803 | 5.7438
48 | -0.26989 | -0.069273 | 0.27028 | 0.069524 | 0.00039369 | 0.00025062 | 0.40393 | 0.40393 | 0.40393 | 0.99566 | -0.081827 | 0.99725 | -0.051817 | 27.7423
49 | 0.26356 | 0.067687 | -0.26322 | -0.067474 | 0.00033452 | 0.0002129 | 0.39447 | 0.39447 | 0.39447 | 0.99566 | -0.081827 | 0.99428 | -0.108 | 27.0925
50 | -0.27473 | -0.07064 | 0.27502 | 0.070824 | 0.00028877 | 0.00018386 | 0.41057 | 0.41057 | 0.41057 | 0.99725 | -0.051817 | 0.9984 | -0.030214 | 28.1985
51 | 0.25986 | 0.066632 | -0.2594 | -0.066335 | 0.0004666 | 0.00029693 | 0.38944 | 0.38944 | 0.38944 | 0.99428 | -0.108 | 0.99233 | -0.14511 | 26.7472
52 | -0.28033 | -0.072155 | 0.28037 | 0.072178 | 3.5353e-05 | 2.2513e-05 | 0.41849 | 0.41849 | 0.41849 | 0.9984 | -0.030214 | 0.99853 | -0.027621 | 28.7422
53 | 0.25077 | 0.064172 | -0.25063 | -0.064085 | 0.00013695 | 8.7115e-05 | 0.3765 | 0.3765 | 0.3765 | 0.99233 | -0.14511 | 0.99174 | -0.15639 | 25.8587
54 | -0.28598 | -0.073585 | 0.28637 | 0.07383 | 0.00038467 | 0.00024501 | 0.42685 | 0.42685 | 0.42685 | 0.99853 | -0.027621 | 1 | 0 | 29.3169
55 | 0.30865 | 0.078697 | -0.30818 | -0.078396 | 0.00047239 | 0.00030108 | 0.45975 | 0.45975 | 0.45975 | 1 | 0 | 0.99833 | -0.031756 | 31.5764
56 | -0.028483 | -0.0071407 | 0.028494 | 0.0071476 | 1.11e-05 | 6.8944e-06 | 0.04272 | 0.04272 | 0.04272 | 0.99212 | -0.15111 | 0.99255 | -0.14293 | 11.7364
57 | 0.018881 | 0.0047342 | -0.018876 | -0.0047315 | 4.4928e-06 | 2.6825e-06 | 0.028319 | 0.028319 | 0.028319 | 0.99212 | -0.15111 | 0.99187 | -0.1561 | 7.7799
58 | 0.025844 | 0.0064824 | -0.025833 | -0.0064756 | 1.1073e-05 | 6.8328e-06 | 0.038747 | 0.038747 | 0.038747 | 0.99255 | -0.14293 | 0.99208 | -0.15192 | 10.6448
59 | -0.054338 | -0.01363 | 0.054381 | 0.013657 | 4.3084e-05 | 2.735e-05 | 0.081467 | 0.081467 | 0.081467 | 0.99255 | -0.14293 | 0.9934 | -0.12631 | 22.3811
60 | 0.012197 | 0.0030575 | -0.012195 | -0.0030563 | 2.1597e-06 | 1.1602e-06 | 0.018298 | 0.018298 | 0.018298 | 0.99187 | -0.1561 | 0.99167 | -0.15982 | 5.027
61 | 0.0066795 | 0.0016741 | -0.006679 | -0.0016739 | 5.0264e-07 | 1.4942e-07 | 0.010021 | 0.010021 | 0.010021 | 0.99187 | -0.1561 | 0.99178 | -0.15768 | 2.753
62 | 0.013561 | 0.0034 | -0.013557 | -0.0033976 | 4.221e-06 | 2.3503e-06 | 0.02034 | 0.02034 | 0.02034 | 0.99208 | -0.15192 | 0.99174 | -0.15846 | 5.588
63 | -0.059701 | -0.014991 | 0.059748 | 0.015021 | 4.7363e-05 | 3.0108e-05 | 0.089435 | 0.089435 | 0.089435 | 0.9934 | -0.12631 | 0.99427 | -0.1097 | 24.5702
64 | -0.070204 | -0.017641 | 0.070232 | 0.017659 | 2.8484e-05 | 1.814e-05 | 0.10508 | 0.10508 | 0.10508 | 0.99427 | -0.1097 | 0.99471 | -0.1012 | 28.8691
65 | -0.077309 | -0.019433 | 0.077431 | 0.019511 | 0.00012209 | 7.7819e-05 | 0.11567 | 0.11567 | 0.11567 | 0.99471 | -0.1012 | 0.99642 | -0.068183 | 31.7774
66 | 0.0029743 | 0.00074537 | -0.0029742 | -0.00074542 | 4.662e-08 | -4.4827e-08 | 0.0045481 | 0.0045481 | 0.0045481 | 0.97311 | -0.51818 | 0.97309 | -0.51851 | 1.2495
67 | -0.042398 | -0.010633 | 0.042404 | 0.010636 | 5.8174e-06 | 2.9898e-06 | 0.064844 | 0.064843 | 0.064844 | 0.97297 | -0.52082 | 0.97312 | -0.51794 | 4.4535
68 | 0.038766 | 0.009723 | -0.038763 | -0.0097215 | 3.0385e-06 | 1.4866e-06 | 0.05929 | 0.05929 | 0.05929 | 0.97297 | -0.52082 | 0.97289 | -0.52246 | 4.0721
69 | 0.033725 | 0.0084588 | -0.033715 | -0.008453 | 9.7565e-06 | 5.7587e-06 | 0.051584 | 0.051584 | 0.051584 | 0.97289 | -0.52246 | 0.97258 | -0.52853 | 7.0857
70 | 0.0085348 | 0.0021392 | -0.0085336 | -0.0021387 | 1.1123e-06 | 4.9604e-07 | 0.013058 | 0.013058 | 0.013058 | 0.97258 | -0.52853 | 0.97244 | -0.53127 | 3.5874
71 | 0.02518 | 0.0063138 | -0.025178 | -0.0063123 | 2.4845e-06 | 1.5347e-06 | 0.038526 | 0.038526 | 0.038526 | 0.97258 | -0.52853 | 0.97248 | -0.53061 | 10.5841
72 | 0.0051588 | 0.0012929 | -0.0051588 | -0.0012929 | 8.6457e-09 | 9.4313e-10 | 0.0078939 | 0.0078939 | 0.0078939 | 0.97244 | -0.53127 | 0.97244 | -0.53131 | 2.1686
73 | 0.017115 | 0.0042915 | -0.017109 | -0.0042881 | 5.6084e-06 | 3.3189e-06 | 0.026189 | 0.026189 | 0.026189 | 0.97248 | -0.53061 | 0.97213 | -0.53748 | 7.1947
74 | 0.012895 | 0.003232 | -0.012893 | -0.0032307 | 2.3322e-06 | 1.2948e-06 | 0.019739 | 0.019739 | 0.019739 | 0.97213 | -0.53748 | 0.97194 | -0.54128 | 5.4227
75 | 0.30027 | 0.076414 | -0.2999 | -0.076179 | 0.00036871 | 0.00023495 | 0.44796 | 0.44796 | 0.44796 | 0.99833 | -0.031756 | 0.99699 | -0.057263 | 30.7666
76 | 0.22009 | 0.056056 | -0.21996 | -0.05597 | 0.00013495 | 8.5676e-05 | 0.3288 | 0.3288 | 0.3288 | 0.99699 | -0.057263 | 0.99632 | -0.069983 | 22.5827
77 | 0.079809 | 0.020123 | -0.079767 | -0.020096 | 4.1687e-05 | 2.6578e-05 | 0.11916 | 0.11916 | 0.11916 | 0.99699 | -0.057263 | 0.99642 | -0.068183 | 32.7358
78 | -0.0056754 | -0.0014224 | 0.0056754 | 0.0014224 | 1.5824e-08 | 2.6725e-09 | 0.0085309 | 0.0085309 | 0.0085309 | 0.98995 | -0.19249 | 0.98995 | -0.19243 | 2.3436
79 | -0.010026 | -0.0025129 | 0.010027 | 0.0025131 | 5.2766e-07 | 2.5805e-07 | 0.015071 | 0.015071 | 0.015071 | 0.98995 | -0.19243 | 0.99001 | -0.19133 | 4.1404
80 | -0.019562 | -0.0049027 | 0.019571 | 0.0049081 | 8.953e-06 | 5.3746e-06 | 0.029402 | 0.029402 | 0.029402 | 0.99001 | -0.19133 | 0.99051 | -0.18173 | 8.0774
81 | 0.010124 | 0.002537 | -0.010124 | -0.0025369 | 4.956e-08 | 2.4866e-08 | 0.01548 | 0.01548 | 0.01548 | 0.97312 | -0.51803 | 0.97311 | -0.51813 | 4.2528
82 | 0.0048099 | 0.0012052 | -0.0048093 | -0.0012052 | 5.2537e-07 | 1.4527e-08 | 0.0073548 | 0.0073549 | 0.0073549 | 0.97311 | -0.51813 | 0.97299 | -0.52043 | 2.0206
83 | 0.0048093 | 0.0012052 | -0.0048088 | -0.0012052 | 5.6541e-07 | 1.5731e-08 | 0.0073549 | 0.0073551 | 0.0073551 | 0.97299 | -0.52043 | 0.97287 | -0.5229 | 2.0206
84 | 0.11843 | 0.029771 | -0.11841 | -0.029761 | 1.4879e-05 | 9.2799e-06 | 0.18068 | 0.18068 | 0.18068 | 0.97547 | -0.47167 | 0.97533 | -0.4743 | 12.4095
85 | -0.12533 | -0.0315 | 0.1254 | 0.031548 | 7.5353e-05 | 4.7127e-05 | 0.19121 | 0.19121 | 0.19121 | 0.97547 | -0.47167 | 0.97611 | -0.45909 | 13.1327
86 | 0.20892 | 0.053205 | -0.20862 | -0.053016 | 0.00029721 | 0.00018852 | 0.31233 | 0.31233 | 0.31233 | 0.99632 | -0.069983 | 0.99477 | -0.099524 | 21.451
87 | 0.19862 | 0.050509 | -0.19823 | -0.050265 | 0.0003844 | 0.00024361 | 0.29736 | 0.29736 | 0.29736 | 0.99477 | -0.099524 | 0.99267 | -0.13978 | 20.4231
88 | -0.0075628 | -0.0018954 | 0.0075637 | 0.0018958 | 8.9969e-07 | 3.541e-07 | 0.01158 | 0.01158 | 0.01158 | 0.97181 | -0.54378 | 0.97194 | -0.54128 | 3.1813
89 | 0.0053293 | 0.001335 | -0.0053287 | -0.0013349 | 5.5706e-07 | 7.9978e-08 | 0.0081587 | 0.0081588 | 0.0081588 | 0.97194 | -0.54128 | 0.97183 | -0.54348 | 2.2414
90 | 0.04704 | 0.011825 | -0.047001 | -0.0118 | 3.9295e-05 | 2.4877e-05 | 0.070526 | 0.070526 | 0.070526 | 0.99267 | -0.13978 | 0.99177 | -0.15729 | 19.3753
91 | 0.15119 | 0.03844 | -0.15115 | -0.038413 | 4.3062e-05 | 2.7098e-05 | 0.22683 | 0.22683 | 0.22683 | 0.99267 | -0.13978 | 0.99236 | -0.14569 | 15.5793
92 | 0.0010153 | 0.00025384 | -0.0010153 | -0.00025423 | 2.9605e-08 | -3.8585e-07 | 0.0015544 | 0.0015545 | 0.0015545 | 0.97183 | -0.54348 | 0.9718 | -0.54409 | 0.42707
93 | 0.0010153 | 0.00025423 | -0.0010153 | -0.00025445 | 1.7399e-08 | -2.2672e-07 | 0.0015545 | 0.0015546 | 0.0015546 | 0.9718 | -0.54409 | 0.97178 | -0.54445 | 0.4271
94 | 0.031571 | 0.0079307 | -0.031545 | -0.0079148 | 2.5563e-05 | 1.5969e-05 | 0.04738 | 0.04738 | 0.04738 | 0.99165 | -0.15946 | 0.99078 | -0.17644 | 13.0164
95 | -0.039325 | -0.0098741 | 0.039351 | 0.0098904 | 2.5835e-05 | 1.6279e-05 | 0.059015 | 0.059015 | 0.059015 | 0.99165 | -0.15946 | 0.99236 | -0.14569 | 16.213
96 | 0.025063 | 0.0062901 | -0.025048 | -0.0062812 | 1.4449e-05 | 8.8977e-06 | 0.037644 | 0.037644 | 0.037644 | 0.99078 | -0.17644 | 0.99015 | -0.18853 | 10.3417
97 | 0.1118 | 0.028523 | -0.11177 | -0.028507 | 2.5001e-05 | 1.5511e-05 | 0.16782 | 0.16782 | 0.16782 | 0.99236 | -0.14569 | 0.99212 | -0.15033 | 11.5261
98 | 0.020055 | 0.0050298 | -0.020047 | -0.0050252 | 7.6313e-06 | 4.596e-06 | 0.03014 | 0.03014 | 0.03014 | 0.99015 | -0.18853 | 0.98974 | -0.19652 | 8.2803
99 | 0.10819 | 0.02761 | -0.10806 | -0.027525 | 0.00013298 | 8.4417e-05 | 0.16245 | 0.16245 | 0.16245 | 0.99212 | -0.15033 | 0.99079 | -0.1758 | 22.3146
100 | 0.013201 | 0.0033093 | -0.013197 | -0.0033073 | 3.4739e-06 | 1.9211e-06 | 0.019847 | 0.019847 | 0.019847 | 0.98974 | -0.19652 | 0.98946 | -0.20204 | 5.4524
101 | 0.043625 | 0.010954 | -0.043608 | -0.010943 | 1.6419e-05 | 1.0376e-05 | 0.06546 | 0.065461 | 0.065461 | 0.99177 | -0.15729 | 0.99136 | -0.16518 | 17.9837
102 | 0.10505 | 0.026772 | -0.10485 | -0.026638 | 0.00020946 | 0.00013377 | 0.15793 | 0.15793 | 0.15793 | 0.99079 | -0.1758 | 0.98863 | -0.21721 | 43.3887
103 | 0.010045 | 0.0025173 | -0.010045 | -0.0025173 | 5.4227e-08 | 2.6566e-08 | 0.015106 | 0.015106 | 0.015106 | 0.98946 | -0.20204 | 0.98945 | -0.20216 | 4.1501
104 | 0.03833 | 0.0096205 | -0.038308 | -0.0096061 | 2.2937e-05 | 1.4442e-05 | 0.057538 | 0.057539 | 0.057539 | 0.99136 | -0.16518 | 0.99071 | -0.17774 | 15.8073
105 | 0.099347 | 0.02526 | -0.099286 | -0.025221 | 6.08e-05 | 3.8819e-05 | 0.14966 | 0.14966 | 0.14966 | 0.98863 | -0.21721 | 0.98797 | -0.22992 | 41.1152
106 | -0.029279 | -0.0073413 | 0.029285 | 0.0073448 | 5.5641e-06 | 3.4623e-06 | 0.043987 | 0.043987 | 0.043987 | 0.99051 | -0.18173 | 0.99071 | -0.17774 | 12.0843
107 | 0.0067867 | 0.0017007 | -0.0067865 | -0.0017006 | 2.294e-07 | 7.1392e-08 | 0.010206 | 0.010206 | 0.010206 | 0.98945 | -0.20216 | 0.98941 | -0.20287 | 2.8039
108 | 0.0032896 | 0.00082423 | -0.0032893 | -0.00082439 | 2.0597e-07 | -1.5637e-07 | 0.0049472 | 0.0049473 | 0.0049473 | 0.98941 | -0.20287 | 0.98935 | -0.20418 | 1.3592
109 | 0.093077 | 0.023665 | -0.093004 | -0.023619 | 7.2954e-05 | 4.6564e-05 | 0.14031 | 0.14031 | 0.14031 | 0.98797 | -0.22992 | 0.98713 | -0.24621 | 38.5459
110 | 0.08863 | 0.022522 | -0.088535 | -0.022461 | 9.5771e-05 | 6.1111e-05 | 0.13371 | 0.13371 | 0.13371 | 0.98713 | -0.24621 | 0.98596 | -0.26868 | 36.7347
111 | 0.085011 | 0.021578 | -0.084931 | -0.021527 | 7.9708e-05 | 5.0849e-05 | 0.1284 | 0.1284 | 0.1284 | 0.98596 | -0.26868 | 0.98495 | -0.28819 | 35.2736
112 | -0.011342 | -0.0028424 | 0.011342 | 0.0028426 | 4.1561e-07 | 2.2012e-07 | 0.017334 | 0.017334 | 0.017334 | 0.9736 | -0.50987 | 0.97364 | -0.5091 | 4.7621
113 | 0.0053354 | 0.0013371 | -0.0053352 | -0.0013371 | 2.031e-07 | 2.8697e-08 | 0.0081544 | 0.0081544 | 0.0081544 | 0.9736 | -0.50987 | 0.97356 | -0.51067 | 2.2402
114 | -0.025562 | -0.0064067 | 0.025578 | 0.0064161 | 1.5191e-05 | 9.392e-06 | 0.039067 | 0.039067 | 0.039067 | 0.97364 | -0.5091 | 0.97427 | -0.49664 | 10.7327
115 | -0.034791 | -0.0087252 | 0.034827 | 0.0087475 | 3.5478e-05 | 2.2288e-05 | 0.053139 | 0.053139 | 0.053139 | 0.97427 | -0.49664 | 0.97536 | -0.47527 | 14.5986
116 | -0.047615 | -0.011953 | 0.047679 | 0.011993 | 6.3872e-05 | 4.0475e-05 | 0.072649 | 0.072649 | 0.072649 | 0.97536 | -0.47527 | 0.97679 | -0.44718 | 19.9587
117 | -0.064592 | -0.016232 | 0.06476 | 0.016339 | 0.00016782 | 0.00010683 | 0.098413 | 0.098413 | 0.098413 | 0.97679 | -0.44718 | 0.97956 | -0.39291 | 27.0367
118 | 0.077481 | 0.01966 | -0.077397 | -0.019607 | 8.4036e-05 | 5.3575e-05 | 0.11714 | 0.11714 | 0.11714 | 0.98495 | -0.28819 | 0.98378 | -0.31076 | 32.1818
119 | 0.07289 | 0.018477 | -0.072841 | -0.018446 | 4.883e-05 | 3.1116e-05 | 0.11032 | 0.11032 | 0.11032 | 0.98378 | -0.31076 | 0.98306 | -0.32471 | 30.309
120 | 0.064972 | 0.016474 | -0.06476 | -0.016339 | 0.00021222 | 0.00013508 | 0.098413 | 0.098413 | 0.098413 | 0.98306 | -0.32471 | 0.97956 | -0.39291 | 27.0366

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.60416 | 0.1544

## res_load
| p_mw | q_mvar
0 | 0.0022278 | 0.00055835
1 | 0.0058138 | 0.0014571
2 | 0.0028142 | 0.00070531
3 | 0.00048173 | 0.00012073
4 | 0.0062509 | 0.0015666
5 | 0.0033516 | 0.00083999
6 | 0.0037796 | 0.00094726
7 | 0.0043203 | 0.0010828
8 | 0.0057331 | 0.0014368
9 | 0.0044422 | 0.0011133
10 | 0.012631 | 0.0031656
11 | 0.00086191 | 0.00021601
12 | 0.013921 | 0.0034889
13 | 0.014199 | 0.0035587
14 | 0.0043344 | 0.0010863
15 | 0.0029673 | 0.00074368
16 | 0.0048324 | 0.0012111
17 | 0.0038623 | 0.00096797
18 | 0.0041874 | 0.0010495
19 | 0.0031755 | 0.00079587
20 | 0.0032695 | 0.00081942
21 | 0.0020012 | 0.00050156
22 | 0.0034994 | 0.00087703
23 | 0.0038991 | 0.00097721
24 | 0.0052 | 0.0013032
25 | 0.0043228 | 0.0010834
26 | 0.0030879 | 0.0007739
27 | 0.0030557 | 0.00076584
28 | 0.0028307 | 0.00070945
29 | 0.0036069 | 0.00090397
30 | 0.002972 | 0.00074486
31 | 0.0022719 | 0.00056938
32 | 0.0041163 | 0.0010316
33 | 0.0050797 | 0.0012731
34 | 0.00413 | 0.0010351
35 | 0.006331 | 0.0015867
36 | 0.0044521 | 0.0011158
37 | 0.0033594 | 0.00084195
38 | 0.0053124 | 0.0013314
39 | 0.0086277 | 0.0021623
40 | 0.0056151 | 0.0014073
41 | 0.0049767 | 0.0012473
42 | 0.0074882 | 0.0018767
43 | 0.0096021 | 0.0024065
44 | 0.012272 | 0.0030756
45 | 0.0053196 | 0.0013332
46 | 0.012195 | 0.0030563
47 | 0.006679 | 0.0016739
48 | 0.013557 | 0.0033976
49 | 0.010456 | 0.0026205
50 | 0.0070767 | 0.0017736
51 | 0.0029742 | 0.00074542
52 | 0.0036315 | 0.00091013
53 | 0.0057962 | 0.0014527
54 | 0.0050383 | 0.0012627
55 | 0.0033749 | 0.00084582
56 | 0.0080631 | 0.0020208
57 | 0.0051588 | 0.0012929
58 | 0.0042139 | 0.0010561
59 | 0.0079102 | 0.0019825
60 | 0.0056754 | 0.0014224
61 | 0.004351 | 0.0010905
62 | 0.0095346 | 0.0023896
63 | 0.0035494 | 0.00088956
64 | 0.0053136 | 0.0013317
65 | 0.0039749 | 0.0009962
66 | 0.0048088 | 0.0012052
67 | 0.0069022 | 0.0017299
68 | 0.0048 | 0.001203
69 | 0.0042825 | 0.0010733
70 | 0.011034 | 0.0027654
71 | 0.0023361 | 0.00058549
72 | 0.010005 | 0.0025076
73 | 0.0075628 | 0.0018954
74 | 0.0043134 | 0.001081
75 | 0.0010153 | 0.00025445
76 | 0.0077543 | 0.0019434
77 | 0.0064826 | 0.0016247
78 | 0.0049931 | 0.0012514
79 | 0.0035804 | 0.00089732
80 | 0.0068468 | 0.001716
81 | 0.0033763 | 0.00084619
82 | 0.0030067 | 0.00075355
83 | 0.0031521 | 0.00078998
84 | 0.0052779 | 0.0013228
85 | 0.0054982 | 0.001378
86 | 0.0097087 | 0.0024332
87 | 0.0090227 | 0.0022613
88 | 0.0032583 | 0.00081661
89 | 0.0034969 | 0.00087641
90 | 0.0062097 | 0.0015563
91 | 0.0043735 | 0.0010961
92 | 0.003524 | 0.0008832
93 | 0.0060061 | 0.0015053
94 | 0.014221 | 0.003564
95 | 0.0053352 | 0.0013371
96 | 0.0092135 | 0.0023091
97 | 0.012789 | 0.0032052
98 | 0.016912 | 0.0042387
99 | 0.0074496 | 0.001867
100 | 0.004507 | 0.0011296
101 | 0.0078696 | 0.0019723
102 | 0.0032893 | 0.00082439

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1