## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-28_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-28_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-28_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1711-28_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1711-28_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1711-28_0_5_node_27 | 0.4 | n |  | TRUE
6 | bus_LV_1711-28_0_5_node_35 | 0.4 | n |  | TRUE
7 | bus_LV_1711-28_0_5_node_22 | 0.4 | n |  | TRUE
8 | bus_LV_1711-28_0_5_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_1711-28_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_1711-28_0_5_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1711-28_0_5_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_1711-28_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1711-28_0_5_node_34 | 0.4 | n |  | TRUE
14 | bus_LV_1711-28_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_1711-28_0_5_node_21 | 0.4 | n |  | TRUE
16 | bus_LV_1711-28_0_5_node_18 | 0.4 | n |  | TRUE
17 | bus_LV_1711-28_0_5_node_29 | 0.4 | n |  | TRUE
18 | bus_LV_1711-28_0_5_node_28 | 0.4 | n |  | TRUE
19 | bus_LV_1711-28_0_5_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_1711-28_0_5_node_23 | 0.4 | n |  | TRUE
21 | bus_LV_1711-28_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1711-28_0_5_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_1711-28_0_5_node_30 | 0.4 | n |  | TRUE
24 | bus_LV_1711-28_0_5_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_1711-28_0_5_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1711-28_0_5_node_11 | 0.4 | n |  | TRUE
27 | bus_LV_1711-28_0_5_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_1711-28_0_5_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_1711-28_0_5_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_1711-28_0_5_node_31 | 0.4 | n |  | TRUE
31 | bus_LV_1711-28_0_5_node_36 | 0.4 | n |  | TRUE
32 | bus_LV_1711-28_0_5_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_1711-28_0_5_node_32 | 0.4 | n |  | TRUE
34 | bus_MV_229_0_node_13 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-28_0_5_load_0 | 0 | 0.013283 | 0.0033291 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-28_0_5_load_1 | 1 | 0.017333 | 0.004344 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-28_0_5_load_4 | 4 | 0.015406 | 0.003861 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-28_0_5_load_35 | 6 | 0.013622 | 0.003414 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-28_0_5_load_22 | 7 | 0.090072 | 0.022574 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-28_0_5_load_17 | 11 | 0.015479 | 0.0038794 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-28_0_5_load_34 | 13 | 0.011058 | 0.0027714 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-28_0_5_load_21 | 15 | 0.0077509 | 0.0019426 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-28_0_5_load_18 | 16 | 0.017596 | 0.0044099 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-28_0_5_load_29 | 17 | 0.010585 | 0.0026528 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-28_0_5_load_28 | 18 | 0.0055598 | 0.0013934 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-28_0_5_load_25 | 19 | 0.053376 | 0.013377 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-28_0_5_load_23 | 20 | 0.0083574 | 0.0020946 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-28_0_5_load_30 | 23 | 0.0042536 | 0.0010661 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-28_0_5_load_11 | 26 | 0.011532 | 0.0028901 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-28_0_5_load_24 | 28 | 0.035143 | 0.0088077 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-28_0_5_load_31 | 30 | 0.0029742 | 0.00074541 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-28_0_5_load_36 | 31 | 0.016797 | 0.0042097 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-28_0_5_load_26 | 32 | 0.06197 | 0.015531 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-28_0_5_load_32 | 33 | 0.021801 | 0.0054638 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 19 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-28_0_5_line_0 |  | 0 | 1 | 0.0046728 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_1711-28_0_5_line_1 |  | 0 | 2 | 0.024659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_1711-28_0_5_line_2 |  | 1 | 3 | 0.036235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_1711-28_0_5_line_3 |  | 2 | 4 | 0.051981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_1711-28_0_5_line_4 |  | 3 | 5 | 0.064066 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1711-28_0_5_line_5 |  | 3 | 6 | 0.018121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1711-28_0_5_line_6 |  | 4 | 7 | 0.056597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_1711-28_0_5_line_7 |  | 5 | 18 | 0.027616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-28_0_5_line_8 |  | 5 | 19 | 0.069306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1711-28_0_5_line_9 |  | 6 | 13 | 0.021973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-28_0_5_line_10 |  | 7 | 20 | 0.077317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1711-28_0_5_line_11 |  | 8 | 9 | 0.090184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-28_0_5_line_12 |  | 8 | 10 | 0.1321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-28_0_5_line_13 |  | 8 | 11 | 0.030529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-28_0_5_line_14 |  | 9 | 12 | 0.04999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-28_0_5_line_15 |  | 9 | 13 | 0.033454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-28_0_5_line_16 |  | 10 | 17 | 0.025866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-28_0_5_line_17 |  | 11 | 21 | 0.047935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-28_0_5_line_18 |  | 12 | 15 | 0.14599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-28_0_5_line_19 |  | 14 | 15 | 0.01255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-28_0_5_line_20 |  | 14 | 16 | 0.0070325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-28_0_5_line_21 |  | 19 | 32 | 0.043041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-28_0_5_line_22 |  | 20 | 28 | 0.03633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_1711-28_0_5_line_23 |  | 21 | 26 | 0.0187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1711-28_0_5_line_24 |  | 22 | 23 | 0.002328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-28_0_5_line_25 |  | 22 | 24 | 0.19287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-28_0_5_line_26 |  | 23 | 30 | 0.049403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1711-28_0_5_line_27 |  | 24 | 25 | 0.042199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_1711-28_0_5_line_28 |  | 25 | 27 | 0.092746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1711-28_0_5_line_29 |  | 25 | 28 | 0.062707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_1711-28_0_5_line_30 |  | 27 | 29 | 0.19187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1711-28_0_5_line_31 |  | 29 | 31 | 0.052787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-28_0_5_line_32 |  | 30 | 33 | 0.023893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-28_0_5_trafo_25 | 0.63 MVA 20/0.4 kV | 34 | 19 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2681019.0536 | 1225268.8216 | 2681020.6668 | 1225273.2072
1 | 2681010.5409 | 1225245.6783 | 2681019.0536 | 1225268.8216
2 | 2681014.0781 | 1225298.8179 | 2681027.9851 | 1225293.1033 | 2681020.6668 | 1225273.2072
3 | 2681010.5409 | 1225245.6783 | 2681058.1163 | 1225224.7356
4 | 2681014.0781 | 1225298.8179 | 2681019.0386 | 1225315.3743 | 2681030.9736 | 1225309.1437 | 2681037.8087 | 1225309.4147 | 2681051.6428 | 1225303.4768 | 2681060.6837 | 1225310.4602
5 | 2681014.0781 | 1225298.8179 | 2680997.5236 | 1225306.1878
6 | 2681058.1163 | 1225224.7356 | 2681064.7347 | 1225221.8221 | 2681109.9098 | 1225201.919
7 | 2681036.4375 | 1225323.8058 | 2681060.6837 | 1225310.4602
8 | 2681060.6837 | 1225310.4602 | 2681105.0208 | 1225286.0476 | 2681119.0711 | 1225273.7196
9 | 2680977.4497 | 1225315.1244 | 2680997.5236 | 1225306.1878
10 | 2681109.9098 | 1225201.919 | 2681130.9505 | 1225192.649 | 2681162.4045 | 1225181.7704 | 2681181.607 | 1225173.1651
11 | 2680931.6507 | 1225266.4081 | 2680937.0199 | 1225278.0111 | 2680940.2975 | 1225285.0938 | 2680935.7066 | 1225288.7227 | 2680931.2002 | 1225310.1092 | 2680930.3243 | 1225334.3693 | 2680938.163 | 1225332.7525 | 2680946.9205 | 1225328.8023
12 | 2680893.8888 | 1225202.6295 | 2680868.9348 | 1225213.3866 | 2680894.8542 | 1225261.5491 | 2680897.9898 | 1225267.9182 | 2680904.0921 | 1225279.142 | 2680923.7386 | 1225270.0696 | 2680931.6507 | 1225266.4081
13 | 2680931.6507 | 1225266.4081 | 2680959.131 | 1225253.109
14 | 2680944.5346 | 1225350.9181 | 2680931.3778 | 1225353.3409 | 2680930.3243 | 1225334.3693 | 2680938.163 | 1225332.7525 | 2680946.9205 | 1225328.8023
15 | 2680946.9205 | 1225328.8023 | 2680952.3299 | 1225326.3075 | 2680977.4497 | 1225315.1244
16 | 2680893.8888 | 1225202.6295 | 2680883.775 | 1225178.8228
17 | 2681003.9919 | 1225238.3175 | 2680972.4938 | 1225251.9204 | 2680966.0767 | 1225251.5773 | 2680961.1257 | 1225252.1437 | 2680959.131 | 1225253.109
18 | 2680944.5346 | 1225350.9181 | 2680951.1778 | 1225354.6999 | 2680968.7131 | 1225359.2304 | 2680999.691 | 1225369.3142 | 2681062.2097 | 1225394.8714 | 2681077.7274 | 1225407.6747
19 | 2681087.4081 | 1225415.662 | 2681077.7274 | 1225407.6747
20 | 2681087.4081 | 1225415.662 | 2681092.4088 | 1225420.6066
21 | 2681158.7137 | 1225256.9577 | 2681119.0711 | 1225273.7196
22 | 2681214.2777 | 1225157.3088 | 2681197.0763 | 1225166.2327 | 2681181.607 | 1225173.1651
23 | 2681003.9919 | 1225238.3175 | 2681021.161 | 1225230.9064
24 | 2681087.4264 | 1225095.0567 | 2681085.1091 | 1225094.8329
25 | 2681087.4264 | 1225095.0567 | 2681109.9758 | 1225097.2431 | 2681132.3277 | 1225096.1136 | 2681149.6925 | 1225093.1928 | 2681152.9469 | 1225101.3982 | 2681206.5518 | 1225080.8376 | 2681209.7703 | 1225097.2259 | 2681215.6273 | 1225110.8372 | 2681226.1561 | 1225128.2371 | 2681235.5053 | 1225135.9699
26 | 2681085.1091 | 1225094.8329 | 2681074.2889 | 1225093.788 | 2681035.9034 | 1225097.1503
27 | 2681235.5053 | 1225135.9699 | 2681265.2371 | 1225121.3213 | 2681270.1831 | 1225128.9051
28 | 2681270.1831 | 1225128.9051 | 2681275.3654 | 1225136.948 | 2681298.1376 | 1225181.0665 | 2681300.6049 | 1225186.9375 | 2681301.4694 | 1225192.4753 | 2681302.9724 | 1225206.7611 | 2681303.9213 | 1225213.8899
29 | 2681270.1831 | 1225128.9051 | 2681216.2045 | 1225156.3092 | 2681214.2777 | 1225157.3088
30 | 2681265.4801 | 1225346.6215 | 2681261.7946 | 1225342.7908 | 2681249.3 | 1225331.6905 | 2681238.0822 | 1225302.5955 | 2681267.4955 | 1225291.2226 | 2681302.8448 | 1225277.6739 | 2681310.3293 | 1225274.8076 | 2681303.9213 | 1225213.8899
31 | 2681265.4801 | 1225346.6215 | 2681254.0933 | 1225347.1108 | 2681238.4255 | 1225344.6286 | 2681234.037 | 1225341.7557 | 2681226.9486 | 1225340.0578 | 2681222.638 | 1225341.4777 | 2681214.4446 | 1225344.0788
32 | 2681012.0962 | 1225099.1782 | 2681029.031 | 1225097.7522 | 2681035.9034 | 1225097.1503

## bus_geodata
| x | y | coords
0 | 2681019.0536 | 1225268.8216
1 | 2681020.6668 | 1225273.2072
2 | 2681010.5409 | 1225245.6783
3 | 2681014.0781 | 1225298.8179
4 | 2681058.1163 | 1225224.7356
5 | 2681060.6837 | 1225310.4602
6 | 2680997.5236 | 1225306.1878
7 | 2681109.9098 | 1225201.919
8 | 2680931.6507 | 1225266.4081
9 | 2680946.9205 | 1225328.8023
10 | 2680893.8888 | 1225202.6295
11 | 2680959.131 | 1225253.109
12 | 2680944.5346 | 1225350.9181
13 | 2680977.4497 | 1225315.1244
14 | 2681087.4081 | 1225415.662
15 | 2681077.7274 | 1225407.6747
16 | 2681092.4088 | 1225420.6066
17 | 2680883.775 | 1225178.8228
18 | 2681036.4375 | 1225323.8058
19 | 2681119.0711 | 1225273.7196
20 | 2681181.607 | 1225173.1651
21 | 2681003.9919 | 1225238.3175
22 | 2681087.4264 | 1225095.0567
23 | 2681085.1091 | 1225094.8329
24 | 2681235.5053 | 1225135.9699
25 | 2681270.1831 | 1225128.9051
26 | 2681021.161 | 1225230.9064
27 | 2681303.9213 | 1225213.8899
28 | 2681214.2777 | 1225157.3088
29 | 2681265.4801 | 1225346.6215
30 | 2681035.9034 | 1225097.1503
31 | 2681214.4446 | 1225344.0788
32 | 2681158.7137 | 1225256.9577
33 | 2681012.0962 | 1225099.1782
34 | 2681146.9055 | 1225261.9505

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98814 | -0.22618 | 0.013283 | 0.0033291
1 | 0.98837 | -0.22184 | 0.017333 | 0.004344
2 | 0.98703 | -0.24765 | 0 | 0
3 | 0.99026 | -0.18547 | 0 | 0
4 | 0.98469 | -0.29306 | 0.015406 | 0.003861
5 | 0.99489 | -0.096739 | 0 | 0
6 | 0.98879 | -0.21374 | 0.013622 | 0.003414
7 | 0.98234 | -0.33881 | 0.090072 | 0.022574
8 | 0.98221 | -0.34159 | 0 | 0
9 | 0.98534 | -0.28051 | 0 | 0
10 | 0.98092 | -0.36689 | 0 | 0
11 | 0.98145 | -0.3565 | 0.015479 | 0.0038794
12 | 0.98417 | -0.30329 | 0 | 0
13 | 0.98729 | -0.24277 | 0.011058 | 0.0027714
14 | 0.98054 | -0.37412 | 0 | 0
15 | 0.98075 | -0.37012 | 0.0077509 | 0.0019426
16 | 0.98043 | -0.37636 | 0.017596 | 0.0044099
17 | 0.98066 | -0.37185 | 0.010585 | 0.0026528
18 | 0.99475 | -0.099444 | 0.0055598 | 0.0013934
19 | 1 | 0 | -0.38779 | -0.098902
20 | 0.98073 | -0.37006 | 0.0083574 | 0.0020946
21 | 0.98093 | -0.36651 | 0 | 0
22 | 0.97359 | -0.51001 | 0 | 0
23 | 0.97352 | -0.51126 | 0.0042536 | 0.0010661
24 | 0.97881 | -0.40759 | 0 | 0
25 | 0.97938 | -0.39645 | 0 | 0
26 | 0.98074 | -0.37041 | 0.011532 | 0.0028901
27 | 0.97793 | -0.42482 | 0 | 0
28 | 0.98005 | -0.3834 | 0.035143 | 0.0088077
29 | 0.97493 | -0.48375 | 0 | 0
30 | 0.97238 | -0.53379 | 0.0029742 | 0.00074541
31 | 0.9741 | -0.50003 | 0.016797 | 0.0042097
32 | 0.99758 | -0.046602 | 0.06197 | 0.015531
33 | 0.97189 | -0.5434 | 0.021801 | 0.0054638
34 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.2096 | -0.053099 | 0.20965 | 0.053126 | 4.37e-05 | 2.7729e-05 | 0.31584 | 0.31584 | 0.31584 | 0.98814 | -0.22618 | 0.98837 | -0.22184 | 21.6923
1 | 0.19632 | 0.04977 | -0.19612 | -0.049641 | 0.00020233 | 0.00012823 | 0.29584 | 0.29584 | 0.29584 | 0.98814 | -0.22618 | 0.98703 | -0.24765 | 20.3185
2 | -0.22698 | -0.05747 | 0.22738 | 0.057723 | 0.00039717 | 0.00025233 | 0.34193 | 0.34193 | 0.34193 | 0.98837 | -0.22184 | 0.99026 | -0.18547 | 23.4845
3 | 0.19612 | 0.049641 | -0.19569 | -0.049371 | 0.00042651 | 0.00027031 | 0.29584 | 0.29584 | 0.29584 | 0.98703 | -0.24765 | 0.98469 | -0.29306 | 20.3186
4 | -0.3156 | -0.080061 | 0.31696 | 0.080924 | 0.0013528 | 0.00086248 | 0.47459 | 0.47459 | 0.47459 | 0.99026 | -0.18547 | 0.99489 | -0.096739 | 32.5953
5 | 0.088226 | 0.022338 | -0.088106 | -0.022262 | 0.00011958 | 7.6297e-05 | 0.13265 | 0.13265 | 0.13265 | 0.99026 | -0.18547 | 0.98879 | -0.21374 | 36.4433
6 | 0.18029 | 0.04551 | -0.17989 | -0.045261 | 0.00039417 | 0.0002494 | 0.27256 | 0.27256 | 0.27256 | 0.98469 | -0.29306 | 0.98234 | -0.33881 | 18.7198
7 | 0.0055605 | 0.0013935 | -0.0055598 | -0.0013934 | 7.163e-07 | 9.9868e-08 | 0.0083166 | 0.0083167 | 0.0083167 | 0.99489 | -0.096739 | 0.99475 | -0.099444 | 2.2848
8 | -0.32252 | -0.082317 | 0.32403 | 0.083283 | 0.0015152 | 0.00096609 | 0.4829 | 0.4829 | 0.4829 | 0.99489 | -0.096739 | 1 | 0 | 33.1664
9 | 0.074484 | 0.018848 | -0.07438 | -0.018782 | 0.00010365 | 6.6053e-05 | 0.11215 | 0.11215 | 0.11215 | 0.98879 | -0.21374 | 0.98729 | -0.24277 | 30.8116
10 | 0.089821 | 0.022687 | -0.089687 | -0.022605 | 0.00013431 | 8.2048e-05 | 0.13612 | 0.13612 | 0.13612 | 0.98234 | -0.33881 | 0.98073 | -0.37006 | 9.3491
11 | -0.037637 | -0.009446 | 0.037747 | 0.0095152 | 0.00010997 | 6.9236e-05 | 0.057024 | 0.057024 | 0.057024 | 0.98221 | -0.34159 | 0.98534 | -0.28051 | 15.666
12 | 0.0106 | 0.0026605 | -0.010587 | -0.002654 | 1.2777e-05 | 6.5078e-06 | 0.01606 | 0.016061 | 0.016061 | 0.98221 | -0.34159 | 0.98092 | -0.36689 | 4.4122
13 | 0.027037 | 0.0067854 | -0.027018 | -0.0067735 | 1.9211e-05 | 1.1909e-05 | 0.040964 | 0.040964 | 0.040964 | 0.98221 | -0.34159 | 0.98145 | -0.3565 | 11.2539
14 | 0.025461 | 0.0064227 | -0.025433 | -0.0064056 | 2.7735e-05 | 1.7114e-05 | 0.038464 | 0.038464 | 0.038464 | 0.98534 | -0.28051 | 0.98417 | -0.30329 | 10.5672
15 | -0.063208 | -0.015938 | 0.063322 | 0.016011 | 0.00011439 | 7.278e-05 | 0.095488 | 0.095488 | 0.095488 | 0.98534 | -0.28051 | 0.98729 | -0.24277 | 26.2329
16 | 0.010587 | 0.002654 | -0.010585 | -0.0026528 | 2.502e-06 | 1.2748e-06 | 0.016061 | 0.016061 | 0.016061 | 0.98092 | -0.36689 | 0.98066 | -0.37185 | 4.4123
17 | 0.011539 | 0.0028942 | -0.011534 | -0.0028912 | 5.5026e-06 | 2.9163e-06 | 0.017496 | 0.017496 | 0.017496 | 0.98145 | -0.3565 | 0.98093 | -0.36651 | 4.8067
18 | 0.025433 | 0.0064056 | -0.025352 | -0.0063556 | 8.1e-05 | 4.9991e-05 | 0.038464 | 0.038465 | 0.038465 | 0.98417 | -0.30329 | 0.98075 | -0.37012 | 10.5673
19 | -0.017598 | -0.004411 | 0.017601 | 0.004413 | 3.3565e-06 | 1.9898e-06 | 0.026705 | 0.026705 | 0.026705 | 0.98054 | -0.37412 | 0.98075 | -0.37012 | 7.3366
20 | 0.017598 | 0.004411 | -0.017596 | -0.0044099 | 1.8808e-06 | 1.115e-06 | 0.026705 | 0.026705 | 0.026705 | 0.98054 | -0.37412 | 0.98043 | -0.37636 | 7.3366
21 | 0.062108 | 0.015619 | -0.06197 | -0.015531 | 0.00013791 | 8.77e-05 | 0.092437 | 0.092437 | 0.092437 | 1 | 0 | 0.99758 | -0.046602 | 25.3948
22 | 0.081329 | 0.02051 | -0.081278 | -0.020479 | 5.19e-05 | 3.1384e-05 | 0.12344 | 0.12344 | 0.12344 | 0.98073 | -0.37006 | 0.98005 | -0.3834 | 8.4782
23 | 0.011534 | 0.0028912 | -0.011532 | -0.0028901 | 2.1467e-06 | 1.1379e-06 | 0.017496 | 0.017496 | 0.017496 | 0.98093 | -0.36651 | 0.98074 | -0.37041 | 4.8067
24 | 0.029067 | 0.0072989 | -0.029065 | -0.0072978 | 1.7234e-06 | 1.074e-06 | 0.044431 | 0.044431 | 0.044431 | 0.97359 | -0.51001 | 0.97352 | -0.51126 | 12.2062
25 | -0.029067 | -0.0072989 | 0.02921 | 0.0073878 | 0.00014278 | 8.8967e-05 | 0.044431 | 0.04443 | 0.044431 | 0.97359 | -0.51001 | 0.97881 | -0.40759 | 12.2062
26 | 0.024812 | 0.0062317 | -0.024785 | -0.0062153 | 2.6652e-05 | 1.6444e-05 | 0.037929 | 0.037929 | 0.037929 | 0.97352 | -0.51126 | 0.97238 | -0.53379 | 10.4201
27 | -0.02921 | -0.0073878 | 0.029225 | 0.0073968 | 1.5619e-05 | 8.9345e-06 | 0.04443 | 0.044429 | 0.04443 | 0.97881 | -0.40759 | 0.97938 | -0.39645 | 6.103
28 | 0.01688 | 0.0042588 | -0.016857 | -0.0042453 | 2.2895e-05 | 1.3488e-05 | 0.025657 | 0.025657 | 0.025657 | 0.97938 | -0.39645 | 0.97793 | -0.42482 | 7.0487
29 | -0.046106 | -0.011656 | 0.046134 | 0.011671 | 2.8877e-05 | 1.5323e-05 | 0.070086 | 0.070085 | 0.070086 | 0.97938 | -0.39645 | 0.98005 | -0.3834 | 4.8136
30 | 0.016857 | 0.0042453 | -0.01681 | -0.0042174 | 4.7368e-05 | 2.7915e-05 | 0.025657 | 0.025658 | 0.025658 | 0.97793 | -0.42482 | 0.97493 | -0.48375 | 7.049
31 | 0.01681 | 0.0042174 | -0.016797 | -0.0042097 | 1.3032e-05 | 7.6829e-06 | 0.025658 | 0.025659 | 0.025659 | 0.97493 | -0.48375 | 0.9741 | -0.50003 | 7.049
32 | 0.021811 | 0.0054699 | -0.021801 | -0.0054638 | 9.9822e-06 | 6.0924e-06 | 0.033378 | 0.033378 | 0.033378 | 0.97238 | -0.53379 | 0.97189 | -0.5434 | 9.1698

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.44117 | 0.11228

## res_load
| p_mw | q_mvar
0 | 0.013283 | 0.0033291
1 | 0.017333 | 0.004344
2 | 0.015406 | 0.003861
3 | 0.013622 | 0.003414
4 | 0.090072 | 0.022574
5 | 0.015479 | 0.0038794
6 | 0.011058 | 0.0027714
7 | 0.0077509 | 0.0019426
8 | 0.017596 | 0.0044099
9 | 0.010585 | 0.0026528
10 | 0.0055598 | 0.0013934
11 | 0.053376 | 0.013377
12 | 0.0083574 | 0.0020946
13 | 0.0042536 | 0.0010661
14 | 0.011532 | 0.0028901
15 | 0.035143 | 0.0088077
16 | 0.0029742 | 0.00074541
17 | 0.016797 | 0.0042097
18 | 0.06197 | 0.015531
19 | 0.021801 | 0.0054638

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1