## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1711-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1711-2_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_1711-2_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_1711-2_0_4_node_14 | 0.4 | n |  | TRUE
7 | bus_LV_1711-2_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_1711-2_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_1711-2_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1711-2_0_4_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_1711-2_0_4_node_16 | 0.4 | n |  | TRUE
12 | bus_LV_1711-2_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_1711-2_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_1711-2_0_4_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_1711-2_0_4_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_1711-2_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1711-2_0_4_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_1711-2_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_1711-2_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_1711-2_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_1711-2_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_1711-2_0_4_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_1711-2_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_1711-2_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_1711-2_0_4_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_1711-2_0_4_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_1711-2_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_1711-2_0_4_node_25 | 0.4 | n |  | TRUE
29 | bus_MV_230_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-2_0_4_load_0 | 0 | 0.050465 | 0.012648 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-2_0_4_load_14 | 6 | 0.040133 | 0.010058 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-2_0_4_load_11 | 8 | 0.0080144 | 0.0020086 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-2_0_4_load_16 | 11 | 0.088168 | 0.022097 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-2_0_4_load_28 | 12 | 0.0052329 | 0.0013115 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-2_0_4_load_30 | 14 | 0.0078834 | 0.0019758 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-2_0_4_load_17 | 16 | 0.022366 | 0.0056055 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-2_0_4_load_22 | 17 | 0.043921 | 0.011008 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-2_0_4_load_18 | 18 | 0.061439 | 0.015398 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-2_0_4_load_12 | 19 | 0.008011 | 0.0020077 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-2_0_4_load_13 | 21 | 0.0080023 | 0.0020056 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-2_0_4_load_29 | 22 | 0.0079931 | 0.0020033 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-2_0_4_load_21 | 24 | 0.032522 | 0.0081507 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-2_0_4_load_20 | 25 | 0.052908 | 0.01326 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-2_0_4_load_26 | 26 | 0.05291 | 0.01326 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-2_0_4_load_25 | 28 | 0.032534 | 0.0081538 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-2_0_4_line_0 |  | 0 | 1 | 0.047498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-2_0_4_line_1 |  | 0 | 2 | 0.0046922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-2_0_4_line_2 |  | 1 | 3 | 0.044904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-2_0_4_line_3 |  | 2 | 4 | 0.055927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-2_0_4_line_4 |  | 3 | 5 | 0.077821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_1711-2_0_4_line_5 |  | 3 | 6 | 0.025592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1711-2_0_4_line_6 |  | 4 | 14 | 0.073268 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-2_0_4_line_7 |  | 5 | 17 | 0.021732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-2_0_4_line_8 |  | 5 | 18 | 0.042936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_1711-2_0_4_line_9 |  | 5 | 7 | 0.040276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_1711-2_0_4_line_10 |  | 6 | 13 | 0.021848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1711-2_0_4_line_11 |  | 7 | 8 | 0.01061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_1711-2_0_4_line_12 |  | 8 | 19 | 0.016601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_1711-2_0_4_line_13 |  | 9 | 10 | 0.040233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_1711-2_0_4_line_14 |  | 9 | 11 | 0.029153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_1711-2_0_4_line_15 |  | 9 | 12 | 0.081468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-2_0_4_line_16 |  | 10 | 16 | 0.028151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_1711-2_0_4_line_17 |  | 11 | 13 | 0.021354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_1711-2_0_4_line_18 |  | 15 | 16 | 0.0225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_1711-2_0_4_line_19 |  | 18 | 20 | 0.030555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_1711-2_0_4_line_20 |  | 19 | 21 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_1711-2_0_4_line_21 |  | 20 | 25 | 0.019277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_1711-2_0_4_line_22 |  | 20 | 24 | 0.036029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_1711-2_0_4_line_23 |  | 21 | 22 | 0.016598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_1711-2_0_4_line_24 |  | 22 | 23 | 0.014643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-2_0_4_line_25 |  | 23 | 27 | 0.037449 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-2_0_4_line_26 |  | 25 | 26 | 0.008861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1711-2_0_4_line_27 |  | 27 | 28 | 0.023073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-2_0_4_trafo_8 | 0.63 MVA 20/0.4 kV | 29 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2681909.5446 | 1226170.2639 | 2681924.4376 | 1226167.1778 | 2681955.9724 | 1226160.244
1 | 2681960.5552 | 1226159.2364 | 2681955.9724 | 1226160.244
2 | 2681872.9749 | 1226184.626 | 2681871.7395 | 1226178.5493 | 2681878.0662 | 1226177.1243 | 2681894.8242 | 1226173.4746 | 2681898.1931 | 1226172.6982 | 2681909.5446 | 1226170.2639
3 | 2682015.3935 | 1226148.2621 | 2682004.3935 | 1226150.4898 | 2681979.7899 | 1226155.1985 | 2681960.5552 | 1226159.2364
4 | 2681872.9749 | 1226184.626 | 2681878.5427 | 1226227.3094 | 2681881.4414 | 1226234.8099 | 2681887.0018 | 1226260.9598
5 | 2681872.9749 | 1226184.626 | 2681847.9935 | 1226190.1844
6 | 2682029.4798 | 1226220.1607 | 2682015.3935 | 1226148.2621
7 | 2681887.0018 | 1226260.9598 | 2681891.8136 | 1226282.1524
8 | 2681887.0018 | 1226260.9598 | 2681858.5195 | 1226266.6274 | 2681844.9054 | 1226269.4083
9 | 2681887.0018 | 1226260.9598 | 2681896.0822 | 1226258.8388 | 2681911.632 | 1226255.3838 | 2681918.559 | 1226253.8447 | 2681926.4488 | 1226252.3079
10 | 2681826.667 | 1226194.9295 | 2681847.9935 | 1226190.1844
11 | 2681926.4488 | 1226252.3079 | 2681928.684 | 1226262.6802
12 | 2681928.684 | 1226262.6802 | 2681932.1813 | 1226278.9091
13 | 2681786.159 | 1226245.9963 | 2681777.5496 | 1226206.6958
14 | 2681777.5496 | 1226206.6958 | 2681805.9001 | 1226199.9043
15 | 2681777.5496 | 1226206.6958 | 2681704.4338 | 1226242.6271
16 | 2681786.159 | 1226245.9963 | 2681813.7554 | 1226240.4374
17 | 2681826.667 | 1226194.9295 | 2681805.9001 | 1226199.9043
18 | 2681835.8128 | 1226235.9943 | 2681813.7554 | 1226240.4374
19 | 2681814.9683 | 1226275.5235 | 2681844.9054 | 1226269.4083
20 | 2681935.6781 | 1226295.1358 | 2681932.1813 | 1226278.9091
21 | 2681814.9683 | 1226275.5235 | 2681796.0501 | 1226279.2242
22 | 2681821.8044 | 1226310.897 | 2681817.4524 | 1226288.3663 | 2681814.9683 | 1226275.5235
23 | 2681939.1745 | 1226311.3609 | 2681935.6781 | 1226295.1358
24 | 2681942.2593 | 1226325.6754 | 2681939.1745 | 1226311.3609
25 | 2681905.3811 | 1226332.7726 | 2681942.2593 | 1226325.6754
26 | 2681787.354 | 1226280.9254 | 2681796.0501 | 1226279.2242
27 | 2681905.3811 | 1226332.7726 | 2681882.7414 | 1226337.2226

## bus_geodata
| x | y | coords
0 | 2681955.9724 | 1226160.244
1 | 2681909.5446 | 1226170.2639
2 | 2681960.5552 | 1226159.2364
3 | 2681872.9749 | 1226184.626
4 | 2682015.3935 | 1226148.2621
5 | 2681887.0018 | 1226260.9598
6 | 2681847.9935 | 1226190.1844
7 | 2681926.4488 | 1226252.3079
8 | 2681928.684 | 1226262.6802
9 | 2681777.5496 | 1226206.6958
10 | 2681786.159 | 1226245.9963
11 | 2681805.9001 | 1226199.9043
12 | 2681704.4338 | 1226242.6271
13 | 2681826.667 | 1226194.9295
14 | 2682029.4798 | 1226220.1607
15 | 2681835.8128 | 1226235.9943
16 | 2681813.7554 | 1226240.4374
17 | 2681891.8136 | 1226282.1524
18 | 2681844.9054 | 1226269.4083
19 | 2681932.1813 | 1226278.9091
20 | 2681814.9683 | 1226275.5235
21 | 2681935.6781 | 1226295.1358
22 | 2681939.1745 | 1226311.3609
23 | 2681942.2593 | 1226325.6754
24 | 2681821.8044 | 1226310.897
25 | 2681796.0501 | 1226279.2242
26 | 2681787.354 | 1226280.9254
27 | 2681905.3811 | 1226332.7726
28 | 2681882.7414 | 1226337.2226
29 | 2681826.667 | 1226194.9295

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97464 | -0.48695 | 0.050465 | 0.012648
1 | 0.97722 | -0.43623 | 0 | 0
2 | 0.9746 | -0.48763 | 0 | 0
3 | 0.97965 | -0.38852 | 0 | 0
4 | 0.97419 | -0.49572 | 0 | 0
5 | 0.97405 | -0.49807 | 0 | 0
6 | 0.98184 | -0.34601 | 0.040133 | 0.010058
7 | 0.97345 | -0.51002 | 0 | 0
8 | 0.97329 | -0.51317 | 0.0080144 | 0.0020086
9 | 0.9893 | -0.20245 | 0 | 0
10 | 0.99398 | -0.11327 | 0 | 0
11 | 0.98594 | -0.26691 | 0.088168 | 0.022097
12 | 0.98891 | -0.21004 | 0.0052329 | 0.0013115
13 | 0.98392 | -0.30593 | 0 | 0
14 | 0.97365 | -0.50634 | 0.0078834 | 0.0019758
15 | 1 | 0 | -0.53579 | -0.13837
16 | 0.99726 | -0.051375 | 0.022366 | 0.0056055
17 | 0.97316 | -0.51562 | 0.043921 | 0.011008
18 | 0.97205 | -0.53755 | 0.061439 | 0.015398
19 | 0.97307 | -0.51749 | 0.008011 | 0.0020077
20 | 0.97106 | -0.55706 | 0 | 0
21 | 0.97288 | -0.5212 | 0.0080023 | 0.0020056
22 | 0.97257 | -0.5274 | 0.0079931 | 0.0020033
23 | 0.97212 | -0.53618 | 0 | 0
24 | 0.97052 | -0.5679 | 0.032522 | 0.0081507
25 | 0.97059 | -0.56649 | 0.052908 | 0.01326
26 | 0.97015 | -0.57517 | 0.05291 | 0.01326
27 | 0.97098 | -0.55868 | 0 | 0
28 | 0.97028 | -0.57256 | 0.032534 | 0.0081538
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.058355 | -0.014626 | 0.058497 | 0.014716 | 0.00014138 | 8.9891e-05 | 0.089094 | 0.089094 | 0.089094 | 0.97464 | -0.48695 | 0.97722 | -0.43623 | 24.4763
1 | 0.0078907 | 0.0019788 | -0.0078904 | -0.0019787 | 2.5539e-07 | 1.0497e-07 | 0.012047 | 0.012047 | 0.012047 | 0.97464 | -0.48695 | 0.9746 | -0.48763 | 3.3097
2 | -0.058497 | -0.014716 | 0.05863 | 0.014801 | 0.00013366 | 8.4979e-05 | 0.089094 | 0.089093 | 0.089094 | 0.97722 | -0.43623 | 0.97965 | -0.38852 | 24.4762
3 | 0.0078904 | 0.0019787 | -0.0078874 | -0.0019774 | 3.0441e-06 | 1.2516e-06 | 0.012047 | 0.012048 | 0.012048 | 0.9746 | -0.48763 | 0.97419 | -0.49572 | 3.3098
4 | 0.31066 | 0.07878 | -0.30903 | -0.077743 | 0.0016267 | 0.0010372 | 0.4722 | 0.4722 | 0.4722 | 0.97965 | -0.38852 | 0.97405 | -0.49807 | 32.4314
5 | -0.36929 | -0.093581 | 0.37005 | 0.094064 | 0.00075589 | 0.00048248 | 0.56129 | 0.56129 | 0.56129 | 0.97965 | -0.38852 | 0.98184 | -0.34601 | 38.5503
6 | 0.0078874 | 0.0019774 | -0.0078834 | -0.0019758 | 3.9881e-06 | 1.6406e-06 | 0.012048 | 0.012048 | 0.012048 | 0.97419 | -0.49572 | 0.97365 | -0.50634 | 3.3099
7 | 0.043958 | 0.011031 | -0.043921 | -0.011008 | 3.6756e-05 | 2.3254e-05 | 0.067158 | 0.067158 | 0.067158 | 0.97405 | -0.49807 | 0.97316 | -0.51562 | 18.45
8 | 0.20037 | 0.050443 | -0.19999 | -0.050204 | 0.00037735 | 0.00023937 | 0.30618 | 0.30618 | 0.30618 | 0.97405 | -0.49807 | 0.97205 | -0.53755 | 21.0288
9 | 0.064704 | 0.016269 | -0.064667 | -0.016247 | 3.6906e-05 | 2.1616e-05 | 0.098864 | 0.098865 | 0.098865 | 0.97405 | -0.49807 | 0.97345 | -0.51002 | 6.7902
10 | -0.41018 | -0.10412 | 0.41097 | 0.10463 | 0.00079273 | 0.00050624 | 0.62211 | 0.62211 | 0.62211 | 0.98184 | -0.34601 | 0.98392 | -0.30593 | 42.7277
11 | 0.064667 | 0.016247 | -0.064657 | -0.016242 | 9.7227e-06 | 5.695e-06 | 0.098865 | 0.098865 | 0.098865 | 0.97345 | -0.51002 | 0.97329 | -0.51317 | 6.7902
12 | 0.056643 | 0.014233 | -0.056631 | -0.014226 | 1.1676e-05 | 6.6473e-06 | 0.086612 | 0.086613 | 0.086613 | 0.97329 | -0.51317 | 0.97307 | -0.51749 | 5.9487
13 | -0.50671 | -0.12953 | 0.5089 | 0.13093 | 0.0021961 | 0.0014035 | 0.76305 | 0.76305 | 0.76305 | 0.9893 | -0.20245 | 0.99398 | -0.11327 | 52.4074
14 | 0.50147 | 0.12822 | -0.49991 | -0.12722 | 0.0015586 | 0.00099604 | 0.75518 | 0.75518 | 0.75518 | 0.9893 | -0.20245 | 0.98594 | -0.26691 | 51.8666
15 | 0.0052348 | 0.0013116 | -0.0052329 | -0.0013115 | 1.894e-06 | 1.6652e-07 | 0.0078735 | 0.0078739 | 0.0078739 | 0.9893 | -0.20245 | 0.98891 | -0.21004 | 2.1632
16 | -0.5089 | -0.13093 | 0.51044 | 0.13191 | 0.0015366 | 0.00098197 | 0.76305 | 0.76305 | 0.76305 | 0.99398 | -0.11327 | 0.99726 | -0.051375 | 52.4073
17 | 0.41175 | 0.10512 | -0.41097 | -0.10463 | 0.00077482 | 0.0004948 | 0.62211 | 0.62211 | 0.62211 | 0.98594 | -0.26691 | 0.98392 | -0.30593 | 42.7276
18 | 0.53414 | 0.13837 | -0.53281 | -0.13752 | 0.001338 | 0.00085513 | 0.79642 | 0.79642 | 0.79642 | 1 | 0 | 0.99726 | -0.051375 | 54.6993
19 | 0.13855 | 0.034805 | -0.13843 | -0.034724 | 0.0001289 | 8.0984e-05 | 0.21213 | 0.21213 | 0.21213 | 0.97205 | -0.53755 | 0.97106 | -0.55706 | 14.5693
20 | 0.04862 | 0.012219 | -0.048612 | -0.012214 | 8.6052e-06 | 4.6827e-06 | 0.074362 | 0.074362 | 0.074362 | 0.97307 | -0.51749 | 0.97288 | -0.5212 | 5.1073
21 | 0.10589 | 0.026564 | -0.10584 | -0.026534 | 4.7584e-05 | 2.9501e-05 | 0.16227 | 0.16227 | 0.16227 | 0.97106 | -0.55706 | 0.97059 | -0.56649 | 11.1447
22 | 0.032538 | 0.0081605 | -0.032522 | -0.0081507 | 1.6796e-05 | 9.8585e-06 | 0.049863 | 0.049863 | 0.049863 | 0.97106 | -0.55706 | 0.97052 | -0.5679 | 6.8493
23 | 0.040609 | 0.010208 | -0.040597 | -0.010201 | 1.201e-05 | 7.2745e-06 | 0.062123 | 0.062123 | 0.062123 | 0.97288 | -0.5212 | 0.97257 | -0.5274 | 8.5334
24 | 0.032604 | 0.0081978 | -0.032591 | -0.0081892 | 1.367e-05 | 8.5669e-06 | 0.049894 | 0.049894 | 0.049894 | 0.97257 | -0.5274 | 0.97212 | -0.53618 | 13.7071
25 | 0.032591 | 0.0081892 | -0.032556 | -0.0081673 | 3.496e-05 | 2.191e-05 | 0.049894 | 0.049894 | 0.049894 | 0.97212 | -0.53618 | 0.97098 | -0.55868 | 13.7071
26 | 0.052932 | 0.013274 | -0.05291 | -0.01326 | 2.1884e-05 | 1.3896e-05 | 0.081153 | 0.081153 | 0.081153 | 0.97059 | -0.56649 | 0.97015 | -0.57517 | 22.2949
27 | 0.032556 | 0.0081673 | -0.032534 | -0.0081538 | 2.1539e-05 | 1.35e-05 | 0.049894 | 0.049894 | 0.049894 | 0.97098 | -0.55868 | 0.97028 | -0.57256 | 13.7071

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53579 | 0.13837

## res_load
| p_mw | q_mvar
0 | 0.050465 | 0.012648
1 | 0.040133 | 0.010058
2 | 0.0080144 | 0.0020086
3 | 0.088168 | 0.022097
4 | 0.0052329 | 0.0013115
5 | 0.0078834 | 0.0019758
6 | 0.022366 | 0.0056055
7 | 0.043921 | 0.011008
8 | 0.061439 | 0.015398
9 | 0.008011 | 0.0020077
10 | 0.0080023 | 0.0020056
11 | 0.0079931 | 0.0020033
12 | 0.032522 | 0.0081507
13 | 0.052908 | 0.01326
14 | 0.05291 | 0.01326
15 | 0.032534 | 0.0081538

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1