## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-30_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-30_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1711-30_0_5_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1711-30_0_5_node_40 | 0.4 | n |  | TRUE
4 | bus_LV_1711-30_0_5_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_1711-30_0_5_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_1711-30_0_5_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_1711-30_0_5_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1711-30_0_5_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1711-30_0_5_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_1711-30_0_5_node_27 | 0.4 | n |  | TRUE
11 | bus_LV_1711-30_0_5_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_1711-30_0_5_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_1711-30_0_5_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1711-30_0_5_node_32 | 0.4 | n |  | TRUE
15 | bus_LV_1711-30_0_5_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_1711-30_0_5_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_1711-30_0_5_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1711-30_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_1711-30_0_5_node_30 | 0.4 | n |  | TRUE
20 | bus_LV_1711-30_0_5_node_39 | 0.4 | n |  | TRUE
21 | bus_LV_1711-30_0_5_node_42 | 0.4 | n |  | TRUE
22 | bus_LV_1711-30_0_5_node_43 | 0.4 | n |  | TRUE
23 | bus_LV_1711-30_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_1711-30_0_5_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_1711-30_0_5_node_48 | 0.4 | n |  | TRUE
26 | bus_LV_1711-30_0_5_node_41 | 0.4 | n |  | TRUE
27 | bus_LV_1711-30_0_5_node_13 | 0.4 | n |  | TRUE
28 | bus_LV_1711-30_0_5_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_1711-30_0_5_node_16 | 0.4 | n |  | TRUE
30 | bus_LV_1711-30_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_1711-30_0_5_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_1711-30_0_5_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_1711-30_0_5_node_44 | 0.4 | n |  | TRUE
34 | bus_LV_1711-30_0_5_node_45 | 0.4 | n |  | TRUE
35 | bus_LV_1711-30_0_5_node_28 | 0.4 | n |  | TRUE
36 | bus_LV_1711-30_0_5_node_23 | 0.4 | n |  | TRUE
37 | bus_LV_1711-30_0_5_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_1711-30_0_5_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1711-30_0_5_node_46 | 0.4 | n |  | TRUE
40 | bus_LV_1711-30_0_5_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_1711-30_0_5_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_1711-30_0_5_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_1711-30_0_5_node_36 | 0.4 | n |  | TRUE
44 | bus_LV_1711-30_0_5_node_47 | 0.4 | n |  | TRUE
45 | bus_MV_231_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-30_0_5_load_0 | 0 | 0.061721 | 0.015469 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-30_0_5_load_40 | 3 | 0.038975 | 0.0097681 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-30_0_5_load_4 | 5 | 0.04792 | 0.01201 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-30_0_5_load_6 | 7 | 0.045166 | 0.01132 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-30_0_5_load_27 | 10 | 0.021246 | 0.0053248 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-30_0_5_load_19 | 11 | 0.010815 | 0.0027105 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-30_0_5_load_33 | 12 | 0.020454 | 0.0051262 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-30_0_5_load_32 | 14 | 0.015448 | 0.0038715 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-30_0_5_load_10 | 16 | 0.089859 | 0.022521 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-30_0_5_load_25 | 17 | 0.0085877 | 0.0021523 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-30_0_5_load_30 | 19 | 0.0097942 | 0.0024547 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-30_0_5_load_43 | 22 | 0.0094519 | 0.0023689 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-30_0_5_load_34 | 24 | 0.0088603 | 0.0022206 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-30_0_5_load_48 | 25 | 0.022197 | 0.0055631 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-30_0_5_load_41 | 26 | 0.013127 | 0.00329 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-30_0_5_load_13 | 27 | 0.054446 | 0.013646 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-30_0_5_load_21 | 30 | 0.0038362 | 0.00096145 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-30_0_5_load_20 | 31 | 0.0027909 | 0.00069947 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-30_0_5_load_22 | 32 | 0.025627 | 0.0064226 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-30_0_5_load_45 | 34 | 0.0018824 | 0.00047179 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-30_0_5_load_28 | 35 | 0.017002 | 0.0042611 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-30_0_5_load_23 | 36 | 0.0086458 | 0.0021668 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-30_0_5_load_24 | 37 | 0.0081402 | 0.0020401 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-30_0_5_load_26 | 38 | 0.0050199 | 0.0012581 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-30_0_5_load_46 | 39 | 0.0053044 | 0.0013294 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-30_0_5_load_29 | 41 | 0.0078321 | 0.0019629 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-30_0_5_load_31 | 42 | 0.026778 | 0.0067112 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1711-30_0_5_load_47 | 44 | 0.016224 | 0.0040662 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-30_0_5_line_0 |  | 0 | 1 | 0.020209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-30_0_5_line_1 |  | 1 | 2 | 0.024092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-30_0_5_line_2 |  | 2 | 3 | 0.042023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-30_0_5_line_3 |  | 3 | 4 | 0.044188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-30_0_5_line_4 |  | 4 | 28 | 0.18812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
5 | LV_1711-30_0_5_line_5 |  | 5 | 6 | 0.030203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_1711-30_0_5_line_6 |  | 5 | 7 | 0.025169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-30_0_5_line_7 |  | 6 | 8 | 0.05926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_1711-30_0_5_line_8 |  | 6 | 9 | 0.060852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_1711-30_0_5_line_9 |  | 8 | 10 | 0.010636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-30_0_5_line_10 |  | 8 | 11 | 0.052907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_1711-30_0_5_line_11 |  | 9 | 12 | 0.016557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-30_0_5_line_12 |  | 9 | 13 | 0.034735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_1711-30_0_5_line_13 |  | 9 | 14 | 0.071299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-30_0_5_line_14 |  | 10 | 17 | 0.044421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-30_0_5_line_15 |  | 11 | 18 | 0.02358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_1711-30_0_5_line_16 |  | 13 | 15 | 0.056606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-30_0_5_line_17 |  | 13 | 16 | 0.035064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-30_0_5_line_18 |  | 14 | 19 | 0.021309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-30_0_5_line_19 |  | 15 | 20 | 0.093074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-30_0_5_line_20 |  | 15 | 21 | 0.1913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-30_0_5_line_21 |  | 15 | 22 | 0.027315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-30_0_5_line_22 |  | 17 | 35 | 0.033741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1711-30_0_5_line_23 |  | 17 | 36 | 0.048776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1711-30_0_5_line_24 |  | 18 | 27 | 0.0091638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_1711-30_0_5_line_25 |  | 19 | 41 | 0.00058689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-30_0_5_line_26 |  | 20 | 25 | 0.009504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1711-30_0_5_line_27 |  | 20 | 23 | 0.070324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1711-30_0_5_line_28 |  | 21 | 26 | 0.077835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1711-30_0_5_line_29 |  | 23 | 24 | 0.011946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1711-30_0_5_line_30 |  | 27 | 28 | 0.05573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_1711-30_0_5_line_31 |  | 28 | 29 | 0.030658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-30_0_5_line_32 |  | 29 | 30 | 0.043984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1711-30_0_5_line_33 |  | 30 | 31 | 0.022362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1711-30_0_5_line_34 |  | 32 | 33 | 0.055606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1711-30_0_5_line_35 |  | 33 | 34 | 0.018652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1711-30_0_5_line_36 |  | 33 | 35 | 0.060994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1711-30_0_5_line_37 |  | 36 | 37 | 0.013053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1711-30_0_5_line_38 |  | 37 | 38 | 0.024492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1711-30_0_5_line_39 |  | 38 | 39 | 0.02473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1711-30_0_5_line_40 |  | 39 | 40 | 0.040866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1711-30_0_5_line_41 |  | 40 | 43 | 0.05208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1711-30_0_5_line_42 |  | 41 | 42 | 0.012105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1711-30_0_5_line_43 |  | 43 | 44 | 0.036825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-30_0_5_trafo_4 | 0.63 MVA 20/0.4 kV | 45 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2679836.4588 | 1226611.7264 | 2679831.4158 | 1226609.0792 | 2679818.5323 | 1226602.3979
1 | 2679836.4588 | 1226611.7264 | 2679841.4839 | 1226601.5981 | 2679846.8548 | 1226589.9957
2 | 2679846.8548 | 1226589.9957 | 2679884.3308 | 1226609.0072
3 | 2679923.7381 | 1226628.9985 | 2679884.3308 | 1226609.0072
4 | 2679923.7381 | 1226628.9985 | 2679962.729 | 1226648.78 | 2679991.3286 | 1226666.7877 | 2680003.6763 | 1226648.7637 | 2680012.9954 | 1226628.7977 | 2680018.3964 | 1226609.902 | 2680023.2087 | 1226586.3174 | 2680025.0952 | 1226573.434 | 2680026.4863 | 1226563.5572
5 | 2679940.8166 | 1226449.0395 | 2679927.9873 | 1226476.3826
6 | 2679917.2962 | 1226499.1686 | 2679927.9873 | 1226476.3826
7 | 2679940.8166 | 1226449.0395 | 2679943.9107 | 1226447.8136 | 2679995.9005 | 1226427.1871
8 | 2679901.3806 | 1226423.3592 | 2679895.6559 | 1226435.8909 | 2679900.7139 | 1226438.0046 | 2679940.8166 | 1226449.0395
9 | 2679995.9005 | 1226427.1871 | 2679992.0567 | 1226417.2701
10 | 2679995.9005 | 1226427.1871 | 2680000.458 | 1226438.8896 | 2680015.0831 | 1226476.4938
11 | 2679901.3806 | 1226423.3592 | 2679916.9253 | 1226429.183
12 | 2679876.3212 | 1226427.8036 | 2679895.6559 | 1226435.8909 | 2679901.3806 | 1226423.3592
13 | 2679901.3806 | 1226423.3592 | 2679880.2645 | 1226414.7033 | 2679901.0995 | 1226370.9311
14 | 2679976.0028 | 1226375.8516 | 2679992.0567 | 1226417.2701
15 | 2680021.6914 | 1226499.0935 | 2680017.4635 | 1226482.6144 | 2680015.0831 | 1226476.4938
16 | 2679824.1061 | 1226405.9439 | 2679852.7502 | 1226417.9362 | 2679876.3212 | 1226427.8036
17 | 2679876.3212 | 1226427.8036 | 2679861.1865 | 1226459.4332
18 | 2679920.7958 | 1226379.0629 | 2679901.0995 | 1226370.9311 | 2679901.0995 | 1226370.9311
19 | 2679824.1061 | 1226405.9439 | 2679819.7794 | 1226404.1291 | 2679794.0777 | 1226392.5989 | 2679807.8247 | 1226363.4969 | 2679834.1432 | 1226373.1341
20 | 2679684.6154 | 1226421.663 | 2679714.5453 | 1226356.9646 | 2679750.4351 | 1226373.0229 | 2679758.1585 | 1226376.4843 | 2679763.7571 | 1226378.9944 | 2679794.0777 | 1226392.5989 | 2679819.7794 | 1226404.1291 | 2679824.1061 | 1226405.9439
21 | 2679824.1061 | 1226405.9439 | 2679811.8367 | 1226430.3487
22 | 2679976.0028 | 1226375.8516 | 2680006.8595 | 1226362.2019
23 | 2679976.0028 | 1226375.8516 | 2679973.3002 | 1226368.8217 | 2679968.4508 | 1226353.4461 | 2679959.7077 | 1226329.8942
24 | 2680021.6914 | 1226499.0935 | 2680023.6887 | 1226508.037
25 | 2679921.3382 | 1226379.2868 | 2679920.7958 | 1226379.0629
26 | 2679843.1761 | 1226376.1685 | 2679834.1432 | 1226373.1341
27 | 2679834.1432 | 1226373.1341 | 2679844.6922 | 1226351.8835 | 2679852.5221 | 1226336.1223 | 2679879.2118 | 1226347.4659
28 | 2679684.6154 | 1226421.663 | 2679755.7259 | 1226453.3113
29 | 2679879.2118 | 1226347.4659 | 2679883.41 | 1226336.2814
30 | 2680026.4863 | 1226563.5572 | 2680026.3686 | 1226532.3122 | 2680025.2804 | 1226515.1638 | 2680023.6887 | 1226508.037
31 | 2680026.4863 | 1226563.5572 | 2680033.5629 | 1226565.487 | 2680056.1285 | 1226571.7058
32 | 2680056.1285 | 1226571.7058 | 2680060.551 | 1226564.705 | 2680061.8006 | 1226555.2154 | 2680059.4732 | 1226547.3565 | 2680061.4505 | 1226539.5556 | 2680068.1721 | 1226532.3041
33 | 2680080.8058 | 1226514.1308 | 2680078.21 | 1226520.4237 | 2680068.9423 | 1226531.4732 | 2680068.1721 | 1226532.3041
34 | 2680060.4278 | 1226333.4025 | 2680066.9426 | 1226388.625
35 | 2680060.4278 | 1226333.4025 | 2680053.0695 | 1226316.2631
36 | 2680060.4278 | 1226333.4025 | 2680038.8375 | 1226347.5883 | 2680026.938 | 1226353.0987 | 2680016.7394 | 1226357.8314 | 2680006.8595 | 1226362.2019
37 | 2679955.1652 | 1226317.6576 | 2679959.7077 | 1226329.8942
38 | 2679955.1652 | 1226317.6576 | 2679953.2932 | 1226312.6149 | 2679946.643 | 1226294.6963
39 | 2679946.643 | 1226294.6963 | 2679938.0381 | 1226271.5112
40 | 2679923.8189 | 1226233.1987 | 2679938.0381 | 1226271.5112
41 | 2679875.6591 | 1226253.0211 | 2679908.7642 | 1226239.3896 | 2679923.8189 | 1226233.1987
42 | 2679932.5275 | 1226383.9064 | 2679921.3382 | 1226379.2868
43 | 2679875.6591 | 1226253.0211 | 2679875.2291 | 1226263.0221 | 2679877.6673 | 1226271.127 | 2679888.5589 | 1226285.9165

## bus_geodata
| x | y | coords
0 | 2679818.5323 | 1226602.3979
1 | 2679836.4588 | 1226611.7264
2 | 2679846.8548 | 1226589.9957
3 | 2679884.3308 | 1226609.0072
4 | 2679923.7381 | 1226628.9985
5 | 2679927.9873 | 1226476.3826
6 | 2679940.8167 | 1226449.0395
7 | 2679917.2962 | 1226499.1686
8 | 2679995.9005 | 1226427.1871
9 | 2679901.3806 | 1226423.3592
10 | 2679992.0567 | 1226417.2701
11 | 2680015.0831 | 1226476.4938
12 | 2679916.9253 | 1226429.183
13 | 2679876.3212 | 1226427.8036
14 | 2679901.0995 | 1226370.9311
15 | 2679824.1061 | 1226405.9439
16 | 2679861.1865 | 1226459.4332
17 | 2679976.0028 | 1226375.8516
18 | 2680021.6914 | 1226499.0935
19 | 2679920.7958 | 1226379.0629
20 | 2679834.1432 | 1226373.1341
21 | 2679684.6154 | 1226421.663
22 | 2679811.8367 | 1226430.3487
23 | 2679879.2118 | 1226347.4659
24 | 2679883.41 | 1226336.2814
25 | 2679843.1761 | 1226376.1685
26 | 2679755.7259 | 1226453.3113
27 | 2680023.6887 | 1226508.037
28 | 2680026.4863 | 1226563.5572
29 | 2680056.1285 | 1226571.7058
30 | 2680068.1721 | 1226532.3041
31 | 2680080.8058 | 1226514.1308
32 | 2680066.9426 | 1226388.625
33 | 2680060.4278 | 1226333.4025
34 | 2680053.0695 | 1226316.2631
35 | 2680006.8595 | 1226362.2019
36 | 2679959.7077 | 1226329.8942
37 | 2679955.1652 | 1226317.6576
38 | 2679946.643 | 1226294.6963
39 | 2679938.0381 | 1226271.5112
40 | 2679923.8189 | 1226233.1987
41 | 2679921.3382 | 1226379.2868
42 | 2679932.5275 | 1226383.9064
43 | 2679875.6591 | 1226253.0211
44 | 2679888.5589 | 1226285.9165
45 | 2679917.2962 | 1226499.1686

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97273 | -0.5264 | 0.061721 | 0.015469
1 | 0.97389 | -0.50345 | 0 | 0
2 | 0.97527 | -0.47617 | 0 | 0
3 | 0.97769 | -0.42875 | 0.038975 | 0.0097681
4 | 0.98183 | -0.34796 | 0 | 0
5 | 1 | 0 | -0.56876 | -0.14516
6 | 0.99642 | -0.06791 | 0 | 0
7 | 0.99897 | -0.019834 | 0.045166 | 0.01132
8 | 0.99244 | -0.14372 | 0 | 0
9 | 0.99014 | -0.18822 | 0 | 0
10 | 0.99129 | -0.1659 | 0.021246 | 0.0053248
11 | 0.99033 | -0.18421 | 0.010815 | 0.0027105
12 | 0.98983 | -0.19424 | 0.020454 | 0.0051262
13 | 0.98785 | -0.23264 | 0 | 0
14 | 0.98622 | -0.26439 | 0.015448 | 0.0038715
15 | 0.98504 | -0.28704 | 0 | 0
16 | 0.98495 | -0.28908 | 0.089859 | 0.022521
17 | 0.98734 | -0.24219 | 0.0085877 | 0.0021523
18 | 0.98945 | -0.20118 | 0 | 0
19 | 0.98535 | -0.28136 | 0.0097942 | 0.0024547
20 | 0.98237 | -0.33911 | 0 | 0
21 | 0.98272 | -0.33227 | 0 | 0
22 | 0.98481 | -0.29168 | 0.0094519 | 0.0023689
23 | 0.9818 | -0.35037 | 0 | 0
24 | 0.9817 | -0.35228 | 0.0088603 | 0.0022206
25 | 0.98218 | -0.34292 | 0.022197 | 0.0055631
26 | 0.98178 | -0.35073 | 0.013127 | 0.00329
27 | 0.98911 | -0.20778 | 0.054446 | 0.013646
28 | 0.98771 | -0.23446 | 0 | 0
29 | 0.98753 | -0.23809 | 0 | 0
30 | 0.98726 | -0.24331 | 0.0038362 | 0.00096145
31 | 0.9872 | -0.24442 | 0.0027909 | 0.00069947
32 | 0.9831 | -0.32488 | 0.025627 | 0.0064226
33 | 0.98441 | -0.29922 | 0 | 0
34 | 0.98438 | -0.29985 | 0.0018824 | 0.00047179
35 | 0.98596 | -0.26908 | 0.017002 | 0.0042611
36 | 0.9854 | -0.28006 | 0.0086458 | 0.0021668
37 | 0.98498 | -0.28819 | 0.0081402 | 0.0020401
38 | 0.98438 | -0.29989 | 0.0050199 | 0.0012581
39 | 0.98389 | -0.30947 | 0.0053044 | 0.0013294
40 | 0.98328 | -0.32142 | 0 | 0
41 | 0.98533 | -0.28173 | 0.0078321 | 0.0019629
42 | 0.98503 | -0.28755 | 0.026778 | 0.0067112
43 | 0.9825 | -0.33666 | 0 | 0
44 | 0.98194 | -0.34746 | 0.016224 | 0.0040662
45 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.061721 | -0.015469 | 0.061788 | 0.015512 | 6.7556e-05 | 4.2985e-05 | 0.094417 | 0.094417 | 0.094417 | 0.97273 | -0.5264 | 0.97389 | -0.50345 | 25.9386
1 | -0.061788 | -0.015512 | 0.061869 | 0.015563 | 8.0537e-05 | 5.1243e-05 | 0.094417 | 0.094416 | 0.094417 | 0.97389 | -0.50345 | 0.97527 | -0.47617 | 25.9386
2 | -0.061869 | -0.015563 | 0.062009 | 0.015652 | 0.00014048 | 8.938e-05 | 0.094416 | 0.094416 | 0.094416 | 0.97527 | -0.47617 | 0.97769 | -0.42875 | 25.9386
3 | -0.10098 | -0.02542 | 0.10138 | 0.02567 | 0.00039164 | 0.00025009 | 0.15374 | 0.15373 | 0.15374 | 0.97769 | -0.42875 | 0.98183 | -0.34796 | 42.2349
4 | -0.10138 | -0.02567 | 0.10193 | 0.026019 | 0.00055575 | 0.0003485 | 0.15373 | 0.15373 | 0.15373 | 0.98183 | -0.34796 | 0.98771 | -0.23446 | 14.0783
5 | 0.5219 | 0.13381 | -0.52019 | -0.13272 | 0.0017124 | 0.0010944 | 0.77766 | 0.77766 | 0.77766 | 1 | 0 | 0.99642 | -0.06791 | 53.411
6 | 0.045208 | 0.011347 | -0.045166 | -0.01132 | 4.272e-05 | 2.7011e-05 | 0.067276 | 0.067277 | 0.067277 | 1 | 0 | 0.99897 | -0.019834 | 18.4826
7 | 0.294 | 0.075109 | -0.29292 | -0.074425 | 0.0010734 | 0.00068389 | 0.43955 | 0.43955 | 0.43955 | 0.99642 | -0.06791 | 0.99244 | -0.14372 | 30.189
8 | 0.22619 | 0.057608 | -0.22489 | -0.056775 | 0.0013044 | 0.00083323 | 0.33811 | 0.33811 | 0.33811 | 0.99642 | -0.06791 | 0.99014 | -0.18822 | 46.4442
9 | 0.11843 | 0.02997 | -0.11831 | -0.02989 | 0.00012591 | 8.0445e-05 | 0.17768 | 0.17768 | 0.17768 | 0.99244 | -0.14372 | 0.99129 | -0.1659 | 48.8119
10 | 0.17449 | 0.044455 | -0.17415 | -0.04424 | 0.00034016 | 0.00021497 | 0.26188 | 0.26188 | 0.26188 | 0.99244 | -0.14372 | 0.99033 | -0.18421 | 17.9861
11 | 0.020459 | 0.0051297 | -0.020454 | -0.0051262 | 5.8701e-06 | 3.5439e-06 | 0.030748 | 0.030748 | 0.030748 | 0.99014 | -0.18822 | 0.98983 | -0.19424 | 8.4472
12 | 0.14431 | 0.036479 | -0.14401 | -0.036283 | 0.00030665 | 0.00019537 | 0.21699 | 0.21699 | 0.21699 | 0.99014 | -0.18822 | 0.98785 | -0.23264 | 29.8062
13 | 0.060114 | 0.015167 | -0.059896 | -0.015028 | 0.00021839 | 0.00013886 | 0.090377 | 0.090378 | 0.090378 | 0.99014 | -0.18822 | 0.98622 | -0.26439 | 24.829
14 | 0.097062 | 0.024565 | -0.096708 | -0.024339 | 0.00035402 | 0.00022601 | 0.14578 | 0.14578 | 0.14578 | 0.99129 | -0.1659 | 0.98734 | -0.24219 | 40.0503
15 | 0.16333 | 0.04153 | -0.1632 | -0.041446 | 0.00013337 | 8.4147e-05 | 0.24563 | 0.24563 | 0.24563 | 0.99033 | -0.18421 | 0.98945 | -0.20118 | 16.8701
16 | 0.053905 | 0.013608 | -0.053765 | -0.013519 | 0.00014008 | 8.8927e-05 | 0.081233 | 0.081234 | 0.081234 | 0.98785 | -0.23264 | 0.98504 | -0.28704 | 22.3169
17 | 0.090102 | 0.022676 | -0.089859 | -0.022521 | 0.00024233 | 0.00015464 | 0.13576 | 0.13576 | 0.13576 | 0.98785 | -0.23264 | 0.98495 | -0.28908 | 37.2956
18 | 0.044448 | 0.011156 | -0.044412 | -0.011134 | 3.5946e-05 | 2.2734e-05 | 0.06707 | 0.06707 | 0.06707 | 0.98622 | -0.26439 | 0.98535 | -0.28136 | 18.4259
19 | 0.031144 | 0.0078369 | -0.031067 | -0.0077886 | 7.7291e-05 | 4.8284e-05 | 0.047058 | 0.047058 | 0.047058 | 0.98504 | -0.28704 | 0.98237 | -0.33911 | 12.9281
20 | 0.013167 | 0.0033121 | -0.013139 | -0.0032964 | 2.8394e-05 | 1.5743e-05 | 0.019895 | 0.019895 | 0.019895 | 0.98504 | -0.28704 | 0.98272 | -0.33227 | 5.4658
21 | 0.0094539 | 0.0023698 | -0.0094519 | -0.0023689 | 2.0892e-06 | 9.8947e-07 | 0.014281 | 0.014282 | 0.014282 | 0.98504 | -0.28704 | 0.98481 | -0.29168 | 3.9235
22 | 0.044639 | 0.011236 | -0.044582 | -0.011199 | 5.7296e-05 | 3.6238e-05 | 0.067292 | 0.067293 | 0.067293 | 0.98734 | -0.24219 | 0.98596 | -0.26908 | 18.487
23 | 0.043481 | 0.010951 | -0.043402 | -0.010901 | 7.8589e-05 | 4.9675e-05 | 0.065548 | 0.065549 | 0.065549 | 0.98734 | -0.24219 | 0.9854 | -0.28006 | 18.0078
24 | 0.1632 | 0.041446 | -0.16315 | -0.041413 | 5.1833e-05 | 3.2702e-05 | 0.24563 | 0.24563 | 0.24563 | 0.98945 | -0.20118 | 0.98911 | -0.20778 | 16.8701
25 | 0.034618 | 0.0086791 | -0.034618 | -0.0086787 | 6.0152e-07 | 3.775e-07 | 0.052279 | 0.052279 | 0.052279 | 0.98535 | -0.28136 | 0.98533 | -0.28173 | 14.3625
26 | 0.022201 | 0.0055655 | -0.022197 | -0.0055631 | 4.0305e-06 | 2.4592e-06 | 0.033629 | 0.033629 | 0.033629 | 0.98237 | -0.33911 | 0.98218 | -0.34292 | 9.2386
27 | 0.0088658 | 0.0022231 | -0.0088611 | -0.002221 | 4.7563e-06 | 2.1542e-06 | 0.01343 | 0.01343 | 0.01343 | 0.98237 | -0.33911 | 0.9818 | -0.35037 | 3.6895
28 | 0.013139 | 0.0032964 | -0.013127 | -0.00329 | 1.1554e-05 | 6.4092e-06 | 0.019895 | 0.019896 | 0.019896 | 0.98272 | -0.33227 | 0.98178 | -0.35073 | 5.4659
29 | 0.0088611 | 0.002221 | -0.0088603 | -0.0022206 | 8.0802e-07 | 3.6607e-07 | 0.01343 | 0.01343 | 0.01343 | 0.9818 | -0.35037 | 0.9817 | -0.35228 | 3.6896
30 | 0.1087 | 0.027767 | -0.10856 | -0.027681 | 0.00014005 | 8.6772e-05 | 0.16372 | 0.16372 | 0.16372 | 0.98911 | -0.20778 | 0.98771 | -0.23446 | 11.2446
31 | 0.0066301 | 0.0016616 | -0.0066289 | -0.0016612 | 1.147e-06 | 3.4178e-07 | 0.0099884 | 0.0099885 | 0.0099885 | 0.98771 | -0.23446 | 0.98753 | -0.23809 | 2.7441
32 | 0.0066289 | 0.0016612 | -0.0066273 | -0.0016607 | 1.6456e-06 | 4.9063e-07 | 0.0099885 | 0.0099887 | 0.0099887 | 0.98753 | -0.23809 | 0.98726 | -0.24331 | 2.7442
33 | 0.0027911 | 0.00069928 | -0.0027909 | -0.00069947 | 1.484e-07 | -1.9095e-07 | 0.0042067 | 0.0042068 | 0.0042068 | 0.98726 | -0.24331 | 0.9872 | -0.24442 | 1.1557
34 | -0.025627 | -0.0064226 | 0.025658 | 0.006442 | 3.1373e-05 | 1.9372e-05 | 0.038788 | 0.038788 | 0.038788 | 0.9831 | -0.32488 | 0.98441 | -0.29922 | 10.6561
35 | 0.0018825 | 0.00047158 | -0.0018824 | -0.00047179 | 5.6634e-08 | -2.0088e-07 | 0.0028455 | 0.0028456 | 0.0028456 | 0.98441 | -0.29922 | 0.98438 | -0.29985 | 0.78174
36 | -0.02754 | -0.0069136 | 0.02758 | 0.0069382 | 3.9646e-05 | 2.4597e-05 | 0.041634 | 0.041633 | 0.041634 | 0.98441 | -0.29922 | 0.98596 | -0.26908 | 11.4378
37 | 0.034756 | 0.0087346 | -0.034743 | -0.0087261 | 1.3487e-05 | 8.4657e-06 | 0.052493 | 0.052493 | 0.052493 | 0.9854 | -0.28006 | 0.98498 | -0.28819 | 14.4211
38 | 0.026603 | 0.006686 | -0.026588 | -0.0066768 | 1.4839e-05 | 9.1854e-06 | 0.040195 | 0.040195 | 0.040195 | 0.98498 | -0.28819 | 0.98438 | -0.29989 | 11.0427
39 | 0.021568 | 0.0054187 | -0.021558 | -0.0054127 | 9.8604e-06 | 5.9964e-06 | 0.032607 | 0.032607 | 0.032607 | 0.98438 | -0.29989 | 0.98389 | -0.30947 | 8.9581
40 | 0.016254 | 0.0040833 | -0.016244 | -0.0040779 | 9.2628e-06 | 5.4095e-06 | 0.024585 | 0.024585 | 0.024585 | 0.98389 | -0.30947 | 0.98328 | -0.32142 | 6.7542
41 | 0.016244 | 0.0040779 | -0.016233 | -0.004071 | 1.1805e-05 | 6.895e-06 | 0.024585 | 0.024586 | 0.024586 | 0.98328 | -0.32142 | 0.9825 | -0.33666 | 6.7543
42 | 0.026785 | 0.0067158 | -0.026778 | -0.0067112 | 7.4282e-06 | 4.5999e-06 | 0.040452 | 0.040452 | 0.040452 | 0.98533 | -0.28173 | 0.98503 | -0.28755 | 11.1131
43 | 0.016233 | 0.004071 | -0.016224 | -0.0040662 | 8.3471e-06 | 4.8761e-06 | 0.024586 | 0.024586 | 0.024586 | 0.9825 | -0.33666 | 0.98194 | -0.34746 | 6.7543

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.61668 | 0.15717

## res_load
| p_mw | q_mvar
0 | 0.061721 | 0.015469
1 | 0.038975 | 0.0097681
2 | 0.04792 | 0.01201
3 | 0.045166 | 0.01132
4 | 0.021246 | 0.0053248
5 | 0.010815 | 0.0027105
6 | 0.020454 | 0.0051262
7 | 0.015448 | 0.0038715
8 | 0.089859 | 0.022521
9 | 0.0085877 | 0.0021523
10 | 0.0097942 | 0.0024547
11 | 0.0094519 | 0.0023689
12 | 0.0088603 | 0.0022206
13 | 0.022197 | 0.0055631
14 | 0.013127 | 0.00329
15 | 0.054446 | 0.013646
16 | 0.0038362 | 0.00096145
17 | 0.0027909 | 0.00069947
18 | 0.025627 | 0.0064226
19 | 0.0018824 | 0.00047179
20 | 0.017002 | 0.0042611
21 | 0.0086458 | 0.0021668
22 | 0.0081402 | 0.0020401
23 | 0.0050199 | 0.0012581
24 | 0.0053044 | 0.0013294
25 | 0.0078321 | 0.0019629
26 | 0.026778 | 0.0067112
27 | 0.016224 | 0.0040662

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1