## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-32_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-32_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-32_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1711-32_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1711-32_0_6_node_29 | 0.4 | n |  | TRUE
5 | bus_LV_1711-32_0_6_node_30 | 0.4 | n |  | TRUE
6 | bus_LV_1711-32_0_6_node_4 | 0.4 | n |  | TRUE
7 | bus_LV_1711-32_0_6_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1711-32_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1711-32_0_6_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_1711-32_0_6_node_37 | 0.4 | n |  | TRUE
11 | bus_LV_1711-32_0_6_node_27 | 0.4 | n |  | TRUE
12 | bus_LV_1711-32_0_6_node_35 | 0.4 | n |  | TRUE
13 | bus_LV_1711-32_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_1711-32_0_6_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_1711-32_0_6_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_1711-32_0_6_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_1711-32_0_6_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_1711-32_0_6_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1711-32_0_6_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_1711-32_0_6_node_56 | 0.4 | n |  | TRUE
21 | bus_LV_1711-32_0_6_node_54 | 0.4 | n |  | TRUE
22 | bus_LV_1711-32_0_6_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_1711-32_0_6_node_53 | 0.4 | n |  | TRUE
24 | bus_LV_1711-32_0_6_node_14 | 0.4 | n |  | TRUE
25 | bus_LV_1711-32_0_6_node_15 | 0.4 | n |  | TRUE
26 | bus_LV_1711-32_0_6_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1711-32_0_6_node_24 | 0.4 | n |  | TRUE
28 | bus_LV_1711-32_0_6_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_1711-32_0_6_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_1711-32_0_6_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_1711-32_0_6_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_1711-32_0_6_node_41 | 0.4 | n |  | TRUE
33 | bus_LV_1711-32_0_6_node_21 | 0.4 | n |  | TRUE
34 | bus_LV_1711-32_0_6_node_42 | 0.4 | n |  | TRUE
35 | bus_LV_1711-32_0_6_node_40 | 0.4 | n |  | TRUE
36 | bus_LV_1711-32_0_6_node_31 | 0.4 | n |  | TRUE
37 | bus_LV_1711-32_0_6_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_1711-32_0_6_node_33 | 0.4 | n |  | TRUE
39 | bus_LV_1711-32_0_6_node_34 | 0.4 | n |  | TRUE
40 | bus_LV_1711-32_0_6_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_1711-32_0_6_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_1711-32_0_6_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_1711-32_0_6_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_1711-32_0_6_node_45 | 0.4 | n |  | TRUE
45 | bus_LV_1711-32_0_6_node_47 | 0.4 | n |  | TRUE
46 | bus_LV_1711-32_0_6_node_46 | 0.4 | n |  | TRUE
47 | bus_LV_1711-32_0_6_node_51 | 0.4 | n |  | TRUE
48 | bus_LV_1711-32_0_6_node_48 | 0.4 | n |  | TRUE
49 | bus_LV_1711-32_0_6_node_52 | 0.4 | n |  | TRUE
50 | bus_LV_1711-32_0_6_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_1711-32_0_6_node_50 | 0.4 | n |  | TRUE
52 | bus_MV_231_1_node_184 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-32_0_6_load_0 | 0 | 0.00058843 | 0.00014747 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-32_0_6_load_1 | 1 | 0.0030686 | 0.00076906 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-32_0_6_load_3 | 3 | 0.00059518 | 0.00014917 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-32_0_6_load_29 | 4 | 0.00060199 | 0.00015087 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-32_0_6_load_30 | 5 | 0.0011668 | 0.00029243 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-32_0_6_load_4 | 6 | 0.0072158 | 0.0018085 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-32_0_6_load_37 | 10 | 0.0011682 | 0.00029277 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-32_0_6_load_27 | 11 | 0.0028114 | 0.00070461 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-32_0_6_load_35 | 12 | 0.00063314 | 0.00015868 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-32_0_6_load_8 | 13 | 0.015121 | 0.0037897 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-32_0_6_load_9 | 14 | 0.024054 | 0.0060284 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-32_0_6_load_11 | 16 | 0.01665 | 0.0041728 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-32_0_6_load_56 | 20 | 0.017754 | 0.0044496 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-32_0_6_load_54 | 21 | 0.026368 | 0.0066084 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-32_0_6_load_53 | 23 | 0.026346 | 0.006603 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-32_0_6_load_14 | 24 | 0.012273 | 0.0030758 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-32_0_6_load_15 | 25 | 0.011873 | 0.0029755 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-32_0_6_load_24 | 27 | 0.034392 | 0.0086194 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-32_0_6_load_20 | 30 | 0.015392 | 0.0038577 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-32_0_6_load_28 | 31 | 0.000317 | 7.9448e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-32_0_6_load_41 | 32 | 0.00075787 | 0.00018994 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-32_0_6_load_21 | 33 | 0.039288 | 0.0098465 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-32_0_6_load_42 | 34 | 0.072691 | 0.018218 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-32_0_6_load_40 | 35 | 0.0010633 | 0.00026648 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-32_0_6_load_31 | 36 | 0.0013009 | 0.00032603 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-32_0_6_load_32 | 37 | 0.00061555 | 0.00015427 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-32_0_6_load_33 | 38 | 0.00041691 | 0.00010449 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1711-32_0_6_load_36 | 40 | 0.00042638 | 0.00010686 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1711-32_0_6_load_38 | 41 | 0.00017117 | 4.2899e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1711-32_0_6_load_39 | 42 | 0.0011324 | 0.0002838 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1711-32_0_6_load_43 | 43 | 0.012134 | 0.0030411 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1711-32_0_6_load_47 | 45 | 0.033647 | 0.0084327 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1711-32_0_6_load_46 | 46 | 0.012134 | 0.0030411 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1711-32_0_6_load_52 | 49 | 0.036469 | 0.0091401 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1711-32_0_6_load_49 | 50 | 0.018197 | 0.0045605 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1711-32_0_6_load_50 | 51 | 0.037081 | 0.0092933 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-32_0_6_line_0 |  | 0 | 1 | 0.048265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-32_0_6_line_1 |  | 0 | 2 | 0.06453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-32_0_6_line_2 |  | 2 | 3 | 0.065233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-32_0_6_line_3 |  | 3 | 4 | 0.023166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-32_0_6_line_4 |  | 4 | 5 | 0.023402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-32_0_6_line_5 |  | 5 | 36 | 0.0035426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1711-32_0_6_line_6 |  | 6 | 7 | 0.024447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-32_0_6_line_7 |  | 7 | 8 | 0.075553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-32_0_6_line_8 |  | 8 | 9 | 0.02812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-32_0_6_line_9 |  | 8 | 10 | 0.062784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-32_0_6_line_10 |  | 9 | 11 | 0.020933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1711-32_0_6_line_11 |  | 10 | 12 | 0.024935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-32_0_6_line_12 |  | 11 | 31 | 0.03752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-32_0_6_line_13 |  | 12 | 39 | 0.068412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-32_0_6_line_14 |  | 13 | 14 | 0.017916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1711-32_0_6_line_15 |  | 13 | 15 | 0.017595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1711-32_0_6_line_16 |  | 14 | 16 | 0.024655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1711-32_0_6_line_17 |  | 15 | 17 | 0.002616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-32_0_6_line_18 |  | 15 | 18 | 0.045305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1711-32_0_6_line_19 |  | 16 | 19 | 0.017601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1711-32_0_6_line_20 |  | 17 | 20 | 0.024608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-32_0_6_line_21 |  | 18 | 21 | 0.026183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1711-32_0_6_line_22 |  | 19 | 22 | 0.022497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1711-32_0_6_line_23 |  | 21 | 23 | 0.020258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1711-32_0_6_line_24 |  | 22 | 26 | 0.047094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1711-32_0_6_line_25 |  | 22 | 24 | 0.040212 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-32_0_6_line_26 |  | 23 | 47 | 0.030349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
27 | LV_1711-32_0_6_line_27 |  | 24 | 25 | 0.017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1711-32_0_6_line_28 |  | 26 | 27 | 0.033009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_1711-32_0_6_line_29 |  | 27 | 28 | 0.025153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1711-32_0_6_line_30 |  | 28 | 29 | 0.072378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1711-32_0_6_line_31 |  | 28 | 30 | 0.018841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-32_0_6_line_32 |  | 29 | 31 | 0.0044315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1711-32_0_6_line_33 |  | 29 | 32 | 0.0049209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1711-32_0_6_line_34 |  | 30 | 33 | 0.016887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1711-32_0_6_line_35 |  | 32 | 35 | 0.011869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1711-32_0_6_line_36 |  | 34 | 35 | 0.030355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1711-32_0_6_line_37 |  | 36 | 37 | 0.028937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1711-32_0_6_line_38 |  | 37 | 38 | 0.12696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1711-32_0_6_line_39 |  | 38 | 39 | 0.014325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1711-32_0_6_line_40 |  | 39 | 40 | 0.01509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1711-32_0_6_line_41 |  | 40 | 41 | 0.017733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1711-32_0_6_line_42 |  | 41 | 42 | 0.024443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1711-32_0_6_line_43 |  | 43 | 44 | 0.051479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1711-32_0_6_line_44 |  | 44 | 45 | 0.028067 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1711-32_0_6_line_45 |  | 45 | 48 | 0.034199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1711-32_0_6_line_46 |  | 46 | 47 | 0.045195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1711-32_0_6_line_47 |  | 47 | 50 | 0.022933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1711-32_0_6_line_48 |  | 48 | 49 | 0.02944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1711-32_0_6_line_49 |  | 49 | 51 | 0.0012184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1711-32_0_6_line_50 |  | 50 | 51 | 0.04333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-32_0_6_trafo_13 | 0.63 MVA 20/0.4 kV | 52 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2680653.0784 | 1226558.1008 | 2680663.4793 | 1226544.6215 | 2680680.7241 | 1226530.0899 | 2680688.923 | 1226527.2136
1 | 2680751.0248 | 1226510.9415 | 2680739.3431 | 1226515.4527 | 2680710.2301 | 1226519.7385 | 2680688.923 | 1226527.2136
2 | 2680751.0248 | 1226510.9415 | 2680725.2746 | 1226451.0055
3 | 2680716.1299 | 1226429.7205 | 2680725.2746 | 1226451.0055
4 | 2680716.1299 | 1226429.7205 | 2680706.8921 | 1226408.2186
5 | 2680706.8921 | 1226408.2186 | 2680705.4937 | 1226404.9637
6 | 2680572.7497 | 1226027.2311 | 2680548.5158 | 1226030.4497
7 | 2680589.3774 | 1226100.8616 | 2680580.5141 | 1226054.5325 | 2680572.7497 | 1226027.2311
8 | 2680589.3774 | 1226100.8616 | 2680616.8954 | 1226094.7079
9 | 2680589.3774 | 1226100.8616 | 2680604.3327 | 1226161.838
10 | 2680616.8954 | 1226094.7079 | 2680637.4168 | 1226090.5747
11 | 2680604.3327 | 1226161.838 | 2680608.7161 | 1226179.7102 | 2680611.2953 | 1226185.7131
12 | 2680637.4168 | 1226090.5747 | 2680643.5842 | 1226089.3325 | 2680649.3452 | 1226088.7991 | 2680653.8381 | 1226090.0942 | 2680657.4255 | 1226093.3227 | 2680661.4397 | 1226108.7502
13 | 2680638.302 | 1226248.5687 | 2680611.2953 | 1226185.7131
14 | 2680839.1646 | 1226157.6941 | 2680836.341 | 1226144.4179 | 2680837.0237 | 1226140.1286
15 | 2680842.825 | 1226174.9044 | 2680839.1646 | 1226157.6941
16 | 2680837.0237 | 1226140.1286 | 2680840.2365 | 1226119.9432 | 2680841.3165 | 1226115.8681
17 | 2680845.2712 | 1226173.9592 | 2680842.825 | 1226174.9044
18 | 2680800.4545 | 1226191.2624 | 2680842.825 | 1226174.9044
19 | 2680839.9342 | 1226099.2361 | 2680843.4487 | 1226107.823 | 2680841.3165 | 1226115.8681
20 | 2680845.2712 | 1226173.9592 | 2680847.9825 | 1226183.6248 | 2680861.5405 | 1226178.2927
21 | 2680800.4545 | 1226191.2624 | 2680804.7676 | 1226210.256 | 2680806.2727 | 1226216.7902
22 | 2680817.5567 | 1226097.5089 | 2680833.5514 | 1226099.7832 | 2680839.9342 | 1226099.2361
23 | 2680810.7191 | 1226236.5538 | 2680808.855 | 1226228.0013 | 2680806.2727 | 1226216.7902
24 | 2680771.0088 | 1226105.4935 | 2680817.5567 | 1226097.5089
25 | 2680817.5567 | 1226097.5089 | 2680810.8172 | 1226070.1877 | 2680808.6824 | 1226058.3058
26 | 2680817.1824 | 1226266.2069 | 2680810.7191 | 1226236.5538
27 | 2680805.5132 | 1226040.6656 | 2680808.6824 | 1226058.3058
28 | 2680771.0088 | 1226105.4935 | 2680761.7796 | 1226114.6856 | 2680747.6088 | 1226118.2179 | 2680742.3407 | 1226119.3028
29 | 2680719.1481 | 1226129.0392 | 2680742.3407 | 1226119.3028
30 | 2680662.5556 | 1226113.0389 | 2680704.4805 | 1226104.9462 | 2680710.5832 | 1226107.7197 | 2680719.1481 | 1226129.0392
31 | 2680719.1481 | 1226129.0392 | 2680720.3343 | 1226133.803 | 2680732.6245 | 1226140.363
32 | 2680662.5556 | 1226113.0389 | 2680661.4397 | 1226108.7502
33 | 2680662.5556 | 1226113.0389 | 2680663.5999 | 1226117.8478
34 | 2680735.659 | 1226156.974 | 2680734.5346 | 1226150.985 | 2680733.479 | 1226145.5448 | 2680732.6245 | 1226140.363
35 | 2680666.1187 | 1226129.4466 | 2680663.5999 | 1226117.8478
36 | 2680666.1187 | 1226129.4466 | 2680672.5604 | 1226159.1098
37 | 2680694.0711 | 1226378.3765 | 2680705.4937 | 1226404.9637
38 | 2680694.0711 | 1226378.3765 | 2680643.9567 | 1226261.7306
39 | 2680638.302 | 1226248.5687 | 2680643.9567 | 1226261.7306
40 | 2680638.302 | 1226248.5687 | 2680626.0821 | 1226257.4223
41 | 2680626.0821 | 1226257.4223 | 2680614.9675 | 1226265.4751 | 2680611.1117 | 1226266.5686
42 | 2680587.5959 | 1226273.2371 | 2680611.1117 | 1226266.5686
43 | 2680928.0361 | 1226306.5739 | 2680879.5562 | 1226323.8882
44 | 2680928.0361 | 1226306.5739 | 2680920.8331 | 1226279.4468
45 | 2680912.0565 | 1226246.3936 | 2680920.8331 | 1226279.4468
46 | 2680817.1824 | 1226266.2069 | 2680826.9831 | 1226310.3269
47 | 2680817.1824 | 1226266.2069 | 2680839.6309 | 1226261.5188
48 | 2680912.0565 | 1226246.3936 | 2680883.2381 | 1226252.412
49 | 2680882.0454 | 1226252.6611 | 2680883.2381 | 1226252.412
50 | 2680839.6309 | 1226261.5188 | 2680882.0454 | 1226252.6611

## bus_geodata
| x | y | coords
0 | 2680688.923 | 1226527.2136
1 | 2680653.0784 | 1226558.1008
2 | 2680751.0248 | 1226510.9415
3 | 2680725.2746 | 1226451.0055
4 | 2680716.1299 | 1226429.7205
5 | 2680706.8921 | 1226408.2186
6 | 2680548.5158 | 1226030.4497
7 | 2680572.7497 | 1226027.2311
8 | 2680589.3774 | 1226100.8616
9 | 2680616.8954 | 1226094.7079
10 | 2680604.3327 | 1226161.838
11 | 2680637.4168 | 1226090.5747
12 | 2680611.2953 | 1226185.7131
13 | 2680839.1646 | 1226157.6941
14 | 2680837.0237 | 1226140.1286
15 | 2680842.825 | 1226174.9044
16 | 2680841.3165 | 1226115.8681
17 | 2680845.2712 | 1226173.9592
18 | 2680800.4545 | 1226191.2624
19 | 2680839.9342 | 1226099.2361
20 | 2680861.5405 | 1226178.2927
21 | 2680806.2727 | 1226216.7902
22 | 2680817.5567 | 1226097.5089
23 | 2680810.7191 | 1226236.5538
24 | 2680808.6824 | 1226058.3058
25 | 2680805.5132 | 1226040.6656
26 | 2680771.0088 | 1226105.4935
27 | 2680742.3407 | 1226119.3028
28 | 2680719.1481 | 1226129.0392
29 | 2680662.5556 | 1226113.0389
30 | 2680732.6245 | 1226140.363
31 | 2680661.4397 | 1226108.7502
32 | 2680663.5999 | 1226117.8478
33 | 2680735.659 | 1226156.974
34 | 2680672.5604 | 1226159.1098
35 | 2680666.1187 | 1226129.4466
36 | 2680705.4937 | 1226404.9637
37 | 2680694.0711 | 1226378.3765
38 | 2680643.9567 | 1226261.7306
39 | 2680638.302 | 1226248.5687
40 | 2680626.0821 | 1226257.4223
41 | 2680611.1117 | 1226266.5686
42 | 2680587.5959 | 1226273.2371
43 | 2680879.5562 | 1226323.8882
44 | 2680928.0361 | 1226306.5739
45 | 2680920.8331 | 1226279.4468
46 | 2680826.9831 | 1226310.3269
47 | 2680817.1824 | 1226266.2069
48 | 2680912.0565 | 1226246.3936
49 | 2680883.2381 | 1226252.412
50 | 2680839.6309 | 1226261.5188
51 | 2680882.0454 | 1226252.6611
52 | 2680788.3219 | 1226197.1127

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97075 | -0.56546 | 0.00058843 | 0.00014747
1 | 0.97061 | -0.5682 | 0.0030686 | 0.00076906
2 | 0.97097 | -0.5611 | 0 | 0
3 | 0.97119 | -0.55668 | 0.00059518 | 0.00014917
4 | 0.97128 | -0.55486 | 0.00060199 | 0.00015087
5 | 0.97139 | -0.55276 | 0.0011668 | 0.00029243
6 | 0.97357 | -0.50951 | 0.0072158 | 0.0018085
7 | 0.97374 | -0.50627 | 0 | 0
8 | 0.97425 | -0.49625 | 0 | 0
9 | 0.97475 | -0.48638 | 0 | 0
10 | 0.97355 | -0.50998 | 0.0011682 | 0.00029277
11 | 0.97512 | -0.47904 | 0.0028114 | 0.00070461
12 | 0.9733 | -0.5149 | 0.00063314 | 0.00015868
13 | 0.9946 | -0.10237 | 0.015121 | 0.0037897
14 | 0.99321 | -0.12879 | 0.024054 | 0.0060284
15 | 0.99604 | -0.074942 | 0 | 0
16 | 0.99149 | -0.16176 | 0.01665 | 0.0041728
17 | 0.996 | -0.075758 | 0 | 0
18 | 1 | 0 | -0.494 | -0.12587
19 | 0.99035 | -0.18363 | 0 | 0
20 | 0.9956 | -0.083437 | 0.017754 | 0.0044496
21 | 0.99838 | -0.030836 | 0.026368 | 0.0066084
22 | 0.98889 | -0.21166 | 0 | 0
23 | 0.99729 | -0.051643 | 0.026346 | 0.006603
24 | 0.98799 | -0.22898 | 0.012273 | 0.0030758
25 | 0.9878 | -0.23278 | 0.011873 | 0.0029755
26 | 0.98618 | -0.2638 | 0 | 0
27 | 0.98428 | -0.30052 | 0.034392 | 0.0086194
28 | 0.98251 | -0.33485 | 0 | 0
29 | 0.97598 | -0.46216 | 0 | 0
30 | 0.98156 | -0.35347 | 0.015392 | 0.0038577
31 | 0.97589 | -0.46396 | 0.000317 | 7.9448e-05
32 | 0.97564 | -0.46887 | 0.00075787 | 0.00018994
33 | 0.98094 | -0.36548 | 0.039288 | 0.0098465
34 | 0.97276 | -0.52547 | 0.072691 | 0.018218
35 | 0.97482 | -0.48491 | 0.0010633 | 0.00026648
36 | 0.97141 | -0.55236 | 0.0013009 | 0.00032603
37 | 0.97161 | -0.54844 | 0.00061555 | 0.00015427
38 | 0.97255 | -0.52983 | 0.00041691 | 0.00010449
39 | 0.97266 | -0.52763 | 0 | 0
40 | 0.97263 | -0.52811 | 0.00042638 | 0.00010686
41 | 0.97261 | -0.52853 | 0.00017117 | 4.2899e-05
42 | 0.97259 | -0.52904 | 0.0011324 | 0.0002838
43 | 0.98389 | -0.31054 | 0.012134 | 0.0030411
44 | 0.98446 | -0.2993 | 0 | 0
45 | 0.98478 | -0.29318 | 0.033647 | 0.0084327
46 | 0.99471 | -0.10118 | 0.012134 | 0.0030411
47 | 0.9952 | -0.091528 | 0 | 0
48 | 0.98622 | -0.26508 | 0 | 0
49 | 0.98746 | -0.24095 | 0.036469 | 0.0091401
50 | 0.99231 | -0.14719 | 0.018197 | 0.0045605
51 | 0.98755 | -0.23916 | 0.037081 | 0.0092933
52 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.003069 | 0.00076872 | -0.0030686 | -0.00076906 | 4.0054e-07 | -3.4027e-07 | 0.0047041 | 0.0047044 | 0.0047044 | 0.97075 | -0.56546 | 0.97061 | -0.5682 | 1.2924
1 | -0.0036574 | -0.00091619 | 0.0036582 | 0.00091588 | 7.6049e-07 | -3.1124e-07 | 0.0056061 | 0.0056058 | 0.0056061 | 0.97075 | -0.56546 | 0.97097 | -0.5611 | 1.5401
2 | -0.0036582 | -0.00091588 | 0.0036589 | 0.00091556 | 7.687e-07 | -3.1506e-07 | 0.0056058 | 0.0056055 | 0.0056058 | 0.97097 | -0.5611 | 0.97119 | -0.55668 | 1.5401
3 | -0.0042541 | -0.0010647 | 0.0042545 | 0.0010647 | 3.6901e-07 | -5.0527e-08 | 0.0065174 | 0.0065173 | 0.0065174 | 0.97119 | -0.55668 | 0.97128 | -0.55486 | 1.7905
4 | -0.0048565 | -0.0012156 | 0.004857 | 0.0012156 | 4.8572e-07 | 2.1186e-08 | 0.0074396 | 0.0074395 | 0.0074396 | 0.97128 | -0.55486 | 0.97139 | -0.55276 | 2.0438
5 | -0.0060237 | -0.001508 | 0.0060239 | 0.001508 | 1.131e-07 | 2.8528e-08 | 0.0092268 | 0.0092268 | 0.0092268 | 0.97139 | -0.55276 | 0.97141 | -0.55236 | 2.5348
6 | -0.0072158 | -0.0018085 | 0.0072169 | 0.0018089 | 1.115e-06 | 4.0958e-07 | 0.011029 | 0.011029 | 0.011029 | 0.97357 | -0.50951 | 0.97374 | -0.50627 | 3.0299
7 | -0.0072169 | -0.0018089 | 0.0072204 | 0.0018101 | 3.4459e-06 | 1.2651e-06 | 0.011029 | 0.011028 | 0.011029 | 0.97374 | -0.50627 | 0.97425 | -0.49625 | 3.0298
8 | -0.019135 | -0.0047997 | 0.019144 | 0.0048051 | 9.0075e-06 | 5.4145e-06 | 0.029227 | 0.029227 | 0.029227 | 0.97425 | -0.49625 | 0.97475 | -0.48638 | 8.0293
9 | 0.011914 | 0.0029896 | -0.011906 | -0.0029854 | 7.7975e-06 | 4.2092e-06 | 0.018199 | 0.018199 | 0.018199 | 0.97425 | -0.49625 | 0.97355 | -0.50998 | 4.9997
10 | -0.019144 | -0.0048051 | 0.01915 | 0.0048092 | 6.7055e-06 | 4.0305e-06 | 0.029227 | 0.029227 | 0.029227 | 0.97475 | -0.48638 | 0.97512 | -0.47904 | 8.0293
11 | 0.010738 | 0.0026926 | -0.010736 | -0.0026913 | 2.5191e-06 | 1.3022e-06 | 0.016413 | 0.016413 | 0.016413 | 0.97355 | -0.50998 | 0.9733 | -0.5149 | 4.5092
12 | -0.021962 | -0.0055138 | 0.021978 | 0.0055234 | 1.5806e-05 | 9.6473e-06 | 0.033517 | 0.033517 | 0.033517 | 0.97512 | -0.47904 | 0.97589 | -0.46396 | 9.2079
13 | 0.010103 | 0.0025326 | -0.010096 | -0.0025296 | 6.1203e-06 | 3.0673e-06 | 0.015445 | 0.015446 | 0.015446 | 0.9733 | -0.5149 | 0.97266 | -0.52763 | 4.2433
14 | 0.25389 | 0.064869 | -0.25357 | -0.064662 | 0.00032388 | 0.00020658 | 0.38029 | 0.38029 | 0.38029 | 0.9946 | -0.10237 | 0.99321 | -0.12879 | 34.8247
15 | -0.26901 | -0.068658 | 0.26937 | 0.068886 | 0.00035704 | 0.00022782 | 0.40291 | 0.40291 | 0.40291 | 0.9946 | -0.10237 | 0.99604 | -0.074942 | 36.8963
16 | 0.22951 | 0.058634 | -0.22915 | -0.058401 | 0.00036523 | 0.00023279 | 0.34425 | 0.34425 | 0.34425 | 0.99321 | -0.12879 | 0.99149 | -0.16176 | 31.5247
17 | 0.017761 | 0.0044538 | -0.017761 | -0.0044534 | 6.9072e-07 | 4.0801e-07 | 0.026535 | 0.026535 | 0.026535 | 0.99604 | -0.074942 | 0.996 | -0.075758 | 7.2898
18 | -0.28713 | -0.07334 | 0.28817 | 0.074007 | 0.0010444 | 0.00066664 | 0.42944 | 0.42944 | 0.42944 | 0.99604 | -0.074942 | 1 | 0 | 39.3262
19 | 0.2125 | 0.054228 | -0.21227 | -0.054085 | 0.00022426 | 0.00014284 | 0.31926 | 0.31926 | 0.31926 | 0.99149 | -0.16176 | 0.99035 | -0.18363 | 29.2365
20 | 0.017761 | 0.0044534 | -0.017754 | -0.0044496 | 6.4973e-06 | 3.8382e-06 | 0.026535 | 0.026535 | 0.026535 | 0.996 | -0.075758 | 0.9956 | -0.083437 | 7.2898
21 | 0.20418 | 0.051868 | -0.20388 | -0.051675 | 0.00030259 | 0.00019263 | 0.30407 | 0.30407 | 0.30407 | 1 | 0 | 0.99838 | -0.030836 | 27.845
22 | 0.21227 | 0.054085 | -0.21199 | -0.053903 | 0.00028664 | 0.00018258 | 0.31926 | 0.31926 | 0.31926 | 0.99035 | -0.18363 | 0.98889 | -0.21166 | 29.2365
23 | 0.17751 | 0.045067 | -0.17733 | -0.044954 | 0.00017752 | 0.00011282 | 0.26477 | 0.26477 | 0.26477 | 0.99838 | -0.030836 | 0.99729 | -0.051643 | 24.2462
24 | 0.18782 | 0.047838 | -0.18735 | -0.047538 | 0.00047111 | 0.00029971 | 0.28289 | 0.2829 | 0.2829 | 0.98889 | -0.21166 | 0.98618 | -0.2638 | 25.9062
25 | 0.024167 | 0.0060648 | -0.024147 | -0.0060525 | 1.9945e-05 | 1.225e-05 | 0.036368 | 0.036369 | 0.036369 | 0.98889 | -0.21166 | 0.98799 | -0.22898 | 9.9914
26 | 0.15098 | 0.038351 | -0.1507 | -0.038167 | 0.00028926 | 0.00018433 | 0.22546 | 0.22546 | 0.22546 | 0.99729 | -0.051643 | 0.9952 | -0.091528 | 30.9696
27 | 0.011875 | 0.0029767 | -0.011873 | -0.0029755 | 2.1498e-06 | 1.1464e-06 | 0.017885 | 0.017885 | 0.017885 | 0.98799 | -0.22898 | 0.9878 | -0.23278 | 4.9134
28 | 0.18735 | 0.047538 | -0.18702 | -0.047328 | 0.00033021 | 0.00021008 | 0.2829 | 0.2829 | 0.2829 | 0.98618 | -0.2638 | 0.98428 | -0.30052 | 25.9062
29 | 0.15263 | 0.038709 | -0.15238 | -0.038548 | 0.00025145 | 0.00016029 | 0.2309 | 0.2309 | 0.2309 | 0.98428 | -0.30052 | 0.98251 | -0.33485 | 31.7174
30 | 0.097624 | 0.024799 | -0.09703 | -0.02442 | 0.00059429 | 0.00037943 | 0.14797 | 0.14797 | 0.14797 | 0.98251 | -0.33485 | 0.97598 | -0.46216 | 40.6517
31 | 0.054752 | 0.013749 | -0.054703 | -0.013718 | 4.8592e-05 | 3.086e-05 | 0.082931 | 0.082931 | 0.082931 | 0.98251 | -0.33485 | 0.98156 | -0.35347 | 22.7834
32 | 0.022297 | 0.005604 | -0.022295 | -0.0056029 | 1.9211e-06 | 1.1741e-06 | 0.034 | 0.034 | 0.034 | 0.97598 | -0.46216 | 0.97589 | -0.46396 | 9.3406
33 | 0.074733 | 0.018816 | -0.074709 | -0.0188 | 2.3971e-05 | 1.528e-05 | 0.11397 | 0.11397 | 0.11397 | 0.97598 | -0.46216 | 0.97564 | -0.46887 | 31.3111
34 | 0.039311 | 0.0098607 | -0.039288 | -0.0098465 | 2.2492e-05 | 1.4182e-05 | 0.059597 | 0.059597 | 0.059597 | 0.98156 | -0.35347 | 0.98094 | -0.36548 | 16.3728
35 | 0.073951 | 0.01861 | -0.073895 | -0.018574 | 5.6649e-05 | 3.6108e-05 | 0.11282 | 0.11282 | 0.11282 | 0.97564 | -0.46887 | 0.97482 | -0.48491 | 30.9935
36 | -0.072691 | -0.018218 | 0.072832 | 0.018308 | 0.00014074 | 8.9695e-05 | 0.11119 | 0.11119 | 0.11119 | 0.97276 | -0.52547 | 0.97482 | -0.48491 | 30.5477
37 | -0.0073247 | -0.0018341 | 0.0073261 | 0.0018346 | 1.3659e-06 | 5.1589e-07 | 0.011219 | 0.011219 | 0.011219 | 0.97141 | -0.55236 | 0.97161 | -0.54844 | 3.0823
38 | -0.0079416 | -0.0019888 | 0.0079487 | 0.0019918 | 7.0417e-06 | 2.9329e-06 | 0.012162 | 0.012162 | 0.012162 | 0.97161 | -0.54844 | 0.97255 | -0.52983 | 3.3412
39 | -0.0083656 | -0.0020963 | 0.0083665 | 0.0020966 | 8.8005e-07 | 3.8546e-07 | 0.012799 | 0.012799 | 0.012799 | 0.97255 | -0.52983 | 0.97266 | -0.52763 | 3.5163
40 | 0.00173 | 0.00043291 | -0.00173 | -0.00043307 | 3.9633e-08 | -1.6192e-07 | 0.0026464 | 0.0026465 | 0.0026465 | 0.97266 | -0.52763 | 0.97263 | -0.52811 | 0.72706
41 | 0.0013036 | 0.00032621 | -0.0013036 | -0.00032641 | 2.6446e-08 | -2.0316e-07 | 0.0019942 | 0.0019943 | 0.0019943 | 0.97263 | -0.52811 | 0.97261 | -0.52853 | 0.54787
42 | 0.0011324 | 0.00028352 | -0.0011324 | -0.0002838 | 2.7511e-08 | -2.8574e-07 | 0.0017324 | 0.0017325 | 0.0017325 | 0.97261 | -0.52853 | 0.97259 | -0.52904 | 0.47596
43 | -0.012134 | -0.0030411 | 0.012141 | 0.0030446 | 6.5014e-06 | 3.5067e-06 | 0.018352 | 0.018351 | 0.018352 | 0.98389 | -0.31054 | 0.98446 | -0.2993 | 5.0417
44 | -0.012141 | -0.0030446 | 0.012144 | 0.0030465 | 3.5446e-06 | 1.9115e-06 | 0.018351 | 0.018351 | 0.018351 | 0.98446 | -0.2993 | 0.98478 | -0.29318 | 5.0416
45 | -0.045791 | -0.011479 | 0.045853 | 0.011518 | 6.1398e-05 | 3.8859e-05 | 0.069192 | 0.069192 | 0.069192 | 0.98478 | -0.29318 | 0.98622 | -0.26508 | 19.0089
46 | -0.012134 | -0.0030411 | 0.01214 | 0.0030441 | 5.5843e-06 | 2.987e-06 | 0.018152 | 0.018152 | 0.018152 | 0.99471 | -0.10118 | 0.9952 | -0.091528 | 4.9868
47 | 0.13856 | 0.035123 | -0.13819 | -0.034886 | 0.00036959 | 0.00023624 | 0.20731 | 0.20731 | 0.20731 | 0.9952 | -0.091528 | 0.99231 | -0.14719 | 56.9525
48 | -0.045853 | -0.011518 | 0.045906 | 0.011552 | 5.2855e-05 | 3.3451e-05 | 0.069192 | 0.069192 | 0.069192 | 0.98622 | -0.26508 | 0.98746 | -0.24095 | 19.0089
49 | -0.082375 | -0.020692 | 0.082382 | 0.020696 | 7.0422e-06 | 4.4914e-06 | 0.12415 | 0.12415 | 0.12415 | 0.98746 | -0.24095 | 0.98755 | -0.23916 | 34.1067
50 | 0.11999 | 0.030326 | -0.11946 | -0.029989 | 0.00052657 | 0.00033645 | 0.18002 | 0.18002 | 0.18002 | 0.99231 | -0.14719 | 0.98755 | -0.23916 | 49.4562

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.494 | 0.12587

## res_load
| p_mw | q_mvar
0 | 0.00058843 | 0.00014747
1 | 0.0030686 | 0.00076906
2 | 0.00059518 | 0.00014917
3 | 0.00060199 | 0.00015087
4 | 0.0011668 | 0.00029243
5 | 0.0072158 | 0.0018085
6 | 0.0011682 | 0.00029277
7 | 0.0028114 | 0.00070461
8 | 0.00063314 | 0.00015868
9 | 0.015121 | 0.0037897
10 | 0.024054 | 0.0060284
11 | 0.01665 | 0.0041728
12 | 0.017754 | 0.0044496
13 | 0.026368 | 0.0066084
14 | 0.026346 | 0.006603
15 | 0.012273 | 0.0030758
16 | 0.011873 | 0.0029755
17 | 0.034392 | 0.0086194
18 | 0.015392 | 0.0038577
19 | 0.000317 | 7.9448e-05
20 | 0.00075787 | 0.00018994
21 | 0.039288 | 0.0098465
22 | 0.072691 | 0.018218
23 | 0.0010633 | 0.00026648
24 | 0.0013009 | 0.00032603
25 | 0.00061555 | 0.00015427
26 | 0.00041691 | 0.00010449
27 | 0.00042638 | 0.00010686
28 | 0.00017117 | 4.2899e-05
29 | 0.0011324 | 0.0002838
30 | 0.012134 | 0.0030411
31 | 0.033647 | 0.0084327
32 | 0.012134 | 0.0030411
33 | 0.036469 | 0.0091401
34 | 0.018197 | 0.0045605
35 | 0.037081 | 0.0092933

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1