## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-42_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-42_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-42_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1711-42_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1711-42_0_4_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_1711-42_0_4_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1711-42_0_4_node_28 | 0.4 | n |  | TRUE
7 | bus_LV_1711-42_0_4_node_30 | 0.4 | n |  | TRUE
8 | bus_LV_1711-42_0_4_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_1711-42_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_1711-42_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_1711-42_0_4_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1711-42_0_4_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1711-42_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_1711-42_0_4_node_16 | 0.4 | n |  | TRUE
15 | bus_LV_1711-42_0_4_node_35 | 0.4 | n |  | TRUE
16 | bus_LV_1711-42_0_4_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_1711-42_0_4_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_1711-42_0_4_node_24 | 0.4 | n |  | TRUE
19 | bus_LV_1711-42_0_4_node_23 | 0.4 | n |  | TRUE
20 | bus_LV_1711-42_0_4_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_1711-42_0_4_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_1711-42_0_4_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_1711-42_0_4_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_1711-42_0_4_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_1711-42_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_1711-42_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_1711-42_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_1711-42_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_1711-42_0_4_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_1711-42_0_4_node_39 | 0.4 | n |  | TRUE
31 | bus_LV_1711-42_0_4_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1711-42_0_4_node_38 | 0.4 | n |  | TRUE
33 | bus_LV_1711-42_0_4_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_1711-42_0_4_node_32 | 0.4 | n |  | TRUE
35 | bus_MV_228_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-42_0_4_load_0 | 0 | 0.017642 | 0.0044214 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-42_0_4_load_1 | 1 | 0.011841 | 0.0029676 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-42_0_4_load_2 | 2 | 0.022468 | 0.005631 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-42_0_4_load_3 | 3 | 0.015596 | 0.0039088 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-42_0_4_load_14 | 4 | 0.010205 | 0.0025576 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-42_0_4_load_15 | 5 | 0.0094196 | 0.0023608 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-42_0_4_load_30 | 7 | 0.0132 | 0.0033082 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-42_0_4_load_29 | 8 | 0.01751 | 0.0043883 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-42_0_4_load_5 | 9 | 0.019791 | 0.0049601 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-42_0_4_load_12 | 11 | 0.031918 | 0.0079994 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-42_0_4_load_13 | 12 | 0.012915 | 0.0032369 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-42_0_4_load_16 | 14 | 0.01219 | 0.0030552 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-42_0_4_load_24 | 18 | 0.0052028 | 0.0013039 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-42_0_4_load_23 | 19 | 0.020591 | 0.0051607 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-42_0_4_load_26 | 20 | 0.0056292 | 0.0014108 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-42_0_4_load_34 | 22 | 0.0094479 | 0.0023679 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-42_0_4_load_33 | 23 | 0.011367 | 0.0028489 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-42_0_4_load_37 | 24 | 0.019684 | 0.0049333 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-42_0_4_load_18 | 25 | 0.014851 | 0.0037221 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-42_0_4_load_19 | 26 | 0.0087056 | 0.0021818 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-42_0_4_load_20 | 27 | 0.012673 | 0.003176 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-42_0_4_load_22 | 29 | 0.02867 | 0.0071855 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-42_0_4_load_39 | 30 | 0.010922 | 0.0027373 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-42_0_4_load_27 | 31 | 0.014164 | 0.00355 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-42_0_4_load_38 | 32 | 0.010375 | 0.0026001 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-42_0_4_load_31 | 33 | 0.018567 | 0.0046533 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-42_0_4_load_32 | 34 | 0.0074156 | 0.0018585 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 5 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-42_0_4_line_0 |  | 0 | 1 | 0.0052008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-42_0_4_line_1 |  | 0 | 2 | 0.0053482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-42_0_4_line_2 |  | 1 | 3 | 0.0028684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-42_0_4_line_3 |  | 3 | 4 | 0.0038676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-42_0_4_line_4 |  | 4 | 5 | 0.0057383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-42_0_4_line_5 |  | 5 | 23 | 0.0058448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_1711-42_0_4_line_6 |  | 6 | 7 | 0.012298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-42_0_4_line_7 |  | 6 | 8 | 0.0078958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-42_0_4_line_8 |  | 7 | 33 | 0.00026272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-42_0_4_line_9 |  | 9 | 10 | 0.013019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-42_0_4_line_10 |  | 10 | 11 | 0.015641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_1711-42_0_4_line_11 |  | 10 | 12 | 0.010546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_1711-42_0_4_line_12 |  | 11 | 13 | 0.011602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_1711-42_0_4_line_13 |  | 12 | 15 | 0.0095867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_1711-42_0_4_line_14 |  | 13 | 14 | 0.014584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_1711-42_0_4_line_15 |  | 14 | 16 | 0.0079017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1711-42_0_4_line_16 |  | 15 | 22 | 0.0016946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_1711-42_0_4_line_17 |  | 16 | 17 | 0.005412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_1711-42_0_4_line_18 |  | 17 | 24 | 0.015442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_1711-42_0_4_line_19 |  | 18 | 19 | 0.00025485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-42_0_4_line_20 |  | 19 | 28 | 0.011438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-42_0_4_line_21 |  | 20 | 21 | 0.0055041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-42_0_4_line_22 |  | 21 | 31 | 0.0087962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1711-42_0_4_line_23 |  | 21 | 28 | 0.00681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1711-42_0_4_line_24 |  | 22 | 23 | 0.0056341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_1711-42_0_4_line_25 |  | 24 | 31 | 0.011036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1711-42_0_4_line_26 |  | 25 | 26 | 0.0057766 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1711-42_0_4_line_27 |  | 25 | 27 | 0.0096828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1711-42_0_4_line_28 |  | 26 | 28 | 0.008688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
29 | LV_1711-42_0_4_line_29 |  | 27 | 29 | 0.00030164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_1711-42_0_4_line_30 |  | 29 | 30 | 0.0083366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1711-42_0_4_line_31 |  | 30 | 32 | 0.00030581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-42_0_4_line_32 |  | 32 | 34 | 0.0043491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_1711-42_0_4_line_33 |  | 33 | 34 | 0.0054354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-42_0_4_trafo_15 | 0.63 MVA 20/0.4 kV | 35 | 5 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2681581.1274 | 1224455.6336 | 2681578.8464 | 1224450.9598
1 | 2681581.1274 | 1224455.6336 | 2681583.473 | 1224460.44
2 | 2681578.8464 | 1224450.9598 | 2681577.5883 | 1224448.3819
3 | 2681575.8921 | 1224444.9061 | 2681577.5883 | 1224448.3819
4 | 2681575.8921 | 1224444.9061 | 2681573.3753 | 1224439.7491
5 | 2681573.3753 | 1224439.7491 | 2681570.8119 | 1224434.4965
6 | 2681610.4782 | 1224461.1203 | 2681612.6773 | 1224458.9045 | 2681613.2924 | 1224455.5218 | 2681611.6222 | 1224450.0322
7 | 2681610.4782 | 1224461.1203 | 2681616.7598 | 1224463.1078 | 2681617.9149 | 1224463.72
8 | 2681611.5457 | 1224449.7808 | 2681611.6222 | 1224450.0322
9 | 2681549.0934 | 1224435.8065 | 2681551.1974 | 1224439.9715 | 2681553.64 | 1224447.9591
10 | 2681549.0934 | 1224435.8065 | 2681544.469 | 1224437.3776 | 2681540.887 | 1224427.2347
11 | 2681549.0934 | 1224435.8065 | 2681552.8272 | 1224433.9231 | 2681558.6916 | 1224431.4514
12 | 2681537.0235 | 1224416.2947 | 2681540.887 | 1224427.2347
13 | 2681567.5976 | 1224427.9103 | 2681563.6346 | 1224429.3681 | 2681558.6916 | 1224431.4514
14 | 2681537.0235 | 1224416.2947 | 2681545.5452 | 1224413.0759 | 2681550.5924 | 1224410.9564
15 | 2681557.8778 | 1224407.8969 | 2681550.5924 | 1224410.9564
16 | 2681567.5976 | 1224427.9103 | 2681568.3409 | 1224429.4332
17 | 2681560.1306 | 1224412.82 | 2681557.8778 | 1224407.8969
18 | 2681560.1306 | 1224412.82 | 2681573.0351 | 1224407.9602 | 2681574.6876 | 1224407.9174
19 | 2681606.9282 | 1224405.1807 | 2681607.1622 | 1224405.0796
20 | 2681596.427 | 1224409.7152 | 2681605.6112 | 1224405.7496 | 2681606.9282 | 1224405.1807
21 | 2681593.7985 | 1224403.4305 | 2681591.3675 | 1224398.4924
22 | 2681593.7985 | 1224403.4305 | 2681585.4764 | 1224406.2794
23 | 2681596.427 | 1224409.7152 | 2681593.7985 | 1224403.4305
24 | 2681570.8119 | 1224434.4965 | 2681568.3409 | 1224429.4332
25 | 2681574.6876 | 1224407.9174 | 2681581.182 | 1224407.7494 | 2681585.4764 | 1224406.2794
26 | 2681599.7975 | 1224417.7228 | 2681602.0384 | 1224423.047
27 | 2681605.7948 | 1224431.9714 | 2681602.0384 | 1224423.047
28 | 2681596.427 | 1224409.7152 | 2681599.7975 | 1224417.7228
29 | 2681605.7948 | 1224431.9714 | 2681605.9118 | 1224432.2495
30 | 2681605.9118 | 1224432.2495 | 2681606.9944 | 1224434.8215 | 2681608.6087 | 1224440.1274
31 | 2681608.6087 | 1224440.1274 | 2681608.6977 | 1224440.42
32 | 2681608.6977 | 1224440.42 | 2681609.9636 | 1224444.5807
33 | 2681611.5457 | 1224449.7808 | 2681609.9636 | 1224444.5807

## bus_geodata
| x | y | coords
0 | 2681581.1274 | 1224455.6336
1 | 2681578.8464 | 1224450.9598
2 | 2681583.473 | 1224460.44
3 | 2681577.5883 | 1224448.3819
4 | 2681575.8921 | 1224444.9061
5 | 2681573.3753 | 1224439.7491
6 | 2681610.4782 | 1224461.1203
7 | 2681611.6222 | 1224450.0322
8 | 2681617.9149 | 1224463.72
9 | 2681553.64 | 1224447.9591
10 | 2681549.0934 | 1224435.8065
11 | 2681540.887 | 1224427.2347
12 | 2681558.6916 | 1224431.4514
13 | 2681537.0235 | 1224416.2947
14 | 2681550.5924 | 1224410.9564
15 | 2681567.5976 | 1224427.9103
16 | 2681557.8778 | 1224407.8969
17 | 2681560.1306 | 1224412.82
18 | 2681607.1621 | 1224405.0796
19 | 2681606.9282 | 1224405.1807
20 | 2681591.3675 | 1224398.4924
21 | 2681593.7985 | 1224403.4305
22 | 2681568.3409 | 1224429.4332
23 | 2681570.8119 | 1224434.4965
24 | 2681574.6876 | 1224407.9174
25 | 2681602.0384 | 1224423.047
26 | 2681599.7975 | 1224417.7228
27 | 2681605.7948 | 1224431.9714
28 | 2681596.427 | 1224409.7152
29 | 2681605.9118 | 1224432.2495
30 | 2681608.6087 | 1224440.1274
31 | 2681585.4764 | 1224406.2794
32 | 2681608.6977 | 1224440.42
33 | 2681611.5457 | 1224449.7808
34 | 2681609.9636 | 1224444.5807
35 | 2681567.5976 | 1224427.9103

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99903 | -0.018581 | 0.017642 | 0.0044214
1 | 0.99922 | -0.014939 | 0.011841 | 0.0029676
2 | 0.99892 | -0.02068 | 0.022468 | 0.005631
3 | 0.99936 | -0.012338 | 0.015596 | 0.0039088
4 | 0.9996 | -0.0077796 | 0.010205 | 0.0025576
5 | 1 | 0 | -0.38762 | -0.097674
6 | 0.98717 | -0.24701 | 0 | 0
7 | 0.98737 | -0.24316 | 0.0132 | 0.0033082
8 | 0.98705 | -0.24948 | 0.01751 | 0.0043883
9 | 0.99686 | -0.060051 | 0.019791 | 0.0049601
10 | 0.99709 | -0.055532 | 0 | 0
11 | 0.99589 | -0.078619 | 0.031918 | 0.0079994
12 | 0.99797 | -0.03878 | 0.012915 | 0.0032369
13 | 0.99511 | -0.093607 | 0 | 0
14 | 0.99412 | -0.11248 | 0.01219 | 0.0030552
15 | 0.9988 | -0.022855 | 0 | 0
16 | 0.99362 | -0.12216 | 0 | 0
17 | 0.99328 | -0.12879 | 0 | 0
18 | 0.99057 | -0.18114 | 0.0052028 | 0.0013039
19 | 0.99057 | -0.18111 | 0.020591 | 0.0051607
20 | 0.99116 | -0.16963 | 0.0056292 | 0.0014108
21 | 0.99119 | -0.16908 | 0 | 0
22 | 0.99895 | -0.020043 | 0.0094479 | 0.0023679
23 | 0.99945 | -0.01039 | 0.011367 | 0.0028489
24 | 0.99229 | -0.14774 | 0.019684 | 0.0049333
25 | 0.98956 | -0.20069 | 0.014851 | 0.0037221
26 | 0.99027 | -0.1869 | 0.0087056 | 0.0021818
27 | 0.9885 | -0.22128 | 0.012673 | 0.003176
28 | 0.99084 | -0.17587 | 0 | 0
29 | 0.98847 | -0.22185 | 0.02867 | 0.0071855
30 | 0.98787 | -0.23345 | 0.010922 | 0.0027373
31 | 0.99166 | -0.16002 | 0.014164 | 0.00355
32 | 0.98785 | -0.23382 | 0.010375 | 0.0026001
33 | 0.98738 | -0.24301 | 0.018567 | 0.0046533
34 | 0.98762 | -0.23823 | 0.0074156 | 0.0018585
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.040112 | -0.010054 | 0.040119 | 0.010058 | 6.9615e-06 | 4.3873e-06 | 0.059745 | 0.059745 | 0.059745 | 0.99903 | -0.018581 | 0.99922 | -0.014939 | 16.4135
1 | 0.02247 | 0.0056324 | -0.022468 | -0.005631 | 2.2466e-06 | 1.3678e-06 | 0.033469 | 0.033469 | 0.033469 | 0.99903 | -0.018581 | 0.99892 | -0.02068 | 9.1947
2 | -0.05196 | -0.013026 | 0.051966 | 0.01303 | 6.4405e-06 | 4.0843e-06 | 0.077378 | 0.077378 | 0.077378 | 0.99922 | -0.014939 | 0.99936 | -0.012338 | 21.2578
3 | -0.067562 | -0.016939 | 0.067577 | 0.016948 | 1.4678e-05 | 9.3434e-06 | 0.1006 | 0.1006 | 0.1006 | 0.99936 | -0.012338 | 0.9996 | -0.0077796 | 27.6375
4 | -0.077782 | -0.019506 | 0.077811 | 0.019524 | 2.8852e-05 | 1.839e-05 | 0.11579 | 0.11579 | 0.11579 | 0.9996 | -0.0077796 | 1 | 0 | 31.8109
5 | 0.30816 | 0.07815 | -0.30801 | -0.078052 | 0.00015384 | 9.8226e-05 | 0.45887 | 0.45887 | 0.45887 | 1 | 0 | 0.99945 | -0.01039 | 42.0214
6 | -0.017512 | -0.0043895 | 0.017515 | 0.0043914 | 3.2134e-06 | 1.8993e-06 | 0.026396 | 0.026396 | 0.026396 | 0.98717 | -0.24701 | 0.98737 | -0.24316 | 7.2518
7 | 0.017512 | 0.0043895 | -0.01751 | -0.0043883 | 2.0631e-06 | 1.2195e-06 | 0.026396 | 0.026397 | 0.026397 | 0.98717 | -0.24701 | 0.98705 | -0.24948 | 7.2518
8 | -0.030715 | -0.0076996 | 0.030715 | 0.0076997 | 2.111e-07 | 1.3174e-07 | 0.046289 | 0.046289 | 0.046289 | 0.98737 | -0.24316 | 0.98738 | -0.24301 | 12.7168
9 | -0.019791 | -0.0049601 | 0.019795 | 0.0049627 | 4.2608e-06 | 2.5572e-06 | 0.029542 | 0.029542 | 0.029542 | 0.99686 | -0.060051 | 0.99709 | -0.055532 | 8.116
10 | 0.25387 | 0.064242 | -0.25359 | -0.064063 | 0.00028095 | 0.00017919 | 0.37908 | 0.37908 | 0.37908 | 0.99709 | -0.055532 | 0.99589 | -0.078619 | 34.7141
11 | -0.27366 | -0.069205 | 0.27388 | 0.069345 | 0.00022011 | 0.00014046 | 0.40862 | 0.40862 | 0.40862 | 0.99709 | -0.055532 | 0.99797 | -0.03878 | 37.4194
12 | 0.22167 | 0.056064 | -0.22151 | -0.055962 | 0.00015926 | 0.00010148 | 0.33139 | 0.33139 | 0.33139 | 0.99589 | -0.078619 | 0.99511 | -0.093607 | 30.3468
13 | -0.2868 | -0.072582 | 0.28702 | 0.072722 | 0.00021939 | 0.00014003 | 0.42788 | 0.42788 | 0.42788 | 0.99797 | -0.03878 | 0.9988 | -0.022855 | 39.1829
14 | 0.22151 | 0.055962 | -0.22131 | -0.055835 | 0.00020019 | 0.00012755 | 0.33139 | 0.33139 | 0.33139 | 0.99511 | -0.093607 | 0.99412 | -0.11248 | 30.3468
15 | 0.20912 | 0.05278 | -0.20902 | -0.052718 | 9.6852e-05 | 6.1678e-05 | 0.31314 | 0.31314 | 0.31314 | 0.99412 | -0.11248 | 0.99362 | -0.12216 | 28.6759
16 | -0.28702 | -0.072722 | 0.28706 | 0.072747 | 3.8781e-05 | 2.4753e-05 | 0.42788 | 0.42788 | 0.42788 | 0.9988 | -0.022855 | 0.99895 | -0.020043 | 39.1828
17 | 0.20902 | 0.052718 | -0.20895 | -0.052676 | 6.6336e-05 | 4.2245e-05 | 0.31314 | 0.31314 | 0.31314 | 0.99362 | -0.12216 | 0.99328 | -0.12879 | 28.6759
18 | 0.20895 | 0.052676 | -0.20877 | -0.052555 | 0.00018928 | 0.00012054 | 0.31314 | 0.31314 | 0.31314 | 0.99328 | -0.12879 | 0.99229 | -0.14774 | 28.676
19 | -0.0052028 | -0.0013039 | 0.0052028 | 0.0013039 | 5.8375e-09 | 4.5573e-10 | 0.0078155 | 0.0078155 | 0.0078155 | 0.99057 | -0.18114 | 0.99057 | -0.18111 | 2.1471
20 | -0.025794 | -0.0064646 | 0.025801 | 0.0064686 | 6.44e-06 | 3.9743e-06 | 0.038748 | 0.038748 | 0.038748 | 0.99057 | -0.18111 | 0.99084 | -0.17587 | 10.645
21 | -0.0056292 | -0.0014108 | 0.0056293 | 0.0014108 | 1.4741e-07 | 2.3403e-08 | 0.008451 | 0.008451 | 0.008451 | 0.99116 | -0.16963 | 0.99119 | -0.16908 | 2.3217
22 | -0.17473 | -0.043953 | 0.17481 | 0.044001 | 7.5689e-05 | 4.8101e-05 | 0.26237 | 0.26237 | 0.26237 | 0.99119 | -0.16908 | 0.99166 | -0.16002 | 24.0266
23 | 0.1691 | 0.042542 | -0.16905 | -0.042507 | 5.4884e-05 | 3.4863e-05 | 0.25392 | 0.25392 | 0.25392 | 0.99119 | -0.16908 | 0.99084 | -0.17587 | 23.2527
24 | -0.2965 | -0.075115 | 0.29664 | 0.075203 | 0.00013756 | 8.7815e-05 | 0.44195 | 0.44195 | 0.44195 | 0.99895 | -0.020043 | 0.99945 | -0.01039 | 40.4716
25 | 0.18908 | 0.047622 | -0.18897 | -0.047551 | 0.00011097 | 7.0592e-05 | 0.28362 | 0.28362 | 0.28362 | 0.99229 | -0.14774 | 0.99166 | -0.16002 | 25.9729
26 | -0.13438 | -0.033752 | 0.13446 | 0.033809 | 8.8469e-05 | 5.6546e-05 | 0.20209 | 0.20209 | 0.20209 | 0.98956 | -0.20069 | 0.99027 | -0.1869 | 55.5193
27 | 0.11952 | 0.03003 | -0.11941 | -0.029955 | 0.00011733 | 7.4967e-05 | 0.17976 | 0.17976 | 0.17976 | 0.98956 | -0.20069 | 0.9885 | -0.22128 | 49.384
28 | -0.14317 | -0.035991 | 0.14325 | 0.036039 | 7.5421e-05 | 4.8046e-05 | 0.21517 | 0.21517 | 0.21517 | 0.99027 | -0.1869 | 0.99084 | -0.17587 | 29.5565
29 | 0.10673 | 0.026779 | -0.10673 | -0.026777 | 2.9204e-06 | 1.8652e-06 | 0.16068 | 0.16068 | 0.16068 | 0.9885 | -0.22128 | 0.98847 | -0.22185 | 44.1433
30 | 0.078061 | 0.019592 | -0.078018 | -0.019564 | 4.3178e-05 | 2.7527e-05 | 0.11752 | 0.11752 | 0.11752 | 0.98847 | -0.22185 | 0.98787 | -0.23345 | 32.2862
31 | 0.067096 | 0.016827 | -0.067095 | -0.016826 | 1.1715e-06 | 7.4583e-07 | 0.10107 | 0.10107 | 0.10107 | 0.98787 | -0.23345 | 0.98785 | -0.23382 | 27.7666
32 | 0.056721 | 0.014226 | -0.056709 | -0.014219 | 1.1906e-05 | 7.5644e-06 | 0.085443 | 0.085443 | 0.085443 | 0.98785 | -0.23382 | 0.98762 | -0.23823 | 23.4733
33 | -0.049282 | -0.012353 | 0.049293 | 0.01236 | 1.1243e-05 | 7.1262e-06 | 0.07427 | 0.07427 | 0.07427 | 0.98738 | -0.24301 | 0.98762 | -0.23823 | 20.4039

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.39704 | 0.10003

## res_load
| p_mw | q_mvar
0 | 0.017642 | 0.0044214
1 | 0.011841 | 0.0029676
2 | 0.022468 | 0.005631
3 | 0.015596 | 0.0039088
4 | 0.010205 | 0.0025576
5 | 0.0094196 | 0.0023608
6 | 0.0132 | 0.0033082
7 | 0.01751 | 0.0043883
8 | 0.019791 | 0.0049601
9 | 0.031918 | 0.0079994
10 | 0.012915 | 0.0032369
11 | 0.01219 | 0.0030552
12 | 0.0052028 | 0.0013039
13 | 0.020591 | 0.0051607
14 | 0.0056292 | 0.0014108
15 | 0.0094479 | 0.0023679
16 | 0.011367 | 0.0028489
17 | 0.019684 | 0.0049333
18 | 0.014851 | 0.0037221
19 | 0.0087056 | 0.0021818
20 | 0.012673 | 0.003176
21 | 0.02867 | 0.0071855
22 | 0.010922 | 0.0027373
23 | 0.014164 | 0.00355
24 | 0.010375 | 0.0026001
25 | 0.018567 | 0.0046533
26 | 0.0074156 | 0.0018585

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1