## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-54_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-54_0_6_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1711-54_0_6_node_14 | 0.4 | n |  | TRUE
3 | bus_LV_1711-54_0_6_node_15 | 0.4 | n |  | TRUE
4 | bus_LV_1711-54_0_6_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1711-54_0_6_node_18 | 0.4 | n |  | TRUE
6 | bus_LV_1711-54_0_6_node_17 | 0.4 | n |  | TRUE
7 | bus_LV_1711-54_0_6_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1711-54_0_6_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_1711-54_0_6_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_1711-54_0_6_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_1711-54_0_6_node_12 | 0.4 | n |  | TRUE
12 | bus_LV_1711-54_0_6_node_13 | 0.4 | n |  | TRUE
13 | bus_LV_1711-54_0_6_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_1711-54_0_6_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_1711-54_0_6_node_24 | 0.4 | n |  | TRUE
16 | bus_LV_1711-54_0_6_node_31 | 0.4 | n |  | TRUE
17 | bus_LV_1711-54_0_6_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_1711-54_0_6_node_20 | 0.4 | n |  | TRUE
19 | bus_LV_1711-54_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_1711-54_0_6_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_1711-54_0_6_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_1711-54_0_6_node_29 | 0.4 | n |  | TRUE
23 | bus_LV_1711-54_0_6_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_1711-54_0_6_node_30 | 0.4 | n |  | TRUE
25 | bus_LV_1711-54_0_6_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_1711-54_0_6_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_1711-54_0_6_node_25 | 0.4 | n |  | TRUE
28 | bus_LV_1711-54_0_6_node_28 | 0.4 | n |  | TRUE
29 | bus_MV_230_0_node_10 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-54_0_6_load_0 | 0 | 0.013926 | 0.0034902 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-54_0_6_load_14 | 2 | 0.022467 | 0.0056308 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-54_0_6_load_15 | 3 | 0.0093664 | 0.0023474 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-54_0_6_load_17 | 6 | 0.056966 | 0.014277 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-54_0_6_load_19 | 9 | 0.056874 | 0.014254 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-54_0_6_load_21 | 13 | 0.045941 | 0.011514 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-54_0_6_load_31 | 16 | 0.047233 | 0.011838 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-54_0_6_load_26 | 20 | 0.058487 | 0.014658 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-54_0_6_load_29 | 22 | 0.063044 | 0.0158 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-54_0_6_load_16 | 23 | 0.056488 | 0.014157 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-54_0_6_load_30 | 24 | 0.065 | 0.01629 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-54_0_6_load_22 | 26 | 0.045055 | 0.011292 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-54_0_6_load_28 | 28 | 0.024827 | 0.0062222 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 20 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-54_0_6_line_0 |  | 0 | 1 | 0.023414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-54_0_6_line_1 |  | 1 | 2 | 0.052187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-54_0_6_line_2 |  | 1 | 3 | 0.076574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-54_0_6_line_3 |  | 2 | 12 | 0.10265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-54_0_6_line_4 |  | 4 | 5 | 0.008447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-54_0_6_line_5 |  | 4 | 6 | 0.019975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1711-54_0_6_line_6 |  | 5 | 22 | 0.021049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-54_0_6_line_7 |  | 5 | 19 | 0.051074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_1711-54_0_6_line_8 |  | 6 | 23 | 0.0093921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-54_0_6_line_9 |  | 7 | 8 | 0.039618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-54_0_6_line_10 |  | 7 | 9 | 0.021314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1711-54_0_6_line_11 |  | 8 | 13 | 0.030326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-54_0_6_line_12 |  | 9 | 17 | 0.026633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-54_0_6_line_13 |  | 10 | 11 | 0.036601 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-54_0_6_line_14 |  | 10 | 12 | 0.033466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-54_0_6_line_15 |  | 11 | 21 | 0.02516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-54_0_6_line_16 |  | 14 | 15 | 0.040597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-54_0_6_line_17 |  | 14 | 16 | 0.029216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-54_0_6_line_18 |  | 15 | 24 | 0.01607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-54_0_6_line_19 |  | 15 | 25 | 0.009657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-54_0_6_line_20 |  | 17 | 18 | 0.010248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-54_0_6_line_21 |  | 18 | 26 | 0.030184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-54_0_6_line_22 |  | 19 | 20 | 0.011051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1711-54_0_6_line_23 |  | 20 | 27 | 0.026463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1711-54_0_6_line_24 |  | 21 | 27 | 0.030586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-54_0_6_line_25 |  | 22 | 28 | 0.016993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-54_0_6_line_26 |  | 25 | 27 | 0.043749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_1711-54_0_6_line_27 |  | 25 | 26 | 0.020566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-54_0_6_trafo_26 | 0.63 MVA 20/0.4 kV | 29 | 20 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2681228.2536 | 1226223.7853 | 2681231.3225 | 1226200.5729
1 | 2681228.2536 | 1226223.7853 | 2681238.6531 | 1226225.5284 | 2681279.9943 | 1226230.532
2 | 2681228.2536 | 1226223.7853 | 2681219.2248 | 1226288.2058 | 2681217.462 | 1226297.9439 | 2681215.995 | 1226298.6498
3 | 2681373.0914 | 1226269.5171 | 2681356.453 | 1226262.2513 | 2681332.677 | 1226248.6505 | 2681309.6943 | 1226234.1266 | 2681279.9943 | 1226230.532
4 | 2681331.6824 | 1226160.0657 | 2681335.9109 | 1226167.384
5 | 2681331.6824 | 1226160.0657 | 2681330.1873 | 1226140.1469
6 | 2681335.9109 | 1226167.384 | 2681340.0036 | 1226188.0309
7 | 2681386.9975 | 1226167.3379 | 2681365.7815 | 1226165.5132 | 2681335.9109 | 1226167.384
8 | 2681329.4843 | 1226130.7811 | 2681330.1873 | 1226140.1469
9 | 2681431.1861 | 1226093.6145 | 2681470.6941 | 1226089.3967
10 | 2681431.1861 | 1226093.6145 | 2681432.7688 | 1226114.8699
11 | 2681470.6941 | 1226089.3967 | 2681472.6757 | 1226119.6582
12 | 2681434.7464 | 1226141.429 | 2681432.7688 | 1226114.8699
13 | 2681397.0681 | 1226255.7022 | 2681393.3374 | 1226268.5266 | 2681390.792 | 1226277.2644 | 2681404.0039 | 1226282.3151
14 | 2681373.0914 | 1226269.5171 | 2681390.792 | 1226277.2644 | 2681404.0039 | 1226282.3151
15 | 2681384.6629 | 1226233.7955 | 2681397.0681 | 1226255.7022
16 | 2681438.5301 | 1226211.6728 | 2681479.109 | 1226208.3482
17 | 2681479.109 | 1226208.3482 | 2681481.2576 | 1226237.4846
18 | 2681438.5301 | 1226211.6728 | 2681444.1084 | 1226226.743
19 | 2681436.7269 | 1226202.1862 | 2681438.5301 | 1226211.6728
20 | 2681434.7464 | 1226141.429 | 2681433.2052 | 1226151.5592
21 | 2681433.2052 | 1226151.5592 | 2681435.2998 | 1226181.6702
22 | 2681386.9975 | 1226167.3379 | 2681388.7664 | 1226178.2461
23 | 2681393.0025 | 1226204.3673 | 2681388.7664 | 1226178.2461
24 | 2681393.0025 | 1226204.3673 | 2681384.6629 | 1226233.7955
25 | 2681345.4288 | 1226203.5454 | 2681345.0145 | 1226198.4739 | 2681341.0734 | 1226193.4277 | 2681340.0036 | 1226188.0309
26 | 2681393.0025 | 1226204.3673 | 2681417.0066 | 1226204.6291 | 2681436.7269 | 1226202.1862
27 | 2681436.7269 | 1226202.1862 | 2681435.2998 | 1226181.6702

## bus_geodata
| x | y | coords
0 | 2681231.3225 | 1226200.5729
1 | 2681228.2536 | 1226223.7853
2 | 2681279.9943 | 1226230.532
3 | 2681215.995 | 1226298.6498
4 | 2681331.6824 | 1226160.0657
5 | 2681335.9109 | 1226167.384
6 | 2681330.1873 | 1226140.1469
7 | 2681431.1861 | 1226093.6145
8 | 2681470.6941 | 1226089.3967
9 | 2681432.7688 | 1226114.8699
10 | 2681404.0039 | 1226282.3151
11 | 2681397.0681 | 1226255.7022
12 | 2681373.0914 | 1226269.5171
13 | 2681472.6757 | 1226119.6582
14 | 2681479.109 | 1226208.3482
15 | 2681438.5301 | 1226211.6728
16 | 2681481.2576 | 1226237.4846
17 | 2681434.7464 | 1226141.429
18 | 2681433.2052 | 1226151.5592
19 | 2681386.9975 | 1226167.3379
20 | 2681388.7664 | 1226178.2461
21 | 2681384.6629 | 1226233.7955
22 | 2681340.0036 | 1226188.0309
23 | 2681329.4843 | 1226130.7811
24 | 2681444.1084 | 1226226.743
25 | 2681436.7269 | 1226202.1862
26 | 2681435.2998 | 1226181.6702
27 | 2681393.0025 | 1226204.3673
28 | 2681345.4288 | 1226203.5454
29 | 2681386.9975 | 1226167.3379

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9865 | -0.25966 | 0.013926 | 0.0034902
1 | 0.9868 | -0.25382 | 0 | 0
2 | 0.98792 | -0.23208 | 0.022467 | 0.0056308
3 | 0.98614 | -0.26667 | 0.0093664 | 0.0023474
4 | 0.99374 | -0.11999 | 0 | 0
5 | 0.99462 | -0.10309 | 0 | 0
6 | 0.99167 | -0.16007 | 0.056966 | 0.014277
7 | 0.98539 | -0.281 | 0 | 0
8 | 0.98371 | -0.31373 | 0 | 0
9 | 0.98629 | -0.26344 | 0.056874 | 0.014254
10 | 0.99364 | -0.12147 | 0 | 0
11 | 0.99518 | -0.091943 | 0 | 0
12 | 0.99223 | -0.14855 | 0 | 0
13 | 0.98242 | -0.33885 | 0.045941 | 0.011514
14 | 0.9913 | -0.16691 | 0 | 0
15 | 0.99305 | -0.13296 | 0 | 0
16 | 0.99003 | -0.19142 | 0.047233 | 0.011838
17 | 0.98881 | -0.2145 | 0 | 0
18 | 0.98979 | -0.19573 | 0 | 0
19 | 0.99932 | -0.012935 | 0 | 0
20 | 1 | 0 | -0.51355 | -0.13012
21 | 0.99624 | -0.071699 | 0 | 0
22 | 0.99293 | -0.13573 | 0.063044 | 0.0158
23 | 0.99119 | -0.16948 | 0.056488 | 0.014157
24 | 0.9921 | -0.15144 | 0.065 | 0.01629
25 | 0.99404 | -0.11382 | 0 | 0
26 | 0.99265 | -0.14068 | 0.045055 | 0.011292
27 | 0.99752 | -0.047145 | 0 | 0
28 | 0.99255 | -0.14319 | 0.024827 | 0.0062222
29 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.013926 | -0.0034902 | 0.01393 | 0.0034923 | 3.8742e-06 | 2.1804e-06 | 0.021006 | 0.021005 | 0.021006 | 0.9865 | -0.25966 | 0.9868 | -0.25382 | 5.7707
1 | -0.023302 | -0.0058425 | 0.023326 | 0.0058573 | 2.4163e-05 | 1.4797e-05 | 0.035138 | 0.035138 | 0.035138 | 0.9868 | -0.25382 | 0.98792 | -0.23208 | 9.6534
2 | 0.0093721 | 0.0023501 | -0.0093664 | -0.0023474 | 5.7357e-06 | 2.6932e-06 | 0.014133 | 0.014133 | 0.014133 | 0.9868 | -0.25382 | 0.98614 | -0.26667 | 3.8827
3 | -0.045793 | -0.011488 | 0.045976 | 0.011604 | 0.00018315 | 0.0001159 | 0.068978 | 0.068978 | 0.068978 | 0.98792 | -0.23208 | 0.99223 | -0.14855 | 18.9501
4 | -0.1137 | -0.028589 | 0.11379 | 0.028648 | 9.1848e-05 | 5.8673e-05 | 0.17028 | 0.17028 | 0.17028 | 0.99374 | -0.11999 | 0.99462 | -0.10309 | 46.7806
5 | 0.1137 | 0.028589 | -0.11348 | -0.02845 | 0.00021719 | 0.00013875 | 0.17028 | 0.17028 | 0.17028 | 0.99374 | -0.11999 | 0.99167 | -0.16007 | 46.7807
6 | 0.088017 | 0.022115 | -0.08788 | -0.022028 | 0.0001369 | 8.7346e-05 | 0.1317 | 0.1317 | 0.1317 | 0.99462 | -0.10309 | 0.99293 | -0.13573 | 36.1809
7 | -0.20181 | -0.050763 | 0.20268 | 0.051321 | 0.00087328 | 0.00055757 | 0.30198 | 0.30198 | 0.30198 | 0.99462 | -0.10309 | 0.99932 | -0.012935 | 41.4807
8 | 0.056514 | 0.014173 | -0.056488 | -0.014157 | 2.5329e-05 | 1.6089e-05 | 0.084803 | 0.084803 | 0.084803 | 0.99167 | -0.16007 | 0.99119 | -0.16948 | 23.2975
9 | 0.046068 | 0.011594 | -0.045996 | -0.011549 | 7.1936e-05 | 4.5535e-05 | 0.069584 | 0.069584 | 0.069584 | 0.98539 | -0.281 | 0.98371 | -0.31373 | 19.1165
10 | -0.046068 | -0.011594 | 0.046107 | 0.011619 | 3.8701e-05 | 2.4497e-05 | 0.069584 | 0.069584 | 0.069584 | 0.98539 | -0.281 | 0.98629 | -0.26344 | 19.1165
11 | 0.045996 | 0.011549 | -0.045941 | -0.011514 | 5.5065e-05 | 3.4857e-05 | 0.069584 | 0.069584 | 0.069584 | 0.98371 | -0.31373 | 0.98242 | -0.33885 | 19.1166
12 | -0.10298 | -0.025873 | 0.10322 | 0.026027 | 0.00024115 | 0.000154 | 0.15539 | 0.15539 | 0.15539 | 0.98629 | -0.26344 | 0.98881 | -0.2145 | 42.6895
13 | -0.046036 | -0.011642 | 0.046101 | 0.011683 | 6.5305e-05 | 4.132e-05 | 0.068978 | 0.068978 | 0.068978 | 0.99364 | -0.12147 | 0.99518 | -0.091943 | 18.9499
14 | 0.046036 | 0.011642 | -0.045976 | -0.011604 | 5.9712e-05 | 3.7782e-05 | 0.068978 | 0.068978 | 0.068978 | 0.99364 | -0.12147 | 0.99223 | -0.14855 | 18.95
15 | -0.046101 | -0.011683 | 0.046146 | 0.011711 | 4.4891e-05 | 2.8403e-05 | 0.068978 | 0.068978 | 0.068978 | 0.99518 | -0.091943 | 0.99624 | -0.071699 | 18.9499
16 | -0.047288 | -0.011873 | 0.047365 | 0.011921 | 7.6723e-05 | 4.8579e-05 | 0.070991 | 0.070991 | 0.070991 | 0.9913 | -0.16691 | 0.99305 | -0.13296 | 19.5029
17 | 0.047288 | 0.011873 | -0.047233 | -0.011838 | 5.5214e-05 | 3.4961e-05 | 0.070991 | 0.070991 | 0.070991 | 0.9913 | -0.16691 | 0.99003 | -0.19142 | 19.503
18 | 0.065057 | 0.016327 | -0.065 | -0.01629 | 5.7275e-05 | 3.6448e-05 | 0.097491 | 0.097491 | 0.097491 | 0.99305 | -0.13296 | 0.9921 | -0.15144 | 26.7833
19 | -0.11242 | -0.028248 | 0.11252 | 0.028314 | 0.0001028 | 6.5665e-05 | 0.16848 | 0.16848 | 0.16848 | 0.99305 | -0.13296 | 0.99404 | -0.11382 | 46.2862
20 | -0.10322 | -0.026027 | 0.10332 | 0.026086 | 9.2793e-05 | 5.9256e-05 | 0.15539 | 0.15539 | 0.15539 | 0.98881 | -0.2145 | 0.98979 | -0.19573 | 42.6895
21 | -0.10332 | -0.026086 | 0.10359 | 0.026261 | 0.00027331 | 0.00017453 | 0.15539 | 0.15539 | 0.15539 | 0.98979 | -0.19573 | 0.99265 | -0.14068 | 42.6895
22 | -0.20268 | -0.051321 | 0.2028 | 0.051401 | 0.00012597 | 8.0184e-05 | 0.30198 | 0.30198 | 0.30198 | 0.99932 | -0.012935 | 1 | 0 | 27.6538
23 | 0.3091 | 0.078717 | -0.3084 | -0.078269 | 0.00070111 | 0.00044767 | 0.46039 | 0.46039 | 0.46039 | 1 | 0 | 0.99752 | -0.047145 | 42.16
24 | -0.046146 | -0.011711 | 0.046201 | 0.011746 | 5.4572e-05 | 3.4527e-05 | 0.068978 | 0.068977 | 0.068978 | 0.99624 | -0.071699 | 0.99752 | -0.047145 | 18.9499
25 | 0.024836 | 0.0062277 | -0.024827 | -0.0062222 | 8.828e-06 | 5.4302e-06 | 0.03722 | 0.03722 | 0.03722 | 0.99293 | -0.13573 | 0.99255 | -0.14319 | 10.2254
26 | -0.26136 | -0.065988 | 0.2622 | 0.066523 | 0.0008378 | 0.00053449 | 0.39141 | 0.39141 | 0.39141 | 0.99404 | -0.11382 | 0.99752 | -0.047145 | 35.8434
27 | 0.14884 | 0.037675 | -0.14864 | -0.037552 | 0.00019163 | 0.00012211 | 0.22293 | 0.22293 | 0.22293 | 0.99404 | -0.11382 | 0.99265 | -0.14068 | 30.6221

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.57204 | 0.14478

## res_load
| p_mw | q_mvar
0 | 0.013926 | 0.0034902
1 | 0.022467 | 0.0056308
2 | 0.0093664 | 0.0023474
3 | 0.056966 | 0.014277
4 | 0.056874 | 0.014254
5 | 0.045941 | 0.011514
6 | 0.047233 | 0.011838
7 | 0.058487 | 0.014658
8 | 0.063044 | 0.0158
9 | 0.056488 | 0.014157
10 | 0.065 | 0.01629
11 | 0.045055 | 0.011292
12 | 0.024827 | 0.0062222

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1