## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-65_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-65_0_5_node_2 | 0.4 | n |  | TRUE
2 | bus_LV_1711-65_0_5_node_12 | 0.4 | n |  | TRUE
3 | bus_LV_1711-65_0_5_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_1711-65_0_5_node_3 | 0.4 | n |  | TRUE
5 | bus_LV_1711-65_0_5_node_15 | 0.4 | n |  | TRUE
6 | bus_LV_1711-65_0_5_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_1711-65_0_5_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_1711-65_0_5_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_1711-65_0_5_node_27 | 0.4 | n |  | TRUE
10 | bus_LV_1711-65_0_5_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_1711-65_0_5_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_1711-65_0_5_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_1711-65_0_5_node_19 | 0.4 | n |  | TRUE
14 | bus_LV_1711-65_0_5_node_17 | 0.4 | n |  | TRUE
15 | bus_LV_1711-65_0_5_node_28 | 0.4 | n |  | TRUE
16 | bus_LV_1711-65_0_5_node_14 | 0.4 | n |  | TRUE
17 | bus_LV_1711-65_0_5_node_16 | 0.4 | n |  | TRUE
18 | bus_LV_1711-65_0_5_node_22 | 0.4 | n |  | TRUE
19 | bus_LV_1711-65_0_5_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_1711-65_0_5_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_1711-65_0_5_node_21 | 0.4 | n |  | TRUE
22 | bus_LV_1711-65_0_5_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_1711-65_0_5_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_1711-65_0_5_node_25 | 0.4 | n |  | TRUE
25 | bus_MV_231_0_node_187 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-65_0_5_load_0 | 0 | 0.014265 | 0.0035751 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-65_0_5_load_12 | 2 | 0.045171 | 0.011321 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-65_0_5_load_13 | 3 | 0.025789 | 0.0064632 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-65_0_5_load_15 | 5 | 0.034407 | 0.0086232 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-65_0_5_load_27 | 9 | 0.044989 | 0.011275 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-65_0_5_load_29 | 10 | 0.017839 | 0.004471 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-65_0_5_load_19 | 13 | 0.037968 | 0.0095156 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-65_0_5_load_17 | 14 | 0.024918 | 0.006245 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-65_0_5_load_28 | 15 | 0.010625 | 0.0026629 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-65_0_5_load_14 | 16 | 0.051672 | 0.01295 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-65_0_5_load_24 | 19 | 0.021441 | 0.0053737 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-65_0_5_load_20 | 20 | 0.039698 | 0.0099492 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-65_0_5_load_21 | 21 | 0.019823 | 0.0049681 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-65_0_5_load_25 | 24 | 0.013919 | 0.0034885 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 1 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-65_0_5_line_0 |  | 0 | 1 | 0.20002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-65_0_5_line_1 |  | 1 | 2 | 0.050906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_1711-65_0_5_line_2 |  | 1 | 3 | 0.01373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_1711-65_0_5_line_3 |  | 2 | 15 | 0.026271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-65_0_5_line_4 |  | 2 | 9 | 0.03454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-65_0_5_line_5 |  | 3 | 6 | 0.0078057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_1711-65_0_5_line_6 |  | 4 | 5 | 0.060194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-65_0_5_line_7 |  | 4 | 6 | 0.023228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-65_0_5_line_8 |  | 5 | 16 | 0.013526 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-65_0_5_line_9 |  | 6 | 14 | 0.043828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-65_0_5_line_10 |  | 7 | 8 | 0.24182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1711-65_0_5_line_11 |  | 7 | 9 | 0.036746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-65_0_5_line_12 |  | 8 | 10 | 0.07263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-65_0_5_line_13 |  | 11 | 12 | 0.065666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-65_0_5_line_14 |  | 11 | 13 | 0.021614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-65_0_5_line_15 |  | 12 | 14 | 0.052901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-65_0_5_line_16 |  | 13 | 20 | 0.027898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-65_0_5_line_17 |  | 15 | 22 | 0.021511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-65_0_5_line_18 |  | 17 | 18 | 0.033152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-65_0_5_line_19 |  | 17 | 19 | 0.020962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-65_0_5_line_20 |  | 18 | 22 | 0.00612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-65_0_5_line_21 |  | 18 | 21 | 0.023991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-65_0_5_line_22 |  | 22 | 23 | 0.037628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1711-65_0_5_line_23 |  | 23 | 24 | 0.023454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-65_0_5_trafo_2 | 0.63 MVA 20/0.4 kV | 25 | 1 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9
0 | 2679667.9627 | 1226336.1268 | 2679663.4911 | 1226348.5198 | 2679661.2396 | 1226354.7494 | 2679642.1845 | 1226363.6671 | 2679585.7368 | 1226363.4452 | 2679585.8721 | 1226380.5252 | 2679571.8052 | 1226375.8339 | 2679551.9014 | 1226367.1731 | 2679521.3692 | 1226351.7658 | 2679508.3136 | 1226344.5451
1 | 2679667.9627 | 1226336.1268 | 2679714.5453 | 1226356.9646
2 | 2679667.9627 | 1226336.1268 | 2679659.7418 | 1226332.4476 | 2679658.1295 | 1226328.0082
3 | 2679714.5453 | 1226356.9646 | 2679738.5258 | 1226367.6943
4 | 2679714.5453 | 1226356.9646 | 2679700.0433 | 1226388.3131
5 | 2679655.465 | 1226320.6713 | 2679658.1295 | 1226328.0082
6 | 2679645.9299 | 1226299.6517 | 2679645.7048 | 1226271.174 | 2679645.236 | 1226252.3995 | 2679640.9954 | 1226240.1789
7 | 2679645.9299 | 1226299.6517 | 2679649.9966 | 1226305.6102 | 2679655.465 | 1226320.6713
8 | 2679640.9954 | 1226240.1789 | 2679640.9954 | 1226240.1789 | 2679628.1817 | 1226235.849
9 | 2679655.465 | 1226320.6713 | 2679673.996 | 1226280.954
10 | 2679531.151 | 1226535.1981 | 2679568.8345 | 1226544.0522 | 2679581.975 | 1226547.1411 | 2679585.4091 | 1226540.8828 | 2679644.7934 | 1226432.6374 | 2679650.7745 | 1226417.3294 | 2679663.1175 | 1226422.8205 | 2679674.0411 | 1226427.3142 | 2679677.502 | 1226418.499 | 2679684.6154 | 1226421.663
11 | 2679684.6154 | 1226421.663 | 2679700.0433 | 1226388.3131
12 | 2679531.151 | 1226535.1981 | 2679525.4082 | 1226533.8427 | 2679521.3067 | 1226534.4549 | 2679509.1167 | 1226595.8393
13 | 2679703.2194 | 1226239.9339 | 2679731.7336 | 1226261.6861 | 2679752.8821 | 1226282.6836
14 | 2679752.8821 | 1226282.6836 | 2679744.1044 | 1226302.4349
15 | 2679703.2194 | 1226239.9339 | 2679690.4136 | 1226245.7664 | 2679673.996 | 1226280.954
16 | 2679744.1044 | 1226302.4349 | 2679769.3586 | 1226314.2901
17 | 2679758.1585 | 1226376.4843 | 2679750.4351 | 1226373.0229 | 2679738.5258 | 1226367.6943
18 | 2679763.7571 | 1226378.9944 | 2679794.0777 | 1226392.5989
19 | 2679794.0777 | 1226392.5989 | 2679803.0311 | 1226373.6447
20 | 2679763.7571 | 1226378.9944 | 2679758.1585 | 1226376.4843
21 | 2679763.7571 | 1226378.9944 | 2679775.2005 | 1226357.909
22 | 2679741.8384 | 1226410.3885 | 2679747.2811 | 1226399.076 | 2679752.404 | 1226388.4375 | 2679758.1585 | 1226376.4843
23 | 2679741.8384 | 1226410.3885 | 2679720.832 | 1226399.9561

## bus_geodata
| x | y | coords
0 | 2679508.3136 | 1226344.5451
1 | 2679667.9627 | 1226336.1268
2 | 2679714.5453 | 1226356.9646
3 | 2679658.1295 | 1226328.0082
4 | 2679645.9299 | 1226299.6517
5 | 2679640.9954 | 1226240.1789
6 | 2679655.465 | 1226320.6713
7 | 2679684.6154 | 1226421.663
8 | 2679531.151 | 1226535.1981
9 | 2679700.0433 | 1226388.3131
10 | 2679509.1167 | 1226595.8393
11 | 2679752.8821 | 1226282.6836
12 | 2679703.2194 | 1226239.9339
13 | 2679744.1044 | 1226302.4349
14 | 2679673.996 | 1226280.954
15 | 2679738.5258 | 1226367.6943
16 | 2679628.1817 | 1226235.849
17 | 2679794.0777 | 1226392.5989
18 | 2679763.7571 | 1226378.9944
19 | 2679803.0311 | 1226373.6447
20 | 2679769.3586 | 1226314.2901
21 | 2679775.2005 | 1226357.909
22 | 2679758.1585 | 1226376.4843
23 | 2679741.8384 | 1226410.3885
24 | 2679720.832 | 1226399.9561
25 | 2679655.465 | 1226320.6713

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99741 | -0.049871 | 0.014265 | 0.0035751
1 | 1 | 0 | -0.40736 | -0.10291
2 | 0.99596 | -0.077428 | 0.045171 | 0.011321
3 | 0.99865 | -0.025695 | 0.025789 | 0.0064632
4 | 0.99614 | -0.073629 | 0 | 0
5 | 0.9914 | -0.16508 | 0.034407 | 0.0086232
6 | 0.99797 | -0.038573 | 0 | 0
7 | 0.99338 | -0.12722 | 0 | 0
8 | 0.98942 | -0.20375 | 0 | 0
9 | 0.99398 | -0.11564 | 0.044989 | 0.011275
10 | 0.98823 | -0.22685 | 0.017839 | 0.004471
11 | 0.98534 | -0.28149 | 0 | 0
12 | 0.99004 | -0.19037 | 0 | 0
13 | 0.98379 | -0.31167 | 0.037968 | 0.0095156
14 | 0.99383 | -0.11759 | 0.024918 | 0.006245
15 | 0.99438 | -0.10786 | 0.010625 | 0.0026629
16 | 0.99076 | -0.17748 | 0.051672 | 0.01295
17 | 0.99242 | -0.14584 | 0 | 0
18 | 0.99307 | -0.13327 | 0 | 0
19 | 0.99201 | -0.1538 | 0.021441 | 0.0053737
20 | 0.98277 | -0.33164 | 0.039698 | 0.0099492
21 | 0.99263 | -0.14168 | 0.019823 | 0.0049681
22 | 0.9933 | -0.12881 | 0 | 0
23 | 0.99282 | -0.13806 | 0 | 0
24 | 0.99252 | -0.14384 | 0.013919 | 0.0034885
25 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.014265 | -0.0035751 | 0.014299 | 0.0035942 | 3.3969e-05 | 1.9123e-05 | 0.021281 | 0.02128 | 0.021281 | 0.99741 | -0.049871 | 1 | 0 | 5.8465
1 | 0.17486 | 0.044227 | -0.17422 | -0.043815 | 0.00064693 | 0.00041271 | 0.26034 | 0.26034 | 0.26034 | 1 | 0 | 0.99596 | -0.077428 | 35.7613
2 | 0.21655 | 0.055084 | -0.21628 | -0.054913 | 0.00026777 | 0.00017101 | 0.32251 | 0.32251 | 0.32251 | 1 | 0 | 0.99865 | -0.025695 | 44.3014
3 | 0.066007 | 0.016618 | -0.065911 | -0.016557 | 9.5866e-05 | 6.1013e-05 | 0.098645 | 0.098645 | 0.098645 | 0.99596 | -0.077428 | 0.99438 | -0.10786 | 27.1002
4 | 0.063038 | 0.015876 | -0.062923 | -0.015802 | 0.00011496 | 7.3126e-05 | 0.094209 | 0.094209 | 0.094209 | 0.99596 | -0.077428 | 0.99398 | -0.11564 | 25.8817
5 | 0.19049 | 0.04845 | -0.19037 | -0.048374 | 0.00011812 | 7.5392e-05 | 0.28409 | 0.28409 | 0.28409 | 0.99865 | -0.025695 | 0.99797 | -0.038573 | 39.0232
6 | 0.086487 | 0.021833 | -0.08611 | -0.021593 | 0.00037708 | 0.00024055 | 0.12925 | 0.12925 | 0.12925 | 0.99614 | -0.073629 | 0.9914 | -0.16508 | 35.5077
7 | -0.086487 | -0.021833 | 0.086632 | 0.021926 | 0.00014551 | 9.2823e-05 | 0.12925 | 0.12925 | 0.12925 | 0.99614 | -0.073629 | 0.99797 | -0.038573 | 35.5077
8 | 0.051703 | 0.01297 | -0.051672 | -0.01295 | 3.0547e-05 | 1.9376e-05 | 0.077606 | 0.077606 | 0.077606 | 0.9914 | -0.16508 | 0.99076 | -0.17748 | 21.3203
9 | 0.10374 | 0.026448 | -0.10335 | -0.026197 | 0.00039405 | 0.00025162 | 0.15484 | 0.15484 | 0.15484 | 0.99797 | -0.038573 | 0.99383 | -0.11759 | 42.5388
10 | 0.017924 | 0.0045214 | -0.017859 | -0.0044826 | 6.5427e-05 | 3.8755e-05 | 0.02686 | 0.026861 | 0.026861 | 0.99338 | -0.12722 | 0.98942 | -0.20375 | 7.3794
11 | -0.017924 | -0.0045214 | 0.017934 | 0.0045272 | 9.9413e-06 | 5.8864e-06 | 0.02686 | 0.02686 | 0.02686 | 0.99338 | -0.12722 | 0.99398 | -0.11564 | 7.3791
12 | 0.017859 | 0.0044826 | -0.017839 | -0.004471 | 1.9652e-05 | 1.1645e-05 | 0.026861 | 0.026861 | 0.026861 | 0.98942 | -0.20375 | 0.98823 | -0.22685 | 7.3795
13 | -0.077815 | -0.01956 | 0.078155 | 0.019777 | 0.00034017 | 0.00021687 | 0.11753 | 0.11753 | 0.11753 | 0.98534 | -0.28149 | 0.99004 | -0.19037 | 32.2895
14 | 0.077815 | 0.01956 | -0.077703 | -0.019489 | 0.00011197 | 7.1384e-05 | 0.11753 | 0.11753 | 0.11753 | 0.98534 | -0.28149 | 0.98379 | -0.31167 | 32.2895
15 | -0.078155 | -0.019777 | 0.078429 | 0.019952 | 0.00027404 | 0.0001747 | 0.11753 | 0.11753 | 0.11753 | 0.99004 | -0.19037 | 0.99383 | -0.11759 | 32.2894
16 | 0.039736 | 0.0099731 | -0.039698 | -0.0099492 | 3.7797e-05 | 2.3836e-05 | 0.060107 | 0.060107 | 0.060107 | 0.98379 | -0.31167 | 0.98277 | -0.33164 | 16.5129
17 | 0.055286 | 0.013894 | -0.055231 | -0.013859 | 5.523e-05 | 3.5068e-05 | 0.082745 | 0.082745 | 0.082745 | 0.99438 | -0.10786 | 0.9933 | -0.12881 | 22.7322
18 | -0.021449 | -0.0053786 | 0.021462 | 0.0053864 | 1.2859e-05 | 7.8014e-06 | 0.032162 | 0.032162 | 0.032162 | 0.99242 | -0.14584 | 0.99307 | -0.13327 | 8.8357
19 | 0.021449 | 0.0053786 | -0.021441 | -0.0053737 | 8.1312e-06 | 4.9332e-06 | 0.032162 | 0.032162 | 0.032162 | 0.99242 | -0.14584 | 0.99201 | -0.1538 | 8.8357
20 | -0.041293 | -0.010359 | 0.041302 | 0.010365 | 8.7871e-06 | 5.5446e-06 | 0.061877 | 0.061877 | 0.061877 | 0.99307 | -0.13327 | 0.9933 | -0.12881 | 16.9993
21 | 0.019831 | 0.0049729 | -0.019823 | -0.0049681 | 7.9441e-06 | 4.774e-06 | 0.029716 | 0.029716 | 0.029716 | 0.99307 | -0.13327 | 0.99263 | -0.14168 | 8.1637
22 | 0.013929 | 0.0034941 | -0.013923 | -0.0034907 | 6.1447e-06 | 3.4458e-06 | 0.020868 | 0.020868 | 0.020868 | 0.9933 | -0.12881 | 0.99282 | -0.13806 | 5.733
23 | 0.013923 | 0.0034907 | -0.013919 | -0.0034885 | 3.8302e-06 | 2.1481e-06 | 0.020868 | 0.020868 | 0.020868 | 0.99282 | -0.13806 | 0.99252 | -0.14384 | 5.733

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.40736 | 0.10291

## res_load
| p_mw | q_mvar
0 | 0.014265 | 0.0035751
1 | 0.045171 | 0.011321
2 | 0.025789 | 0.0064632
3 | 0.034407 | 0.0086232
4 | 0.044989 | 0.011275
5 | 0.017839 | 0.004471
6 | 0.037968 | 0.0095156
7 | 0.024918 | 0.006245
8 | 0.010625 | 0.0026629
9 | 0.051672 | 0.01295
10 | 0.021441 | 0.0053737
11 | 0.039698 | 0.0099492
12 | 0.019823 | 0.0049681
13 | 0.013919 | 0.0034885

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1