## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-90_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-90_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-90_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_1711-90_0_4_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_1711-90_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1711-90_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1711-90_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_1711-90_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_1711-90_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_1711-90_0_4_node_28 | 0.4 | n |  | TRUE
10 | bus_LV_1711-90_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_1711-90_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_1711-90_0_4_node_11 | 0.4 | n |  | TRUE
13 | bus_LV_1711-90_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_1711-90_0_4_node_12 | 0.4 | n |  | TRUE
15 | bus_LV_1711-90_0_4_node_42 | 0.4 | n |  | TRUE
16 | bus_LV_1711-90_0_4_node_24 | 0.4 | n |  | TRUE
17 | bus_LV_1711-90_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_1711-90_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_1711-90_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_1711-90_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_1711-90_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_1711-90_0_4_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_1711-90_0_4_node_18 | 0.4 | n |  | TRUE
24 | bus_LV_1711-90_0_4_node_29 | 0.4 | n |  | TRUE
25 | bus_LV_1711-90_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_1711-90_0_4_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_1711-90_0_4_node_30 | 0.4 | n |  | TRUE
28 | bus_LV_1711-90_0_4_node_33 | 0.4 | n |  | TRUE
29 | bus_LV_1711-90_0_4_node_32 | 0.4 | n |  | TRUE
30 | bus_LV_1711-90_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_1711-90_0_4_node_41 | 0.4 | n |  | TRUE
32 | bus_LV_1711-90_0_4_node_40 | 0.4 | n |  | TRUE
33 | bus_LV_1711-90_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_1711-90_0_4_node_34 | 0.4 | n |  | TRUE
35 | bus_LV_1711-90_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_1711-90_0_4_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_1711-90_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_1711-90_0_4_node_43 | 0.4 | n |  | TRUE
39 | bus_LV_1711-90_0_4_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_1711-90_0_4_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_1711-90_0_4_node_37 | 0.4 | n |  | TRUE
42 | bus_LV_1711-90_0_4_node_38 | 0.4 | n |  | TRUE
43 | bus_MV_228_1_node_100 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-90_0_4_load_0 | 0 | 0.0042586 | 0.0010673 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-90_0_4_load_1 | 1 | 0.0022431 | 0.00056218 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-90_0_4_load_3 | 2 | 0.007523 | 0.0018855 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-90_0_4_load_4 | 4 | 0.0095208 | 0.0023861 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-90_0_4_load_5 | 5 | 0.029303 | 0.0073441 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-90_0_4_load_28 | 9 | 0.0038287 | 0.00095956 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-90_0_4_load_11 | 12 | 0.0053383 | 0.0013379 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-90_0_4_load_12 | 14 | 0.008106 | 0.0020316 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-90_0_4_load_42 | 15 | 0.0026513 | 0.00066449 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-90_0_4_load_24 | 16 | 0.084876 | 0.021272 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-90_0_4_load_25 | 17 | 0.053171 | 0.013326 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-90_0_4_load_13 | 18 | 0.011715 | 0.0029362 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-90_0_4_load_14 | 19 | 0.004813 | 0.0012063 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-90_0_4_load_15 | 20 | 0.0051145 | 0.0012818 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-90_0_4_load_16 | 21 | 0.027332 | 0.0068501 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-90_0_4_load_17 | 22 | 0.010982 | 0.0027525 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-90_0_4_load_29 | 24 | 0.00791 | 0.0019824 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-90_0_4_load_30 | 27 | 0.0027132 | 0.00068 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-90_0_4_load_33 | 28 | 0.014237 | 0.0035681 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-90_0_4_load_32 | 29 | 0.020995 | 0.0052617 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-90_0_4_load_41 | 31 | 0.016343 | 0.004096 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-90_0_4_load_40 | 32 | 0.0018077 | 0.00045306 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-90_0_4_load_19 | 33 | 0.0092978 | 0.0023302 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-90_0_4_load_34 | 34 | 0.0025725 | 0.00064472 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-90_0_4_load_31 | 35 | 0.071661 | 0.01796 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-90_0_4_load_39 | 36 | 0.0036108 | 0.00090496 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-90_0_4_load_26 | 37 | 0.043578 | 0.010922 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1711-90_0_4_load_43 | 38 | 0.002768 | 0.00069372 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1711-90_0_4_load_35 | 39 | 0.0033346 | 0.00083574 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1711-90_0_4_load_36 | 40 | 0.0017768 | 0.00044531 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1711-90_0_4_load_37 | 41 | 0.0021171 | 0.0005306 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1711-90_0_4_load_38 | 42 | 0.0070259 | 0.0017609 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 37 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-90_0_4_line_0 |  | 0 | 1 | 0.0088154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-90_0_4_line_1 |  | 1 | 2 | 0.0057775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-90_0_4_line_2 |  | 2 | 6 | 0.024667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-90_0_4_line_3 |  | 3 | 4 | 0.066247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-90_0_4_line_4 |  | 3 | 5 | 0.037374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-90_0_4_line_5 |  | 4 | 7 | 0.037397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1711-90_0_4_line_6 |  | 5 | 8 | 0.044884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-90_0_4_line_7 |  | 6 | 9 | 0.033386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-90_0_4_line_8 |  | 6 | 7 | 0.011948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-90_0_4_line_9 |  | 7 | 10 | 0.17743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-90_0_4_line_10 |  | 8 | 11 | 0.14847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1711-90_0_4_line_11 |  | 10 | 12 | 0.048534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-90_0_4_line_12 |  | 11 | 13 | 0.030807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-90_0_4_line_13 |  | 12 | 14 | 0.037176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_1711-90_0_4_line_14 |  | 13 | 15 | 0.052822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-90_0_4_line_15 |  | 14 | 18 | 0.012095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_1711-90_0_4_line_16 |  | 15 | 38 | 0.016598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-90_0_4_line_17 |  | 16 | 17 | 0.0041018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-90_0_4_line_18 |  | 17 | 37 | 0.026289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-90_0_4_line_19 |  | 18 | 19 | 0.019031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_1711-90_0_4_line_20 |  | 19 | 20 | 0.0011048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_1711-90_0_4_line_21 |  | 20 | 21 | 0.0189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_1711-90_0_4_line_22 |  | 21 | 22 | 0.017369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_1711-90_0_4_line_23 |  | 22 | 23 | 0.055119 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_1711-90_0_4_line_24 |  | 23 | 24 | 0.051159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-90_0_4_line_25 |  | 23 | 25 | 0.036079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_1711-90_0_4_line_26 |  | 23 | 26 | 0.14817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1711-90_0_4_line_27 |  | 24 | 27 | 0.030057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1711-90_0_4_line_28 |  | 25 | 28 | 0.090871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1711-90_0_4_line_29 |  | 25 | 29 | 0.019145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_1711-90_0_4_line_30 |  | 26 | 33 | 0.01221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_1711-90_0_4_line_31 |  | 28 | 34 | 0.00067521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-90_0_4_line_32 |  | 29 | 35 | 0.01534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_1711-90_0_4_line_33 |  | 30 | 31 | 0.066432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_1711-90_0_4_line_34 |  | 30 | 32 | 0.067866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_1711-90_0_4_line_35 |  | 32 | 36 | 0.045009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_1711-90_0_4_line_36 |  | 34 | 39 | 0.014889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1711-90_0_4_line_37 |  | 35 | 37 | 0.010697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_1711-90_0_4_line_38 |  | 36 | 42 | 0.0066363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_1711-90_0_4_line_39 |  | 39 | 40 | 0.0039928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1711-90_0_4_line_40 |  | 40 | 41 | 0.0005441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_1711-90_0_4_line_41 |  | 41 | 42 | 0.010665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-90_0_4_trafo_26 | 0.63 MVA 20/0.4 kV | 43 | 37 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2679914.5676 | 1225939.4125 | 2679910.8703 | 1225931.41 | 2679910.8703 | 1225931.41
1 | 2679907.2694 | 1225926.8919 | 2679907.2694 | 1225926.8919 | 2679910.8703 | 1225931.41
2 | 2679883.3283 | 1225932.0185 | 2679893.3816 | 1225931.3752 | 2679907.2694 | 1225926.8919
3 | 2679943.3544 | 1226004.1731 | 2679914.6127 | 1226009.4685 | 2679897.4526 | 1225976.6642
4 | 2679943.3544 | 1226004.1731 | 2679951.8272 | 1226040.5736
5 | 2679880.1187 | 1225943.5276 | 2679897.4526 | 1225976.6642
6 | 2679962.0026 | 1226084.2888 | 2679951.8272 | 1226040.5736
7 | 2679883.3283 | 1225932.0185 | 2679879.1557 | 1225909.6696 | 2679874.0063 | 1225900.3458
8 | 2679880.1187 | 1225943.5276 | 2679883.3283 | 1225932.0185
9 | 2679786.4675 | 1225871.5341 | 2679790.4067 | 1225886.4414 | 2679825.6172 | 1225977.6083 | 2679880.1187 | 1225943.5276
10 | 2680110.6856 | 1226076.2049 | 2679962.0026 | 1226084.2888
11 | 2679786.4675 | 1225871.5341 | 2679810.2313 | 1225866.0712 | 2679833.7987 | 1225860.7993
12 | 2680127.6838 | 1226101.9289 | 2680117.216 | 1226086.0884 | 2680110.6856 | 1226076.2049
13 | 2679833.7987 | 1225860.7993 | 2679855.7629 | 1225855.8861 | 2679870.055 | 1225852.5844
14 | 2680127.6838 | 1226101.9289 | 2680121.2112 | 1226129.4047 | 2680110.2045 | 1226151.3979
15 | 2679870.055 | 1225852.5844 | 2679881.8399 | 1225849.8619
16 | 2680110.2045 | 1226151.3979 | 2680109.3388 | 1226153.1276 | 2680101.0678 | 1226165.236
17 | 2680053.5525 | 1225881.8858 | 2680055.484 | 1225885.5044
18 | 2680041.1728 | 1225858.6945 | 2680053.5525 | 1225881.8858
19 | 2679900.383 | 1225845.5782 | 2679881.8399 | 1225849.8619
20 | 2679900.383 | 1225845.5782 | 2679901.4594 | 1225845.3296
21 | 2679919.874 | 1225841.0755 | 2679901.4594 | 1225845.3296
22 | 2679936.7975 | 1225837.1659 | 2679919.874 | 1225841.0755
23 | 2679990.5587 | 1225825.0086 | 2679962.8647 | 1225831.2518 | 2679954.8737 | 1225832.9901 | 2679936.7975 | 1225837.1659
24 | 2679990.5587 | 1225825.0086 | 2679997.383 | 1225857.6001 | 2679997.5271 | 1225875.4598
25 | 2680025.6288 | 1225816.541 | 2680016.0925 | 1225818.7476 | 2680005.8389 | 1225821.3004 | 2679990.5587 | 1225825.0086
26 | 2679989.3818 | 1225718.0317 | 2679985.4496 | 1225717.2895 | 2679975.2811 | 1225717.453 | 2679965.4073 | 1225721.6343 | 2680002.603 | 1225813.3181 | 2680005.8389 | 1225821.3004 | 2679990.5587 | 1225825.0086
27 | 2679997.7696 | 1225905.5154 | 2679997.5271 | 1225875.4598
28 | 2680025.6288 | 1225816.541 | 2680072.985 | 1225804.9033 | 2680113.522 | 1225793.516
29 | 2680025.6288 | 1225816.541 | 2680030.7617 | 1225834.9847
30 | 2679989.3818 | 1225718.0317 | 2680000.4797 | 1225723.123
31 | 2680114.172 | 1225793.3334 | 2680113.522 | 1225793.516
32 | 2680030.7617 | 1225834.9847 | 2680033.2073 | 1225843.7723 | 2680036.1354 | 1225849.2577
33 | 2680250.9623 | 1225733.7856 | 2680269.9002 | 1225768.0418 | 2680252.4601 | 1225789.0987
34 | 2680250.9623 | 1225733.7856 | 2680190.9916 | 1225765.5543
35 | 2680148.9194 | 1225781.5471 | 2680190.9916 | 1225765.5543
36 | 2680114.172 | 1225793.3334 | 2680128.5066 | 1225789.3066 | 2680128.5066 | 1225789.3066
37 | 2680041.1728 | 1225858.6945 | 2680036.1354 | 1225849.2577
38 | 2680142.7161 | 1225783.9052 | 2680148.9194 | 1225781.5471
39 | 2680128.5066 | 1225789.3066 | 2680132.2388 | 1225787.8879
40 | 2680132.7474 | 1225787.6946 | 2680132.2388 | 1225787.8879
41 | 2680142.7161 | 1225783.9052 | 2680132.7474 | 1225787.6946

## bus_geodata
| x | y | coords
0 | 2679914.5676 | 1225939.4125
1 | 2679910.8703 | 1225931.41
2 | 2679907.2694 | 1225926.8919
3 | 2679943.3544 | 1226004.1731
4 | 2679897.4526 | 1225976.6642
5 | 2679951.8272 | 1226040.5736
6 | 2679883.3283 | 1225932.0185
7 | 2679880.1187 | 1225943.5276
8 | 2679962.0026 | 1226084.2888
9 | 2679874.0063 | 1225900.3458
10 | 2679786.4675 | 1225871.5341
11 | 2680110.6856 | 1226076.2049
12 | 2679833.7987 | 1225860.7993
13 | 2680127.6838 | 1226101.9289
14 | 2679870.055 | 1225852.5844
15 | 2680110.2045 | 1226151.3979
16 | 2680055.484 | 1225885.5044
17 | 2680053.5525 | 1225881.8858
18 | 2679881.8399 | 1225849.8619
19 | 2679900.383 | 1225845.5782
20 | 2679901.4594 | 1225845.3296
21 | 2679919.874 | 1225841.0755
22 | 2679936.7975 | 1225837.1659
23 | 2679990.5587 | 1225825.0086
24 | 2679997.5271 | 1225875.4598
25 | 2680025.6288 | 1225816.541
26 | 2679989.3818 | 1225718.0317
27 | 2679997.7696 | 1225905.5154
28 | 2680113.522 | 1225793.516
29 | 2680030.7617 | 1225834.9847
30 | 2680250.9623 | 1225733.7856
31 | 2680252.4601 | 1225789.0987
32 | 2680190.9916 | 1225765.5543
33 | 2680000.4797 | 1225723.123
34 | 2680114.172 | 1225793.3334
35 | 2680036.1354 | 1225849.2577
36 | 2680148.9194 | 1225781.5471
37 | 2680041.1728 | 1225858.6945
38 | 2680101.0678 | 1226165.236
39 | 2680128.5066 | 1225789.3066
40 | 2680132.2388 | 1225787.8879
41 | 2680132.7474 | 1225787.6946
42 | 2680142.7161 | 1225783.9052
43 | 2680025.6288 | 1225816.541

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97579 | -0.4659 | 0.0042586 | 0.0010673
1 | 0.97582 | -0.46521 | 0.0022431 | 0.00056218
2 | 0.97586 | -0.46452 | 0.007523 | 0.0018855
3 | 0.97269 | -0.52689 | 0 | 0
4 | 0.97483 | -0.4846 | 0.0095208 | 0.0023861
5 | 0.97148 | -0.55084 | 0.029303 | 0.0073441
6 | 0.97618 | -0.45819 | 0 | 0
7 | 0.97638 | -0.45429 | 0 | 0
8 | 0.97125 | -0.55534 | 0 | 0
9 | 0.97606 | -0.46053 | 0.0038287 | 0.00095956
10 | 0.98665 | -0.25489 | 0 | 0
11 | 0.9705 | -0.57023 | 0 | 0
12 | 0.98946 | -0.20106 | 0.0053383 | 0.0013379
13 | 0.97034 | -0.57332 | 0 | 0
14 | 0.99063 | -0.17877 | 0.008106 | 0.0020316
15 | 0.97007 | -0.57862 | 0.0026513 | 0.00066449
16 | 0.99638 | -0.069572 | 0.084876 | 0.021272
17 | 0.9967 | -0.063462 | 0.053171 | 0.013326
18 | 0.99091 | -0.17336 | 0.011715 | 0.0029362
19 | 0.99143 | -0.16353 | 0.004813 | 0.0012063
20 | 0.99146 | -0.16293 | 0.0051145 | 0.0012818
21 | 0.99203 | -0.15208 | 0.027332 | 0.0068501
22 | 0.99269 | -0.13932 | 0.010982 | 0.0027525
23 | 0.99499 | -0.095374 | 0 | 0
24 | 0.9945 | -0.10495 | 0.00791 | 0.0019824
25 | 0.99672 | -0.062514 | 0 | 0
26 | 0.99373 | -0.11967 | 0 | 0
27 | 0.99442 | -0.10639 | 0.0027132 | 0.00068
28 | 0.99232 | -0.14712 | 0.014237 | 0.0035681
29 | 0.99794 | -0.039221 | 0.020995 | 0.0052617
30 | 0.98949 | -0.20193 | 0 | 0
31 | 0.9885 | -0.22128 | 0.016343 | 0.004096
32 | 0.99051 | -0.18221 | 0.0018077 | 0.00045306
33 | 0.99363 | -0.12167 | 0.0092978 | 0.0023302
34 | 0.9923 | -0.14758 | 0.0025725 | 0.00064472
35 | 0.99902 | -0.018723 | 0.071661 | 0.01796
36 | 0.99126 | -0.1677 | 0.0036108 | 0.00090496
37 | 1 | 0 | -0.44385 | -0.11206
38 | 0.97003 | -0.57948 | 0.002768 | 0.00069372
39 | 0.99181 | -0.15708 | 0.0033346 | 0.00083574
40 | 0.99169 | -0.15939 | 0.0017768 | 0.00044531
41 | 0.99167 | -0.15969 | 0.0021171 | 0.0005306
42 | 0.99139 | -0.16514 | 0.0070259 | 0.0017609
43 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0042586 | -0.0010673 | 0.0042587 | 0.0010673 | 1.3941e-07 | -2.0899e-08 | 0.0064941 | 0.006494 | 0.0064941 | 0.97579 | -0.4659 | 0.97582 | -0.46521 | 1.7841
1 | -0.0065018 | -0.0016295 | 0.006502 | 0.0016295 | 2.1297e-07 | 6.412e-08 | 0.0099145 | 0.0099145 | 0.0099145 | 0.97582 | -0.46521 | 0.97586 | -0.46452 | 2.7238
2 | -0.014025 | -0.003515 | 0.014029 | 0.0035174 | 4.2306e-06 | 2.3993e-06 | 0.021386 | 0.021386 | 0.021386 | 0.97586 | -0.46452 | 0.97618 | -0.45819 | 5.8752
3 | -0.03477 | -0.0087282 | 0.03484 | 0.0087724 | 7.0298e-05 | 4.4167e-05 | 0.053196 | 0.053195 | 0.053196 | 0.97269 | -0.52689 | 0.97483 | -0.4846 | 14.6142
4 | 0.03477 | 0.0087282 | -0.03473 | -0.0087033 | 3.966e-05 | 2.4919e-05 | 0.053196 | 0.053196 | 0.053196 | 0.97269 | -0.52689 | 0.97148 | -0.55084 | 14.6142
5 | -0.044361 | -0.011159 | 0.044425 | 0.011199 | 6.4328e-05 | 4.0703e-05 | 0.067728 | 0.067728 | 0.067728 | 0.97483 | -0.4846 | 0.97638 | -0.45429 | 18.6066
6 | 0.0054266 | 0.0013592 | -0.0054255 | -0.0013591 | 1.1628e-06 | 1.8861e-07 | 0.0083117 | 0.0083119 | 0.0083119 | 0.97148 | -0.55084 | 0.97125 | -0.55534 | 2.2835
7 | 0.0038291 | 0.00095942 | -0.0038287 | -0.00095956 | 4.2653e-07 | -1.4436e-07 | 0.0058367 | 0.0058369 | 0.0058369 | 0.97618 | -0.45819 | 0.97606 | -0.46053 | 1.6035
8 | -0.017858 | -0.0044768 | 0.017862 | 0.0044788 | 3.3203e-06 | 1.9756e-06 | 0.027222 | 0.027222 | 0.027222 | 0.97618 | -0.45819 | 0.97638 | -0.45429 | 7.4787
9 | -0.062287 | -0.015678 | 0.062887 | 0.01606 | 0.00059985 | 0.00038166 | 0.09495 | 0.094949 | 0.09495 | 0.97638 | -0.45429 | 0.98665 | -0.25489 | 26.0852
10 | 0.0054255 | 0.0013591 | -0.0054216 | -0.0013584 | 3.8468e-06 | 6.2599e-07 | 0.0083119 | 0.0083126 | 0.0083126 | 0.97125 | -0.55534 | 0.9705 | -0.57023 | 2.2837
11 | -0.062887 | -0.01606 | 0.063051 | 0.016164 | 0.00016408 | 0.00010439 | 0.094949 | 0.094949 | 0.094949 | 0.98665 | -0.25489 | 0.98946 | -0.20106 | 26.085
12 | 0.0054216 | 0.0013584 | -0.0054208 | -0.0013583 | 7.9829e-07 | 1.303e-07 | 0.0083126 | 0.0083127 | 0.0083127 | 0.9705 | -0.57023 | 0.97034 | -0.57332 | 2.2837
13 | -0.068389 | -0.017502 | 0.068463 | 0.017548 | 7.3916e-05 | 4.635e-05 | 0.10298 | 0.10298 | 0.10298 | 0.98946 | -0.20106 | 0.99063 | -0.17877 | 14.1452
14 | 0.0054208 | 0.0013583 | -0.0054194 | -0.0013581 | 1.3688e-06 | 2.2373e-07 | 0.0083127 | 0.008313 | 0.008313 | 0.97034 | -0.57332 | 0.97007 | -0.57862 | 2.2838
15 | -0.076569 | -0.01958 | 0.076589 | 0.019592 | 2.0048e-05 | 1.2364e-05 | 0.11515 | 0.11515 | 0.11515 | 0.99063 | -0.17877 | 0.99091 | -0.17336 | 10.5451
16 | 0.0027681 | 0.00069359 | -0.002768 | -0.00069372 | 1.1221e-07 | -1.3309e-07 | 0.004246 | 0.0042461 | 0.0042461 | 0.97007 | -0.57862 | 0.97003 | -0.57948 | 1.1665
17 | -0.084876 | -0.021272 | 0.084901 | 0.021288 | 2.4714e-05 | 1.5763e-05 | 0.12676 | 0.12676 | 0.12676 | 0.99638 | -0.069572 | 0.9967 | -0.063462 | 34.823
18 | -0.13807 | -0.034614 | 0.13849 | 0.034881 | 0.0004189 | 0.00026775 | 0.20614 | 0.20614 | 0.20614 | 0.9967 | -0.063462 | 1 | 0 | 56.631
19 | -0.088304 | -0.022528 | 0.088346 | 0.022555 | 4.1919e-05 | 2.6093e-05 | 0.13274 | 0.13274 | 0.13274 | 0.99091 | -0.17336 | 0.99143 | -0.16353 | 12.1561
20 | -0.093159 | -0.023761 | 0.093162 | 0.023762 | 2.7055e-06 | 1.6888e-06 | 0.13997 | 0.13997 | 0.13997 | 0.99143 | -0.16353 | 0.99146 | -0.16293 | 12.8176
21 | -0.098277 | -0.025044 | 0.098328 | 0.025077 | 5.1499e-05 | 3.2227e-05 | 0.14764 | 0.14764 | 0.14764 | 0.99146 | -0.16293 | 0.99203 | -0.15208 | 13.5205
22 | -0.12566 | -0.031927 | 0.12574 | 0.031975 | 7.7262e-05 | 4.8774e-05 | 0.18864 | 0.18864 | 0.18864 | 0.99203 | -0.15208 | 0.99269 | -0.13932 | 17.2748
23 | -0.13672 | -0.034728 | 0.13701 | 0.034911 | 0.00028984 | 0.00018335 | 0.2051 | 0.2051 | 0.2051 | 0.99269 | -0.13932 | 0.99499 | -0.095374 | 18.7824
24 | 0.010628 | 0.0026646 | -0.010623 | -0.0026622 | 4.847e-06 | 2.4379e-06 | 0.015895 | 0.015895 | 0.015895 | 0.99499 | -0.095374 | 0.9945 | -0.10495 | 4.3668
25 | -0.15695 | -0.039911 | 0.1572 | 0.040069 | 0.00024889 | 0.00015788 | 0.23492 | 0.23492 | 0.23492 | 0.99499 | -0.095374 | 0.99672 | -0.062514 | 21.5129
26 | 0.0093095 | 0.0023356 | -0.0092987 | -0.0023307 | 1.0772e-05 | 4.9721e-06 | 0.013923 | 0.013924 | 0.013924 | 0.99499 | -0.095374 | 0.99373 | -0.11967 | 3.8252
27 | 0.0027134 | 0.00067972 | -0.0027132 | -0.00068 | 1.8578e-07 | -2.7106e-07 | 0.0040598 | 0.00406 | 0.00406 | 0.9945 | -0.10495 | 0.99442 | -0.10639 | 1.1154
28 | 0.053115 | 0.01342 | -0.052901 | -0.013284 | 0.00021448 | 0.00013609 | 0.079335 | 0.079335 | 0.079335 | 0.99672 | -0.062514 | 0.99232 | -0.14712 | 21.7954
29 | -0.21031 | -0.05349 | 0.21055 | 0.05364 | 0.00023633 | 0.0001505 | 0.31425 | 0.31425 | 0.31425 | 0.99672 | -0.062514 | 0.99794 | -0.039221 | 28.7779
30 | 0.0092987 | 0.0023307 | -0.0092978 | -0.0023302 | 8.8771e-07 | 4.0996e-07 | 0.013924 | 0.013924 | 0.013924 | 0.99373 | -0.11967 | 0.99363 | -0.12167 | 3.8253
31 | 0.038663 | 0.0097162 | -0.038663 | -0.0097157 | 8.5137e-07 | 5.3616e-07 | 0.057986 | 0.057986 | 0.057986 | 0.99232 | -0.14712 | 0.9923 | -0.14758 | 15.9303
32 | -0.23154 | -0.058902 | 0.23177 | 0.059048 | 0.00022896 | 0.00014593 | 0.34556 | 0.34556 | 0.34556 | 0.99794 | -0.039221 | 0.99902 | -0.018723 | 31.6446
33 | 0.016358 | 0.0041048 | -0.016343 | -0.004096 | 1.5078e-05 | 8.7976e-06 | 0.024602 | 0.024602 | 0.024602 | 0.98949 | -0.20193 | 0.9885 | -0.22128 | 6.7588
34 | -0.016358 | -0.0041048 | 0.016374 | 0.0041138 | 1.5403e-05 | 8.9854e-06 | 0.024602 | 0.024602 | 0.024602 | 0.98949 | -0.20193 | 0.99051 | -0.18221 | 6.7588
35 | -0.018182 | -0.0045669 | 0.018194 | 0.0045744 | 1.2595e-05 | 7.4812e-06 | 0.027317 | 0.027317 | 0.027317 | 0.99051 | -0.18221 | 0.99126 | -0.1677 | 7.5048
36 | 0.03609 | 0.0090709 | -0.036074 | -0.0090607 | 1.6359e-05 | 1.0278e-05 | 0.054129 | 0.054129 | 0.054129 | 0.9923 | -0.14758 | 0.99181 | -0.15708 | 14.8705
37 | -0.30343 | -0.077008 | 0.30371 | 0.077182 | 0.00027354 | 0.00017465 | 0.4523 | 0.4523 | 0.4523 | 0.99902 | -0.018723 | 1 | 0 | 41.419
38 | -0.021805 | -0.0054793 | 0.021808 | 0.0054809 | 2.6672e-06 | 1.6214e-06 | 0.032737 | 0.032737 | 0.032737 | 0.99126 | -0.1677 | 0.99139 | -0.16514 | 8.9938
39 | 0.032739 | 0.0082249 | -0.032736 | -0.0082227 | 3.6135e-06 | 2.2611e-06 | 0.049126 | 0.049126 | 0.049126 | 0.99181 | -0.15708 | 0.99169 | -0.15939 | 13.4961
40 | 0.030959 | 0.0077773 | -0.030958 | -0.0077771 | 4.4041e-07 | 2.7484e-07 | 0.04646 | 0.04646 | 0.04646 | 0.99169 | -0.15939 | 0.99167 | -0.15969 | 12.7637
41 | 0.028841 | 0.0072465 | -0.028834 | -0.0072418 | 7.4922e-06 | 4.6575e-06 | 0.043283 | 0.043283 | 0.043283 | 0.99167 | -0.15969 | 0.99139 | -0.16514 | 11.8909

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.48742 | 0.12299

## res_load
| p_mw | q_mvar
0 | 0.0042586 | 0.0010673
1 | 0.0022431 | 0.00056218
2 | 0.007523 | 0.0018855
3 | 0.0095208 | 0.0023861
4 | 0.029303 | 0.0073441
5 | 0.0038287 | 0.00095956
6 | 0.0053383 | 0.0013379
7 | 0.008106 | 0.0020316
8 | 0.0026513 | 0.00066449
9 | 0.084876 | 0.021272
10 | 0.053171 | 0.013326
11 | 0.011715 | 0.0029362
12 | 0.004813 | 0.0012063
13 | 0.0051145 | 0.0012818
14 | 0.027332 | 0.0068501
15 | 0.010982 | 0.0027525
16 | 0.00791 | 0.0019824
17 | 0.0027132 | 0.00068
18 | 0.014237 | 0.0035681
19 | 0.020995 | 0.0052617
20 | 0.016343 | 0.004096
21 | 0.0018077 | 0.00045306
22 | 0.0092978 | 0.0023302
23 | 0.0025725 | 0.00064472
24 | 0.071661 | 0.01796
25 | 0.0036108 | 0.00090496
26 | 0.043578 | 0.010922
27 | 0.002768 | 0.00069372
28 | 0.0033346 | 0.00083574
29 | 0.0017768 | 0.00044531
30 | 0.0021171 | 0.0005306
31 | 0.0070259 | 0.0017609

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1