## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_1711-94_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_1711-94_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_1711-94_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_1711-94_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_1711-94_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_1711-94_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_1711-94_0_5_node_82 | 0.4 | n |  | TRUE
7 | bus_LV_1711-94_0_5_node_77 | 0.4 | n |  | TRUE
8 | bus_LV_1711-94_0_5_node_71 | 0.4 | n |  | TRUE
9 | bus_LV_1711-94_0_5_node_70 | 0.4 | n |  | TRUE
10 | bus_LV_1711-94_0_5_node_87 | 0.4 | n |  | TRUE
11 | bus_LV_1711-94_0_5_node_81 | 0.4 | n |  | TRUE
12 | bus_LV_1711-94_0_5_node_78 | 0.4 | n |  | TRUE
13 | bus_LV_1711-94_0_5_node_72 | 0.4 | n |  | TRUE
14 | bus_LV_1711-94_0_5_node_69 | 0.4 | n |  | TRUE
15 | bus_LV_1711-94_0_5_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_1711-94_0_5_node_7 | 0.4 | n |  | TRUE
17 | bus_LV_1711-94_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_1711-94_0_5_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_1711-94_0_5_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_1711-94_0_5_node_63 | 0.4 | n |  | TRUE
21 | bus_LV_1711-94_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_1711-94_0_5_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_1711-94_0_5_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_1711-94_0_5_node_22 | 0.4 | n |  | TRUE
25 | bus_LV_1711-94_0_5_node_53 | 0.4 | n |  | TRUE
26 | bus_LV_1711-94_0_5_node_23 | 0.4 | n |  | TRUE
27 | bus_LV_1711-94_0_5_node_52 | 0.4 | n |  | TRUE
28 | bus_LV_1711-94_0_5_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_1711-94_0_5_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_1711-94_0_5_node_54 | 0.4 | n |  | TRUE
31 | bus_LV_1711-94_0_5_node_27 | 0.4 | n |  | TRUE
32 | bus_LV_1711-94_0_5_node_50 | 0.4 | n |  | TRUE
33 | bus_LV_1711-94_0_5_node_37 | 0.4 | n |  | TRUE
34 | bus_LV_1711-94_0_5_node_64 | 0.4 | n |  | TRUE
35 | bus_LV_1711-94_0_5_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_1711-94_0_5_node_65 | 0.4 | n |  | TRUE
37 | bus_LV_1711-94_0_5_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_1711-94_0_5_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_1711-94_0_5_node_107 | 0.4 | n |  | TRUE
40 | bus_LV_1711-94_0_5_node_99 | 0.4 | n |  | TRUE
41 | bus_LV_1711-94_0_5_node_98 | 0.4 | n |  | TRUE
42 | bus_LV_1711-94_0_5_node_15 | 0.4 | n |  | TRUE
43 | bus_LV_1711-94_0_5_node_16 | 0.4 | n |  | TRUE
44 | bus_LV_1711-94_0_5_node_17 | 0.4 | n |  | TRUE
45 | bus_LV_1711-94_0_5_node_18 | 0.4 | n |  | TRUE
46 | bus_LV_1711-94_0_5_node_19 | 0.4 | n |  | TRUE
47 | bus_LV_1711-94_0_5_node_30 | 0.4 | n |  | TRUE
48 | bus_LV_1711-94_0_5_node_20 | 0.4 | n |  | TRUE
49 | bus_LV_1711-94_0_5_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_1711-94_0_5_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_1711-94_0_5_node_29 | 0.4 | n |  | TRUE
52 | bus_LV_1711-94_0_5_node_105 | 0.4 | n |  | TRUE
53 | bus_LV_1711-94_0_5_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_1711-94_0_5_node_104 | 0.4 | n |  | TRUE
55 | bus_LV_1711-94_0_5_node_59 | 0.4 | n |  | TRUE
56 | bus_LV_1711-94_0_5_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_1711-94_0_5_node_55 | 0.4 | n |  | TRUE
58 | bus_LV_1711-94_0_5_node_106 | 0.4 | n |  | TRUE
59 | bus_LV_1711-94_0_5_node_114 | 0.4 | n |  | TRUE
60 | bus_LV_1711-94_0_5_node_108 | 0.4 | n |  | TRUE
61 | bus_LV_1711-94_0_5_node_109 | 0.4 | n |  | TRUE
62 | bus_LV_1711-94_0_5_node_112 | 0.4 | n |  | TRUE
63 | bus_LV_1711-94_0_5_node_93 | 0.4 | n |  | TRUE
64 | bus_LV_1711-94_0_5_node_95 | 0.4 | n |  | TRUE
65 | bus_LV_1711-94_0_5_node_92 | 0.4 | n |  | TRUE
66 | bus_LV_1711-94_0_5_node_97 | 0.4 | n |  | TRUE
67 | bus_LV_1711-94_0_5_node_100 | 0.4 | n |  | TRUE
68 | bus_LV_1711-94_0_5_node_31 | 0.4 | n |  | TRUE
69 | bus_LV_1711-94_0_5_node_32 | 0.4 | n |  | TRUE
70 | bus_LV_1711-94_0_5_node_33 | 0.4 | n |  | TRUE
71 | bus_LV_1711-94_0_5_node_35 | 0.4 | n |  | TRUE
72 | bus_LV_1711-94_0_5_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_1711-94_0_5_node_48 | 0.4 | n |  | TRUE
74 | bus_LV_1711-94_0_5_node_94 | 0.4 | n |  | TRUE
75 | bus_LV_1711-94_0_5_node_47 | 0.4 | n |  | TRUE
76 | bus_LV_1711-94_0_5_node_38 | 0.4 | n |  | TRUE
77 | bus_LV_1711-94_0_5_node_39 | 0.4 | n |  | TRUE
78 | bus_LV_1711-94_0_5_node_40 | 0.4 | n |  | TRUE
79 | bus_LV_1711-94_0_5_node_41 | 0.4 | n |  | TRUE
80 | bus_LV_1711-94_0_5_node_42 | 0.4 | n |  | TRUE
81 | bus_LV_1711-94_0_5_node_43 | 0.4 | n |  | TRUE
82 | bus_LV_1711-94_0_5_node_44 | 0.4 | n |  | TRUE
83 | bus_LV_1711-94_0_5_node_88 | 0.4 | n |  | TRUE
84 | bus_LV_1711-94_0_5_node_89 | 0.4 | n |  | TRUE
85 | bus_LV_1711-94_0_5_node_45 | 0.4 | n |  | TRUE
86 | bus_LV_1711-94_0_5_node_46 | 0.4 | n |  | TRUE
87 | bus_LV_1711-94_0_5_node_115 | 0.4 | n |  | TRUE
88 | bus_LV_1711-94_0_5_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_1711-94_0_5_node_57 | 0.4 | n |  | TRUE
90 | bus_LV_1711-94_0_5_node_58 | 0.4 | n |  | TRUE
91 | bus_LV_1711-94_0_5_node_60 | 0.4 | n |  | TRUE
92 | bus_LV_1711-94_0_5_node_61 | 0.4 | n |  | TRUE
93 | bus_LV_1711-94_0_5_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_1711-94_0_5_node_62 | 0.4 | n |  | TRUE
95 | bus_LV_1711-94_0_5_node_67 | 0.4 | n |  | TRUE
96 | bus_LV_1711-94_0_5_node_68 | 0.4 | n |  | TRUE
97 | bus_LV_1711-94_0_5_node_73 | 0.4 | n |  | TRUE
98 | bus_LV_1711-94_0_5_node_76 | 0.4 | n |  | TRUE
99 | bus_LV_1711-94_0_5_node_110 | 0.4 | n |  | TRUE
100 | bus_LV_1711-94_0_5_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_1711-94_0_5_node_83 | 0.4 | n |  | TRUE
102 | bus_LV_1711-94_0_5_node_80 | 0.4 | n |  | TRUE
103 | bus_LV_1711-94_0_5_node_86 | 0.4 | n |  | TRUE
104 | bus_LV_1711-94_0_5_node_84 | 0.4 | n |  | TRUE
105 | bus_LV_1711-94_0_5_node_85 | 0.4 | n |  | TRUE
106 | bus_LV_1711-94_0_5_node_90 | 0.4 | n |  | TRUE
107 | bus_LV_1711-94_0_5_node_91 | 0.4 | n |  | TRUE
108 | bus_LV_1711-94_0_5_node_96 | 0.4 | n |  | TRUE
109 | bus_LV_1711-94_0_5_node_102 | 0.4 | n |  | TRUE
110 | bus_LV_1711-94_0_5_node_101 | 0.4 | n |  | TRUE
111 | bus_LV_1711-94_0_5_node_103 | 0.4 | n |  | TRUE
112 | bus_LV_1711-94_0_5_node_113 | 0.4 | n |  | TRUE
113 | bus_LV_1711-94_0_5_node_111 | 0.4 | n |  | TRUE
114 | bus_MV_25_0_node_204 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_1711-94_0_5_load_0 | 0 | 0.0041392 | 0.0010374 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_1711-94_0_5_load_1 | 1 | 0.0018882 | 0.00047323 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_1711-94_0_5_load_3 | 3 | 0.0042062 | 0.0010542 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_1711-94_0_5_load_77 | 7 | 0.00081394 | 0.00020399 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_1711-94_0_5_load_71 | 8 | 0.0042952 | 0.0010765 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_1711-94_0_5_load_70 | 9 | 0.0042422 | 0.0010632 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_1711-94_0_5_load_81 | 11 | 0.0039119 | 0.00098043 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_1711-94_0_5_load_78 | 12 | 0.0046905 | 0.0011755 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_1711-94_0_5_load_72 | 13 | 0.008569 | 0.0021476 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_1711-94_0_5_load_69 | 14 | 0.0030802 | 0.00077197 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_1711-94_0_5_load_6 | 15 | 0.0034471 | 0.00086393 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_1711-94_0_5_load_9 | 17 | 0.0037798 | 0.00094731 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_1711-94_0_5_load_63 | 20 | 0.0028453 | 0.00071309 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_1711-94_0_5_load_13 | 22 | 0.020898 | 0.0052376 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_1711-94_0_5_load_21 | 23 | 0.014523 | 0.0036398 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_1711-94_0_5_load_53 | 25 | 0.01397 | 0.0035012 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_1711-94_0_5_load_52 | 27 | 0.014142 | 0.0035442 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_1711-94_0_5_load_28 | 28 | 0.0074401 | 0.0018647 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_1711-94_0_5_load_64 | 34 | 0.0022775 | 0.00057081 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_1711-94_0_5_load_66 | 35 | 0.0044498 | 0.0011152 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_1711-94_0_5_load_65 | 36 | 0.00392 | 0.00098244 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_1711-94_0_5_load_107 | 39 | 0.011957 | 0.0029967 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_1711-94_0_5_load_98 | 41 | 0.017022 | 0.004266 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_1711-94_0_5_load_15 | 42 | 0.013024 | 0.0032641 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_1711-94_0_5_load_17 | 44 | 0.013059 | 0.0032729 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_1711-94_0_5_load_30 | 47 | 0.0049871 | 0.0012499 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_1711-94_0_5_load_20 | 48 | 0.0085846 | 0.0021515 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_1711-94_0_5_load_105 | 52 | 0.0086663 | 0.002172 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_1711-94_0_5_load_104 | 54 | 0.0081568 | 0.0020443 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_1711-94_0_5_load_59 | 55 | 0.0036197 | 0.00090719 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_1711-94_0_5_load_56 | 56 | 0.0036886 | 0.00092444 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_1711-94_0_5_load_106 | 58 | 0.011267 | 0.0028238 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_1711-94_0_5_load_114 | 59 | 0.0048793 | 0.0012229 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_1711-94_0_5_load_109 | 61 | 0.0034088 | 0.00085432 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_1711-94_0_5_load_112 | 62 | 0.0043211 | 0.001083 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_1711-94_0_5_load_95 | 64 | 0.032322 | 0.0081006 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_1711-94_0_5_load_92 | 65 | 0.010707 | 0.0026835 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_1711-94_0_5_load_31 | 68 | 0.0075906 | 0.0019024 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_1711-94_0_5_load_32 | 69 | 0.0094436 | 0.0023668 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_1711-94_0_5_load_33 | 70 | 0.0034319 | 0.00086012 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_1711-94_0_5_load_49 | 72 | 0.010696 | 0.0026806 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_1711-94_0_5_load_48 | 73 | 0.0030657 | 0.00076834 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_1711-94_0_5_load_94 | 74 | 0.002404 | 0.00060249 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_1711-94_0_5_load_47 | 75 | 0.0036777 | 0.00092172 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_1711-94_0_5_load_38 | 76 | 0.0057698 | 0.0014461 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_1711-94_0_5_load_39 | 77 | 0.002071 | 0.00051903 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_1711-94_0_5_load_40 | 78 | 0.010273 | 0.0025746 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_1711-94_0_5_load_41 | 79 | 0.0050709 | 0.0012709 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_1711-94_0_5_load_42 | 80 | 0.0031069 | 0.00077866 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_1711-94_0_5_load_88 | 83 | 0.007538 | 0.0018892 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_1711-94_0_5_load_89 | 84 | 0.0050171 | 0.0012574 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_1711-94_0_5_load_45 | 85 | 0.0020039 | 0.00050223 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_1711-94_0_5_load_46 | 86 | 0.0018717 | 0.00046909 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_1711-94_0_5_load_115 | 87 | 0.0060543 | 0.0015173 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_1711-94_0_5_load_74 | 88 | 0.0085919 | 0.0021533 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_1711-94_0_5_load_57 | 89 | 0.0052985 | 0.0013279 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_1711-94_0_5_load_58 | 90 | 0.0036698 | 0.00091974 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_1711-94_0_5_load_60 | 91 | 0.0044704 | 0.0011204 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_1711-94_0_5_load_61 | 92 | 0.0027054 | 0.00067803 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_1711-94_0_5_load_75 | 93 | 0.0025201 | 0.00063159 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_1711-94_0_5_load_62 | 94 | 0.0021365 | 0.00053546 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_1711-94_0_5_load_67 | 95 | 0.0028007 | 0.00070193 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_1711-94_0_5_load_68 | 96 | 0.002044 | 0.00051227 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_1711-94_0_5_load_73 | 97 | 0.0032069 | 0.00080372 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_1711-94_0_5_load_76 | 98 | 0.0063731 | 0.0015972 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_1711-94_0_5_load_110 | 99 | 0.0024501 | 0.00061405 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_1711-94_0_5_load_79 | 100 | 0.0027239 | 0.00068267 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_1711-94_0_5_load_83 | 101 | 0.00080519 | 0.0002018 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_1711-94_0_5_load_80 | 102 | 0.0039246 | 0.00098359 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_1711-94_0_5_load_86 | 103 | 0.0020117 | 0.00050418 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_1711-94_0_5_load_84 | 104 | 0.0027683 | 0.00069381 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_1711-94_0_5_load_90 | 106 | 0.0045475 | 0.0011397 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_1711-94_0_5_load_91 | 107 | 0.0099268 | 0.0024879 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_1711-94_0_5_load_96 | 108 | 0.0082124 | 0.0020582 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_1711-94_0_5_load_101 | 110 | 0.010955 | 0.0027456 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_1711-94_0_5_load_103 | 111 | 0.0096821 | 0.0024266 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_1711-94_0_5_load_113 | 112 | 0.0065554 | 0.0016429 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_1711-94_0_5_load_111 | 113 | 0.0030532 | 0.00076521 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_1711-94_0_5_line_0 |  | 0 | 1 | 0.029523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_1711-94_0_5_line_1 |  | 0 | 2 | 0.059323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_1711-94_0_5_line_2 |  | 1 | 3 | 0.025015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_1711-94_0_5_line_3 |  | 2 | 4 | 0.007556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_1711-94_0_5_line_4 |  | 2 | 5 | 0.077827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_1711-94_0_5_line_5 |  | 3 | 6 | 0.068869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_1711-94_0_5_line_6 |  | 4 | 7 | 0.027903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_1711-94_0_5_line_7 |  | 5 | 8 | 0.021366 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_1711-94_0_5_line_8 |  | 5 | 9 | 0.0058468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_1711-94_0_5_line_9 |  | 6 | 10 | 0.011761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_1711-94_0_5_line_10 |  | 6 | 11 | 0.037572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_1711-94_0_5_line_11 |  | 7 | 12 | 0.060342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_1711-94_0_5_line_12 |  | 8 | 13 | 0.043279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_1711-94_0_5_line_13 |  | 9 | 14 | 0.053817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_1711-94_0_5_line_14 |  | 10 | 103 | 0.017315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_1711-94_0_5_line_15 |  | 11 | 102 | 0.049387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_1711-94_0_5_line_16 |  | 12 | 100 | 0.034802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_1711-94_0_5_line_17 |  | 13 | 97 | 0.038829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_1711-94_0_5_line_18 |  | 14 | 96 | 0.016536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_1711-94_0_5_line_19 |  | 15 | 16 | 0.040465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_1711-94_0_5_line_20 |  | 16 | 17 | 0.01585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_1711-94_0_5_line_21 |  | 17 | 18 | 0.013331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_1711-94_0_5_line_22 |  | 18 | 21 | 0.038329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_1711-94_0_5_line_23 |  | 18 | 19 | 0.017022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_1711-94_0_5_line_24 |  | 19 | 20 | 0.019542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_1711-94_0_5_line_25 |  | 20 | 34 | 0.018367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_1711-94_0_5_line_26 |  | 21 | 23 | 0.020589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_1711-94_0_5_line_27 |  | 21 | 22 | 0.013757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_1711-94_0_5_line_28 |  | 23 | 26 | 0.017009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_1711-94_0_5_line_29 |  | 24 | 25 | 0.0026294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_1711-94_0_5_line_30 |  | 24 | 26 | 0.0097834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_1711-94_0_5_line_31 |  | 24 | 27 | 0.027494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_1711-94_0_5_line_32 |  | 25 | 29 | 0.024198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
33 | LV_1711-94_0_5_line_33 |  | 26 | 28 | 0.018367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_1711-94_0_5_line_34 |  | 28 | 31 | 0.028911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
35 | LV_1711-94_0_5_line_35 |  | 29 | 30 | 0.046977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
36 | LV_1711-94_0_5_line_36 |  | 30 | 55 | 0.010131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_1711-94_0_5_line_37 |  | 30 | 56 | 0.021634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_1711-94_0_5_line_38 |  | 31 | 32 | 0.028232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
39 | LV_1711-94_0_5_line_39 |  | 31 | 33 | 0.032727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_1711-94_0_5_line_40 |  | 32 | 41 | 0.015851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_1711-94_0_5_line_41 |  | 33 | 66 | 0.014618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_1711-94_0_5_line_42 |  | 34 | 36 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_1711-94_0_5_line_43 |  | 35 | 36 | 0.0092991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_1711-94_0_5_line_44 |  | 37 | 38 | 0.018669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_1711-94_0_5_line_45 |  | 37 | 39 | 0.018732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_1711-94_0_5_line_46 |  | 38 | 40 | 0.036335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_1711-94_0_5_line_47 |  | 38 | 41 | 0.026928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_1711-94_0_5_line_48 |  | 39 | 57 | 0.019174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_1711-94_0_5_line_49 |  | 40 | 54 | 0.012969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_1711-94_0_5_line_50 |  | 42 | 43 | 0.013135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_1711-94_0_5_line_51 |  | 43 | 44 | 0.014951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_1711-94_0_5_line_52 |  | 43 | 45 | 0.023973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_1711-94_0_5_line_53 |  | 44 | 46 | 0.025349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_1711-94_0_5_line_54 |  | 45 | 47 | 0.018717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_1711-94_0_5_line_55 |  | 46 | 48 | 0.020878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_1711-94_0_5_line_56 |  | 48 | 49 | 0.020583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_1711-94_0_5_line_57 |  | 49 | 50 | 0.041435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_1711-94_0_5_line_58 |  | 50 | 71 | 0.02054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_1711-94_0_5_line_59 |  | 50 | 70 | 0.016952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_1711-94_0_5_line_60 |  | 51 | 52 | 0.026642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_1711-94_0_5_line_61 |  | 51 | 53 | 0.02099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_1711-94_0_5_line_62 |  | 51 | 54 | 0.01893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_1711-94_0_5_line_63 |  | 52 | 67 | 0.010843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_1711-94_0_5_line_64 |  | 53 | 59 | 0.12141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_1711-94_0_5_line_65 |  | 55 | 88 | 0.024021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_1711-94_0_5_line_66 |  | 56 | 89 | 0.007828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_1711-94_0_5_line_67 |  | 57 | 58 | 0.032367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_1711-94_0_5_line_68 |  | 59 | 87 | 0.01329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_1711-94_0_5_line_69 |  | 60 | 61 | 0.013923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_1711-94_0_5_line_70 |  | 60 | 62 | 0.018024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_1711-94_0_5_line_71 |  | 61 | 93 | 0.0019415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_1711-94_0_5_line_72 |  | 62 | 112 | 0.0039326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_1711-94_0_5_line_73 |  | 63 | 64 | 0.033453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_1711-94_0_5_line_74 |  | 63 | 65 | 0.013209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_1711-94_0_5_line_75 |  | 64 | 66 | 0.0021275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_1711-94_0_5_line_76 |  | 65 | 74 | 0.042105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_1711-94_0_5_line_77 |  | 67 | 109 | 0.024883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_1711-94_0_5_line_78 |  | 67 | 108 | 0.015171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_1711-94_0_5_line_79 |  | 68 | 69 | 0.006124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_1711-94_0_5_line_80 |  | 69 | 70 | 0.024743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_1711-94_0_5_line_81 |  | 71 | 72 | 0.021383 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_1711-94_0_5_line_82 |  | 71 | 73 | 0.0060509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_1711-94_0_5_line_83 |  | 72 | 74 | 0.022648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_1711-94_0_5_line_84 |  | 73 | 75 | 0.024052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_1711-94_0_5_line_85 |  | 75 | 86 | 0.016222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_1711-94_0_5_line_86 |  | 76 | 77 | 0.017081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_1711-94_0_5_line_87 |  | 76 | 78 | 0.008316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_1711-94_0_5_line_88 |  | 77 | 79 | 0.015518 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_1711-94_0_5_line_89 |  | 79 | 80 | 0.0015016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_1711-94_0_5_line_90 |  | 80 | 81 | 0.021234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_1711-94_0_5_line_91 |  | 81 | 82 | 0.13892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_1711-94_0_5_line_92 |  | 82 | 83 | 0.044069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_1711-94_0_5_line_93 |  | 83 | 84 | 0.012296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_1711-94_0_5_line_94 |  | 84 | 106 | 0.028416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_1711-94_0_5_line_95 |  | 85 | 86 | 0.014113 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_1711-94_0_5_line_96 |  | 88 | 93 | 0.02581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_1711-94_0_5_line_97 |  | 89 | 90 | 0.020876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_1711-94_0_5_line_98 |  | 90 | 91 | 0.013629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_1711-94_0_5_line_99 |  | 91 | 92 | 0.00934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_1711-94_0_5_line_100 |  | 92 | 94 | 0.0085194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_1711-94_0_5_line_101 |  | 94 | 95 | 0.014473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_1711-94_0_5_line_102 |  | 95 | 96 | 0.016123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_1711-94_0_5_line_103 |  | 97 | 98 | 0.029142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_1711-94_0_5_line_104 |  | 98 | 99 | 0.03496 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_1711-94_0_5_line_105 |  | 100 | 101 | 0.00055566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_1711-94_0_5_line_106 |  | 103 | 105 | 0.020023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_1711-94_0_5_line_107 |  | 104 | 105 | 0.079993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_1711-94_0_5_line_108 |  | 106 | 107 | 0.028494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_1711-94_0_5_line_109 |  | 107 | 108 | 0.015005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_1711-94_0_5_line_110 |  | 109 | 110 | 0.017999 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_1711-94_0_5_line_111 |  | 110 | 111 | 0.014645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_1711-94_0_5_line_112 |  | 112 | 113 | 0.043365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_1711-94_0_5_trafo_27 | 0.63 MVA 20/0.4 kV | 114 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2682118.998 | 1223414.7672 | 2682119.1441 | 1223439.5472 | 2682120.7056 | 1223444.0254
1 | 2682139.666 | 1223361.0329 | 2682137.5011 | 1223371.7213 | 2682129.6544 | 1223381.9422 | 2682121.9677 | 1223392.6656 | 2682118.9784 | 1223411.4371 | 2682118.998 | 1223414.7672
2 | 2682128.9418 | 1223467.6457 | 2682120.7056 | 1223444.0254
3 | 2682139.666 | 1223361.0329 | 2682147.093 | 1223362.5363
4 | 2682078.8455 | 1223359.5599 | 2682087.1931 | 1223363.0551 | 2682092.187 | 1223360.6001 | 2682098.4195 | 1223349.7342 | 2682105.0403 | 1223343.7103 | 2682112.3735 | 1223341.5656 | 2682119.8245 | 1223344.0811 | 2682130.5933 | 1223351.8349 | 2682134.1288 | 1223356.1421 | 2682139.666 | 1223361.0329
5 | 2682171.0063 | 1223519.0496 | 2682155.9913 | 1223511.8042 | 2682144.6681 | 1223499.1839 | 2682128.9418 | 1223467.6457
6 | 2682147.093 | 1223362.5363 | 2682144.8982 | 1223372.0903 | 2682142.8066 | 1223380.2114 | 2682142.6749 | 1223388.1037 | 2682143.5784 | 1223389.6839
7 | 2682078.8455 | 1223359.5599 | 2682073.4225 | 1223369.4807 | 2682072.3123 | 1223379.0385 | 2682072.3742 | 1223379.4713
8 | 2682078.8455 | 1223359.5599 | 2682080.7577 | 1223354.0346
9 | 2682171.0063 | 1223519.0496 | 2682182.7132 | 1223517.6102
10 | 2682171.0063 | 1223519.0496 | 2682169.0429 | 1223481.5293
11 | 2682143.5784 | 1223389.6839 | 2682160.9086 | 1223397.3504 | 2682170.3964 | 1223400.6502 | 2682178.1384 | 1223402.4027 | 2682183.184 | 1223402.25 | 2682190.2164 | 1223400.4681 | 2682195.0888 | 1223396.933 | 2682198.7828 | 1223393.4366
12 | 2682072.3742 | 1223379.4713 | 2682076.2066 | 1223406.2661 | 2682079.1153 | 1223422.2142
13 | 2682075.3696 | 1223313.6046 | 2682077.0727 | 1223312.1368 | 2682085.4746 | 1223313.3423 | 2682089.672 | 1223321.35 | 2682088.3087 | 1223332.2163 | 2682080.7577 | 1223354.0346
14 | 2682182.7132 | 1223517.6102 | 2682198.5938 | 1223510.7108
15 | 2682166.4621 | 1223432.2102 | 2682169.0429 | 1223481.5293
16 | 2682198.7828 | 1223393.4366 | 2682201.1904 | 1223391.1578 | 2682207.4346 | 1223381.1039 | 2682213.0119 | 1223369.9178 | 2682215.9731 | 1223363.4073
17 | 2682079.1153 | 1223422.2142 | 2682081.8685 | 1223437.3095 | 2682085.7653 | 1223460.4682
18 | 2682062.8433 | 1223324.4002 | 2682075.3696 | 1223313.6046
19 | 2681971.8158 | 1223283.6455 | 2681967.9183 | 1223281.3792 | 2681959.5279 | 1223280.9857 | 2681952.401 | 1223280.8097 | 2681944.9009 | 1223281.8516 | 2681946.0189 | 1223283.2791 | 2681946.1983 | 1223284.5713 | 2681945.4654 | 1223286.5737 | 2681944.5377 | 1223287.8506 | 2681943.1424 | 1223288.9322 | 2681940.8887 | 1223289.5683 | 2681939.0028 | 1223289.9314
20 | 2681971.8158 | 1223283.6455 | 2681971.2988 | 1223284.8392 | 2681970.9451 | 1223287.3916 | 2681970.9196 | 1223289.2369 | 2681969.9486 | 1223291.4584 | 2681969.1112 | 1223292.2363 | 2681969.1052 | 1223292.6698 | 2681968.9964 | 1223294.514 | 2681968.8253 | 1223295.9237 | 2681968.4488 | 1223297.3751 | 2681968.0366 | 1223298.6703
21 | 2681971.3548 | 1223310.5017 | 2681969.7776 | 1223309.3792 | 2681968.5361 | 1223308.1057 | 2681967.9609 | 1223306.9192 | 2681967.7133 | 1223305.0701 | 2681967.6694 | 1223302.2009 | 2681968.0578 | 1223299.8825 | 2681968.0366 | 1223298.6703
22 | 2681971.3548 | 1223310.5017 | 2681969.3229 | 1223319.8133 | 2681967.8884 | 1223328.6996 | 2681965.3702 | 1223347.4331 | 2681965.2897 | 1223348.3214
23 | 2681979.0084 | 1223306.0262 | 2681975.6459 | 1223300.7097 | 2681974.5528 | 1223302.4292 | 2681971.5327 | 1223309.7036 | 2681971.3548 | 1223310.5017
24 | 2681979.0084 | 1223306.0262 | 2681981.7963 | 1223301.2948 | 2681988.2296 | 1223294.5566 | 2681992.3094 | 1223292.1556
25 | 2681992.3094 | 1223292.1556 | 2681995.983 | 1223289.9936 | 2682004.7122 | 1223286.7227 | 2682009.2787 | 1223285.303
26 | 2681965.2897 | 1223348.3214 | 2681963.4527 | 1223368.8279
27 | 2681965.2897 | 1223348.3214 | 2681962.9651 | 1223346.3993 | 2681962.7429 | 1223342.16 | 2681963.4296 | 1223335.7009
28 | 2681962.8316 | 1223385.824 | 2681963.3628 | 1223369.8316 | 2681963.4527 | 1223368.8279
29 | 2681972.5985 | 1223385.9363 | 2681972.5229 | 1223388.5646
30 | 2681962.8316 | 1223385.824 | 2681967.1501 | 1223386.1503 | 2681972.5985 | 1223385.9363
31 | 2681972.5985 | 1223385.9363 | 2681974.7392 | 1223359.3701 | 2681974.8434 | 1223358.5349
32 | 2681972.9195 | 1223412.7365 | 2681972.1913 | 1223400.0847 | 2681972.5229 | 1223388.5646
33 | 2681962.8316 | 1223385.824 | 2681962.5269 | 1223396.3825 | 2681962.653 | 1223404.1856
34 | 2681964.3199 | 1223433.043 | 2681963.5845 | 1223422.0143 | 2681962.7316 | 1223409.0494 | 2681962.653 | 1223404.1856
35 | 2682016.9765 | 1223416.5458 | 2682009.1107 | 1223416.0705 | 2681988.0137 | 1223407.1072 | 2681983.5397 | 1223407.6126 | 2681975.0422 | 1223411.6984 | 2681972.9195 | 1223412.7365
36 | 2682016.9765 | 1223416.5458 | 2682020.4795 | 1223426.0518
37 | 2682016.9765 | 1223416.5458 | 2682018.69 | 1223402.282 | 2682018.5506 | 1223395.0161
38 | 2681964.3199 | 1223433.043 | 2681964.3817 | 1223439.5704 | 2681964.1978 | 1223445.761 | 2681963.402 | 1223449.03 | 2681964.1125 | 1223451.9528 | 2681966.5471 | 1223460.759
39 | 2681935.8207 | 1223434.5517 | 2681940.1776 | 1223431.5319 | 2681949.378 | 1223425.9659 | 2681961.1198 | 1223432.4652 | 2681964.3199 | 1223433.043
40 | 2681966.5471 | 1223460.759 | 2681968.4629 | 1223471.437 | 2681970.4964 | 1223476.008
41 | 2681929.9048 | 1223447.7904 | 2681935.1699 | 1223434.9986 | 2681935.8207 | 1223434.5517
42 | 2682009.2787 | 1223285.303 | 2682013.1365 | 1223284.1037 | 2682021.3894 | 1223281.271 | 2682029.5534 | 1223277.7366
43 | 2682037.4111 | 1223272.7637 | 2682029.5534 | 1223277.7366 | 2682029.5534 | 1223277.7366
44 | 2681978.0864 | 1223501.7677 | 2681983.3422 | 1223500.6615 | 2681985.3446 | 1223508.3498 | 2681990.5494 | 1223507.0984
45 | 2681990.5494 | 1223507.0984 | 2681986.9371 | 1223496.2525 | 2681984.8486 | 1223489.2572
46 | 2681978.0864 | 1223501.7677 | 2681980.0897 | 1223508.8445 | 2681983.7787 | 1223520.7255 | 2681987.004 | 1223532.678 | 2681988.0558 | 1223536.7063
47 | 2681978.0864 | 1223501.7677 | 2681973.1192 | 1223481.9192 | 2681970.6477 | 1223476.3481 | 2681970.4964 | 1223476.008
48 | 2681979.7419 | 1223470.7807 | 2681981.9639 | 1223479.595 | 2681984.8486 | 1223489.2572
49 | 2681988.0558 | 1223536.7063 | 2681990.4903 | 1223546.0572 | 2681991.2222 | 1223549.2817
50 | 2681936.1257 | 1223336.3898 | 2681935.8305 | 1223334.6957 | 2681936.6437 | 1223332.9168 | 2681937.1857 | 1223332.1126 | 2681937.2523 | 1223323.6233
51 | 2681936.1257 | 1223336.3898 | 2681936.7702 | 1223342.4583 | 2681936.9003 | 1223346.2293 | 2681936.8557 | 1223351.3045
52 | 2681936.1257 | 1223336.3898 | 2681934.3803 | 1223335.3651 | 2681912.3658 | 1223335.718
53 | 2681920.5266 | 1223363.8048 | 2681929.8313 | 1223361.6869 | 2681936.7797 | 1223359.948 | 2681936.8557 | 1223351.3045
54 | 2681912.3658 | 1223335.718 | 2681910.5697 | 1223330.1118 | 2681901.0058 | 1223327.3672 | 2681898.3045 | 1223328.365
55 | 2681920.5266 | 1223363.8048 | 2681924.1594 | 1223377.0303 | 2681926.0182 | 1223383.9475
56 | 2681931.3596 | 1223403.8252 | 2681926.0182 | 1223383.9475
57 | 2681931.3596 | 1223403.8252 | 2681917.9228 | 1223404.7521 | 2681889.9221 | 1223406.9462
58 | 2681872.7695 | 1223418.318 | 2681889.9221 | 1223406.9462
59 | 2681889.9221 | 1223406.9462 | 2681879.8378 | 1223399.5914 | 2681877.9141 | 1223395.5556
60 | 2681995.6376 | 1223567.6871 | 2681994.8179 | 1223567.7314 | 2681989.0684 | 1223567.2408 | 2681969.8681 | 1223561.4631
61 | 2681995.6376 | 1223567.6871 | 2682000.707 | 1223567.4456 | 2682002.4742 | 1223576.2426 | 2682009.0967 | 1223578.3241
62 | 2681995.6376 | 1223567.6871 | 2681993.9509 | 1223561.304 | 2681991.2222 | 1223549.2817
63 | 2681959.4846 | 1223558.3386 | 2681969.8681 | 1223561.4631
64 | 2682009.0967 | 1223578.3241 | 2682013.8994 | 1223579.8246 | 2682031.6599 | 1223589.8093 | 2682056.038 | 1223591.7688 | 2682067.8867 | 1223588.2853 | 2682069.7427 | 1223586.7876 | 2682069.2584 | 1223585.0575 | 2682067.0169 | 1223584.8154 | 2682062.2329 | 1223585.2608 | 2682056.0484 | 1223583.8636 | 2682046.5597 | 1223578.4514 | 2682045.4219 | 1223572.9653 | 2682039.3851 | 1223568.0121 | 2682038.1979 | 1223565.5608 | 2682036.7102 | 1223555.2 | 2682035.4234 | 1223551.3177
65 | 2682020.4795 | 1223426.0518 | 2682020.8147 | 1223426.9612 | 2682030.0304 | 1223448.0909
66 | 2682018.5506 | 1223395.0161 | 2682018.4005 | 1223387.1895
67 | 2681979.7419 | 1223470.7807 | 2682011.2596 | 1223463.4148
68 | 2682031.242 | 1223538.7024 | 2682035.4234 | 1223551.3177
69 | 2682043.1521 | 1223487.3208 | 2682040.7357 | 1223473.6091
70 | 2682043.1521 | 1223487.3208 | 2682044.6573 | 1223495.8584 | 2682048.9111 | 1223504.1905
71 | 2682040.3988 | 1223471.697 | 2682040.7357 | 1223473.6091
72 | 2682048.9111 | 1223504.1905 | 2682050.6993 | 1223507.693
73 | 2681939.064 | 1223479.3599 | 2681937.54 | 1223476.0256 | 2681933.9165 | 1223467.0919 | 2681936.5284 | 1223461.3684 | 2681933.0442 | 1223457.1843 | 2681929.0965 | 1223449.7584
74 | 2681939.064 | 1223479.3599 | 2681931.0788 | 1223483.1526 | 2681927.363 | 1223480.8547
75 | 2681929.9048 | 1223447.7904 | 2681929.0965 | 1223449.7584
76 | 2681892.1497 | 1223457.8 | 2681908.5712 | 1223469.2335 | 2681927.363 | 1223480.8547
77 | 2681953.7968 | 1223541.8047 | 2681950.1438 | 1223551.5388 | 2681954.9828 | 1223553.1621 | 2681960.5553 | 1223554.94 | 2681959.4846 | 1223558.3386
78 | 2681959.4846 | 1223558.3386 | 2681949.9379 | 1223555.472 | 2681944.7482 | 1223555.0936
79 | 2681867.337 | 1223373.191 | 2681865.2861 | 1223367.4206
80 | 2681867.337 | 1223373.191 | 2681867.5791 | 1223373.8722 | 2681877.9141 | 1223395.5556
81 | 2681872.7695 | 1223418.318 | 2681882.0685 | 1223437.5736
82 | 2681872.7695 | 1223418.318 | 2681867.4773 | 1223421.2516
83 | 2681892.1497 | 1223457.8 | 2681891.5585 | 1223457.2248 | 2681882.0685 | 1223437.5736
84 | 2681846.4856 | 1223432.9885 | 2681848.2067 | 1223431.9339 | 2681867.4773 | 1223421.2516
85 | 2681846.4856 | 1223432.9885 | 2681833.6361 | 1223440.8619 | 2681832.6413 | 1223441.4438
86 | 2681809.8785 | 1223392.0692 | 2681795.1213 | 1223400.6715
87 | 2681810.4248 | 1223383.7711 | 2681809.8785 | 1223392.0692
88 | 2681781.6578 | 1223408.3884 | 2681790.4055 | 1223403.4205 | 2681795.1213 | 1223400.6715
89 | 2681780.352 | 1223409.1299 | 2681781.6578 | 1223408.3884
90 | 2681764.3813 | 1223421.8421 | 2681766.4344 | 1223417.0338 | 2681780.352 | 1223409.1299
91 | 2681764.3813 | 1223421.8421 | 2681767.0083 | 1223429.3611 | 2681781.1134 | 1223462.0212 | 2681793.7989 | 1223484.2882 | 2681806.1709 | 1223507.2848 | 2681814.6874 | 1223516.1411 | 2681832.4886 | 1223541.9475
92 | 2681832.4886 | 1223541.9475 | 2681845.0495 | 1223533.5479 | 2681871.5201 | 1223521.8039 | 2681871.5201 | 1223521.8039
93 | 2681871.5201 | 1223521.8039 | 2681877.9745 | 1223520.6696 | 2681883.4541 | 1223522.3883
94 | 2681883.4541 | 1223522.3883 | 2681884.5367 | 1223522.7279 | 2681888.6188 | 1223526.998 | 2681898.7031 | 1223539.3006 | 2681903.6253 | 1223541.6775
95 | 2681820.4598 | 1223448.5702 | 2681832.6413 | 1223441.4438
96 | 2682030.0304 | 1223448.0909 | 2682035.1874 | 1223459.9148 | 2682040.2471 | 1223470.8363 | 2682040.3988 | 1223471.697
97 | 2682019.3094 | 1223366.3579 | 2682019.212 | 1223366.6096 | 2682018.3105 | 1223382.4968 | 2682018.4005 | 1223387.1895
98 | 2682019.3094 | 1223366.3579 | 2682024.2294 | 1223353.6477 | 2682024.2294 | 1223353.6477
99 | 2682024.2294 | 1223353.6477 | 2682031.5484 | 1223347.8452
100 | 2682038.2242 | 1223342.5525 | 2682031.5484 | 1223347.8452
101 | 2682038.2242 | 1223342.5525 | 2682038.4 | 1223342.4132 | 2682049.9281 | 1223334.0389
102 | 2682049.9281 | 1223334.0389 | 2682060.9464 | 1223326.035 | 2682062.8433 | 1223324.4002
103 | 2682085.7653 | 1223460.4682 | 2682087.5392 | 1223471.0104 | 2682089.9597 | 1223489.3023
104 | 2682089.9597 | 1223489.3023 | 2682090.0804 | 1223490.2139 | 2682101.4514 | 1223508.1717 | 2682109.0901 | 1223518.4246
105 | 2682215.9731 | 1223363.4073 | 2682216.2032 | 1223362.9015
106 | 2682213.9967 | 1223498.4514 | 2682204.6642 | 1223508.0735 | 2682198.5938 | 1223510.7108
107 | 2682213.9967 | 1223498.4514 | 2682226.1666 | 1223503.0225 | 2682241.4725 | 1223506.2249 | 2682270.9956 | 1223509.0903 | 2682290.7761 | 1223500.1824
108 | 2681903.6253 | 1223541.6775 | 2681909.1075 | 1223544.3249 | 2681919.3777 | 1223547.5239 | 2681930.3146 | 1223551.5346
109 | 2681930.3146 | 1223551.5346 | 2681938.8461 | 1223554.6632 | 2681944.7482 | 1223555.0936
110 | 2681953.7968 | 1223541.8047 | 2681951.6323 | 1223540.9299 | 2681956.0111 | 1223525.8897
111 | 2681943.7781 | 1223520.3413 | 2681956.3847 | 1223524.6065 | 2681956.0111 | 1223525.8897
112 | 2682050.6993 | 1223507.693 | 2682061.184 | 1223528.2302 | 2682071.9019 | 1223545.4774

## bus_geodata
| x | y | coords
0 | 2682118.998 | 1223414.7672
1 | 2682120.7056 | 1223444.0254
2 | 2682139.666 | 1223361.0329
3 | 2682128.9418 | 1223467.6457
4 | 2682147.093 | 1223362.5363
5 | 2682078.8455 | 1223359.5599
6 | 2682171.0063 | 1223519.0496
7 | 2682143.5784 | 1223389.6839
8 | 2682072.3742 | 1223379.4713
9 | 2682080.7577 | 1223354.0346
10 | 2682182.7132 | 1223517.6102
11 | 2682169.0429 | 1223481.5293
12 | 2682198.7828 | 1223393.4366
13 | 2682079.1153 | 1223422.2142
14 | 2682075.3696 | 1223313.6046
15 | 2681939.0028 | 1223289.9314
16 | 2681971.8158 | 1223283.6455
17 | 2681968.0366 | 1223298.6703
18 | 2681971.3548 | 1223310.5017
19 | 2681979.0084 | 1223306.0262
20 | 2681992.3094 | 1223292.1556
21 | 2681965.2897 | 1223348.3214
22 | 2681963.4296 | 1223335.7009
23 | 2681963.4527 | 1223368.8279
24 | 2681972.5985 | 1223385.9363
25 | 2681972.5229 | 1223388.5646
26 | 2681962.8316 | 1223385.824
27 | 2681974.8434 | 1223358.5349
28 | 2681962.653 | 1223404.1856
29 | 2681972.9195 | 1223412.7365
30 | 2682016.9765 | 1223416.5458
31 | 2681964.3199 | 1223433.043
32 | 2681966.5471 | 1223460.759
33 | 2681935.8207 | 1223434.5517
34 | 2682009.2787 | 1223285.303
35 | 2682037.4111 | 1223272.7637
36 | 2682029.5534 | 1223277.7366
37 | 2681990.5494 | 1223507.0984
38 | 2681978.0864 | 1223501.7677
39 | 2681984.8486 | 1223489.2572
40 | 2681988.0558 | 1223536.7063
41 | 2681970.4964 | 1223476.008
42 | 2681937.2523 | 1223323.6233
43 | 2681936.1257 | 1223336.3898
44 | 2681936.8557 | 1223351.3045
45 | 2681912.3658 | 1223335.718
46 | 2681920.5266 | 1223363.8048
47 | 2681898.3045 | 1223328.365
48 | 2681926.0182 | 1223383.9475
49 | 2681931.3596 | 1223403.8252
50 | 2681889.9221 | 1223406.9462
51 | 2681995.6376 | 1223567.6871
52 | 2681969.8681 | 1223561.4631
53 | 2682009.0967 | 1223578.3241
54 | 2681991.2222 | 1223549.2817
55 | 2682020.4795 | 1223426.0518
56 | 2682018.5506 | 1223395.0161
57 | 2681979.7419 | 1223470.7807
58 | 2682011.2596 | 1223463.4148
59 | 2682035.4234 | 1223551.3177
60 | 2682043.1521 | 1223487.3208
61 | 2682040.7357 | 1223473.6091
62 | 2682048.9111 | 1223504.1905
63 | 2681939.064 | 1223479.3599
64 | 2681929.0965 | 1223449.7584
65 | 2681927.363 | 1223480.8547
66 | 2681929.9048 | 1223447.7904
67 | 2681959.4846 | 1223558.3386
68 | 2681865.2861 | 1223367.4206
69 | 2681867.337 | 1223373.191
70 | 2681877.9141 | 1223395.5556
71 | 2681872.7695 | 1223418.318
72 | 2681882.0685 | 1223437.5736
73 | 2681867.4773 | 1223421.2516
74 | 2681892.1497 | 1223457.8
75 | 2681846.4856 | 1223432.9885
76 | 2681809.8785 | 1223392.0692
77 | 2681795.1213 | 1223400.6715
78 | 2681810.4248 | 1223383.7711
79 | 2681781.6578 | 1223408.3884
80 | 2681780.352 | 1223409.1299
81 | 2681764.3813 | 1223421.8421
82 | 2681832.4886 | 1223541.9475
83 | 2681871.5201 | 1223521.8039
84 | 2681883.4541 | 1223522.3883
85 | 2681820.4598 | 1223448.5702
86 | 2681832.6413 | 1223441.4438
87 | 2682031.242 | 1223538.7024
88 | 2682030.0304 | 1223448.0909
89 | 2682018.4005 | 1223387.1895
90 | 2682019.3094 | 1223366.3579
91 | 2682024.2294 | 1223353.6477
92 | 2682031.5484 | 1223347.8452
93 | 2682040.3988 | 1223471.697
94 | 2682038.2242 | 1223342.5525
95 | 2682049.9281 | 1223334.0389
96 | 2682062.8433 | 1223324.4002
97 | 2682085.7653 | 1223460.4682
98 | 2682089.9597 | 1223489.3023
99 | 2682109.0901 | 1223518.4246
100 | 2682215.9731 | 1223363.4073
101 | 2682216.2032 | 1223362.9015
102 | 2682166.4621 | 1223432.2102
103 | 2682198.5938 | 1223510.7108
104 | 2682290.7761 | 1223500.1824
105 | 2682213.9967 | 1223498.4514
106 | 2681903.6253 | 1223541.6775
107 | 2681930.3146 | 1223551.5346
108 | 2681944.7482 | 1223555.0936
109 | 2681953.7968 | 1223541.8047
110 | 2681956.0111 | 1223525.8897
111 | 2681943.7781 | 1223520.3413
112 | 2682050.6993 | 1223507.693
113 | 2682071.9019 | 1223545.4774
114 | 2681969.4794 | 1223433.9813

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97441 | -0.49385 | 0.0041392 | 0.0010374
1 | 0.9739 | -0.504 | 0.0018882 | 0.00047323
2 | 0.97568 | -0.46898 | 0 | 0
3 | 0.97351 | -0.51174 | 0.0042062 | 0.0010542
4 | 0.97561 | -0.47023 | 0 | 0
5 | 0.97799 | -0.42363 | 0 | 0
6 | 0.9727 | -0.52774 | 0 | 0
7 | 0.97538 | -0.47485 | 0.00081394 | 0.00020399
8 | 0.97749 | -0.43333 | 0.0042952 | 0.0010765
9 | 0.9783 | -0.41758 | 0.0042422 | 0.0010632
10 | 0.97265 | -0.52878 | 0 | 0
11 | 0.97242 | -0.53317 | 0.0039119 | 0.00098043
12 | 0.97492 | -0.48394 | 0.0046905 | 0.0011755
13 | 0.97667 | -0.44961 | 0.008569 | 0.0021476
14 | 0.98135 | -0.35794 | 0.0030802 | 0.00077197
15 | 0.99275 | -0.13878 | 0.0034471 | 0.00086393
16 | 0.99288 | -0.13631 | 0 | 0
17 | 0.99293 | -0.13535 | 0.0037798 | 0.00094731
18 | 0.99301 | -0.13364 | 0 | 0
19 | 0.9928 | -0.1377 | 0 | 0
20 | 0.99256 | -0.14237 | 0.0028453 | 0.00071309
21 | 0.99374 | -0.11961 | 0 | 0
22 | 0.99348 | -0.12469 | 0.020898 | 0.0052376
23 | 0.99452 | -0.1045 | 0.014523 | 0.0036398
24 | 0.99471 | -0.1007 | 0 | 0
25 | 0.99455 | -0.10387 | 0.01397 | 0.0035012
26 | 0.99539 | -0.087683 | 0 | 0
27 | 0.99436 | -0.10755 | 0.014142 | 0.0035442
28 | 0.99715 | -0.054255 | 0.0074401 | 0.0018647
29 | 0.99317 | -0.13014 | 0 | 0
30 | 0.9905 | -0.18133 | 0 | 0
31 | 1 | 0 | -0.49989 | -0.12737
32 | 0.99805 | -0.037027 | 0 | 0
33 | 0.99617 | -0.072653 | 0 | 0
34 | 0.99239 | -0.14583 | 0.0022775 | 0.00057081
35 | 0.99218 | -0.14977 | 0.0044498 | 0.0011152
36 | 0.99222 | -0.14904 | 0.00392 | 0.00098244
37 | 0.99324 | -0.12863 | 0 | 0
38 | 0.99364 | -0.12098 | 0 | 0
39 | 0.99284 | -0.13632 | 0.011957 | 0.0029967
40 | 0.98994 | -0.19176 | 0 | 0
41 | 0.99695 | -0.057879 | 0.017022 | 0.004266
42 | 0.97862 | -0.41228 | 0.013024 | 0.0032641
43 | 0.97877 | -0.40917 | 0 | 0
44 | 0.97902 | -0.40427 | 0.013059 | 0.0032729
45 | 0.97866 | -0.41134 | 0 | 0
46 | 0.97975 | -0.38996 | 0 | 0
47 | 0.97858 | -0.41304 | 0.0049871 | 0.0012499
48 | 0.98035 | -0.37818 | 0.0085846 | 0.0021515
49 | 0.98111 | -0.36339 | 0 | 0
50 | 0.98263 | -0.33368 | 0 | 0
51 | 0.98684 | -0.25158 | 0 | 0
52 | 0.9846 | -0.295 | 0.0086663 | 0.002172
53 | 0.98663 | -0.25569 | 0 | 0
54 | 0.98862 | -0.21716 | 0.0081568 | 0.0020443
55 | 0.9902 | -0.18711 | 0.0036197 | 0.00090719
56 | 0.98867 | -0.21635 | 0.0036886 | 0.00092444
57 | 0.99265 | -0.14014 | 0 | 0
58 | 0.99231 | -0.1466 | 0.011267 | 0.0028238
59 | 0.98541 | -0.2795 | 0.0048793 | 0.0012229
60 | 0.98889 | -0.21245 | 0 | 0
61 | 0.98907 | -0.20899 | 0.0034088 | 0.00085432
62 | 0.98866 | -0.21693 | 0.0043211 | 0.001083
63 | 0.9913 | -0.16599 | 0 | 0
64 | 0.99422 | -0.11004 | 0.032322 | 0.0081006
65 | 0.99014 | -0.18817 | 0.010707 | 0.0026835
66 | 0.99447 | -0.10529 | 0 | 0
67 | 0.98378 | -0.31104 | 0 | 0
68 | 0.98188 | -0.3484 | 0.0075906 | 0.0019024
69 | 0.98192 | -0.34756 | 0.0094436 | 0.0023668
70 | 0.98231 | -0.33995 | 0.0034319 | 0.00086012
71 | 0.98377 | -0.31141 | 0 | 0
72 | 0.98517 | -0.28421 | 0.010696 | 0.0026806
73 | 0.98372 | -0.31257 | 0.0030657 | 0.00076834
74 | 0.98688 | -0.25114 | 0.002404 | 0.00060249
75 | 0.98355 | -0.31585 | 0.0036777 | 0.00092172
76 | 0.97406 | -0.50113 | 0.0057698 | 0.0014461
77 | 0.97431 | -0.49609 | 0.002071 | 0.00051903
78 | 0.97398 | -0.5027 | 0.010273 | 0.0025746
79 | 0.97458 | -0.49093 | 0.0050709 | 0.0012709
80 | 0.97461 | -0.49029 | 0.0031069 | 0.00077866
81 | 0.97513 | -0.48005 | 0 | 0
82 | 0.97853 | -0.41333 | 0 | 0
83 | 0.97961 | -0.39226 | 0.007538 | 0.0018892
84 | 0.97999 | -0.3847 | 0.0050171 | 0.0012574
85 | 0.98346 | -0.31749 | 0.0020039 | 0.00050223
86 | 0.98349 | -0.31698 | 0.0018717 | 0.00046909
87 | 0.98533 | -0.28094 | 0.0060543 | 0.0015173
88 | 0.98957 | -0.19926 | 0.0085919 | 0.0021533
89 | 0.98804 | -0.22854 | 0.0052985 | 0.0013279
90 | 0.98645 | -0.25913 | 0.0036698 | 0.00091974
91 | 0.98546 | -0.27826 | 0.0044704 | 0.0011204
92 | 0.98482 | -0.29064 | 0.0027054 | 0.00067803
93 | 0.9891 | -0.20839 | 0.0025201 | 0.00063159
94 | 0.98426 | -0.30154 | 0.0021365 | 0.00053546
95 | 0.98333 | -0.31951 | 0.0028007 | 0.00070193
96 | 0.98234 | -0.33877 | 0.002044 | 0.00051227
97 | 0.97623 | -0.45815 | 0.0032069 | 0.00080372
98 | 0.97599 | -0.46285 | 0.0063731 | 0.0015972
99 | 0.97591 | -0.46442 | 0.0024501 | 0.00061405
100 | 0.9748 | -0.4862 | 0.0027239 | 0.00068267
101 | 0.9748 | -0.48621 | 0.00080519 | 0.0002018
102 | 0.97224 | -0.53674 | 0.0039246 | 0.00098359
103 | 0.97257 | -0.5303 | 0.0020117 | 0.00050418
104 | 0.97231 | -0.53541 | 0.0027683 | 0.00069381
105 | 0.97252 | -0.53133 | 0 | 0
106 | 0.98102 | -0.36469 | 0.0045475 | 0.0011397
107 | 0.98217 | -0.34231 | 0.0099268 | 0.0024879
108 | 0.98291 | -0.32787 | 0.0082124 | 0.0020582
109 | 0.9833 | -0.32029 | 0 | 0
110 | 0.98296 | -0.32699 | 0.010955 | 0.0027456
111 | 0.98283 | -0.32955 | 0.0096821 | 0.0024266
112 | 0.98863 | -0.2176 | 0.0065554 | 0.0016429
113 | 0.98851 | -0.21996 | 0.0030532 | 0.00076521
114 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.01874 | 0.0047037 | -0.018731 | -0.0046982 | 9.0684e-06 | 5.4362e-06 | 0.02862 | 0.02862 | 0.02862 | 0.97441 | -0.49385 | 0.9739 | -0.504 | 7.8627
1 | -0.022879 | -0.005741 | 0.022906 | 0.0057577 | 2.7159e-05 | 1.6642e-05 | 0.034941 | 0.034941 | 0.034941 | 0.97441 | -0.49385 | 0.97568 | -0.46898 | 9.5991
2 | 0.016843 | 0.004225 | -0.016836 | -0.0042213 | 6.2128e-06 | 3.665e-06 | 0.025735 | 0.025735 | 0.025735 | 0.9739 | -0.504 | 0.97351 | -0.51174 | 7.0701
3 | 0.00904 | 0.0022665 | -0.0090394 | -0.0022663 | 5.3862e-07 | 2.5035e-07 | 0.013787 | 0.013787 | 0.013787 | 0.97568 | -0.46898 | 0.97561 | -0.47023 | 3.7877
4 | -0.031946 | -0.0080242 | 0.032015 | 0.0080676 | 6.9296e-05 | 4.3375e-05 | 0.048728 | 0.048727 | 0.048728 | 0.97568 | -0.46898 | 0.97799 | -0.42363 | 13.3867
5 | 0.01263 | 0.0031672 | -0.012621 | -0.0031619 | 9.6259e-06 | 5.305e-06 | 0.019306 | 0.019306 | 0.019306 | 0.97351 | -0.51174 | 0.9727 | -0.52774 | 5.3039
6 | 0.0090394 | 0.0022663 | -0.0090374 | -0.0022653 | 1.989e-06 | 9.2462e-07 | 0.013787 | 0.013787 | 0.013787 | 0.97561 | -0.47023 | 0.97538 | -0.47485 | 3.7877
7 | 0.024929 | 0.0062591 | -0.024917 | -0.006252 | 1.1529e-05 | 7.1106e-06 | 0.037933 | 0.037934 | 0.037934 | 0.97799 | -0.42363 | 0.97749 | -0.43333 | 10.4213
8 | -0.056944 | -0.014327 | 0.056961 | 0.014337 | 1.6466e-05 | 1.0465e-05 | 0.086661 | 0.086661 | 0.086661 | 0.97799 | -0.42363 | 0.9783 | -0.41758 | 23.8079
9 | 0.0047813 | 0.0011972 | -0.0047811 | -0.0011972 | 2.3593e-07 | 5.0168e-09 | 0.0073139 | 0.007314 | 0.007314 | 0.9727 | -0.52774 | 0.97265 | -0.52878 | 2.0093
10 | 0.0078392 | 0.0019647 | -0.0078372 | -0.0019638 | 2.0263e-06 | 8.3059e-07 | 0.011992 | 0.011992 | 0.011992 | 0.9727 | -0.52774 | 0.97242 | -0.53317 | 3.2946
11 | 0.0082235 | 0.0020613 | -0.0082199 | -0.0020598 | 3.5616e-06 | 1.5267e-06 | 0.012546 | 0.012546 | 0.012546 | 0.97538 | -0.47485 | 0.97492 | -0.48394 | 3.4467
12 | 0.020622 | 0.0051755 | -0.020606 | -0.0051658 | 1.5997e-05 | 9.6958e-06 | 0.031395 | 0.031395 | 0.031395 | 0.97749 | -0.43333 | 0.97667 | -0.44961 | 8.6251
13 | -0.061203 | -0.0154 | 0.061378 | 0.015512 | 0.00017497 | 0.00011131 | 0.093113 | 0.093113 | 0.093113 | 0.9783 | -0.41758 | 0.98135 | -0.35794 | 25.5806
14 | 0.0047811 | 0.0011972 | -0.0047807 | -0.0011972 | 3.4734e-07 | 7.4183e-09 | 0.007314 | 0.0073141 | 0.0073141 | 0.97265 | -0.52878 | 0.97257 | -0.5303 | 2.0094
15 | 0.0039253 | 0.00098341 | -0.0039246 | -0.00098359 | 6.6816e-07 | -1.8494e-07 | 0.0060064 | 0.0060066 | 0.0060066 | 0.97242 | -0.53317 | 0.97224 | -0.53674 | 1.6502
16 | 0.0035295 | 0.00088427 | -0.0035291 | -0.00088446 | 3.7872e-07 | -1.9153e-07 | 0.0053869 | 0.005387 | 0.005387 | 0.97492 | -0.48394 | 0.9748 | -0.4862 | 1.48
17 | 0.012037 | 0.0030182 | -0.012032 | -0.0030156 | 4.8975e-06 | 2.6487e-06 | 0.01834 | 0.01834 | 0.01834 | 0.97667 | -0.44961 | 0.97623 | -0.45815 | 5.0385
18 | -0.064458 | -0.016284 | 0.064517 | 0.016321 | 5.9293e-05 | 3.7738e-05 | 0.097783 | 0.097783 | 0.097783 | 0.98135 | -0.35794 | 0.98234 | -0.33877 | 26.8636
19 | -0.0034471 | -0.00086393 | 0.0034475 | 0.00086367 | 4.0509e-07 | -2.6402e-07 | 0.0051669 | 0.0051667 | 0.0051669 | 0.99275 | -0.13878 | 0.99288 | -0.13631 | 1.4195
20 | -0.0034475 | -0.00086367 | 0.0034477 | 0.00086357 | 1.5866e-07 | -1.0346e-07 | 0.0051667 | 0.0051666 | 0.0051667 | 0.99288 | -0.13631 | 0.99293 | -0.13535 | 1.4194
21 | -0.0072275 | -0.0018109 | 0.0072281 | 0.0018111 | 5.8647e-07 | 2.0289e-07 | 0.010831 | 0.010831 | 0.010831 | 0.99293 | -0.13535 | 0.99301 | -0.13364 | 2.9756
22 | -0.02073 | -0.0051972 | 0.020743 | 0.0052056 | 1.3869e-05 | 8.3802e-06 | 0.031064 | 0.031063 | 0.031064 | 0.99301 | -0.13364 | 0.99374 | -0.11961 | 8.5339
23 | 0.013501 | 0.0033861 | -0.013499 | -0.0033846 | 2.613e-06 | 1.4522e-06 | 0.020232 | 0.020233 | 0.020233 | 0.99301 | -0.13364 | 0.9928 | -0.1377 | 5.5584
24 | 0.013499 | 0.0033846 | -0.013496 | -0.003383 | 2.9998e-06 | 1.6673e-06 | 0.020233 | 0.020233 | 0.020233 | 0.9928 | -0.1377 | 0.99256 | -0.14237 | 5.5584
25 | 0.010651 | 0.0026699 | -0.010649 | -0.002669 | 1.756e-06 | 8.8647e-07 | 0.015967 | 0.015967 | 0.015967 | 0.99256 | -0.14237 | 0.99239 | -0.14583 | 4.3866
26 | -0.041647 | -0.010446 | 0.041677 | 0.010465 | 3.0028e-05 | 1.8951e-05 | 0.062364 | 0.062364 | 0.062364 | 0.99374 | -0.11961 | 0.99452 | -0.1045 | 17.1331
27 | 0.020903 | 0.0052407 | -0.020898 | -0.0052376 | 5.0545e-06 | 3.0567e-06 | 0.031301 | 0.031301 | 0.031301 | 0.99374 | -0.11961 | 0.99348 | -0.12469 | 8.5992
28 | -0.0562 | -0.014105 | 0.056245 | 0.014134 | 4.5106e-05 | 2.8647e-05 | 0.084094 | 0.084094 | 0.084094 | 0.99452 | -0.1045 | 0.99539 | -0.087683 | 23.1028
29 | 0.1385 | 0.035299 | -0.13848 | -0.035285 | 2.1207e-05 | 1.3504e-05 | 0.2074 | 0.2074 | 0.2074 | 0.99471 | -0.1007 | 0.99455 | -0.10387 | 28.4886
30 | -0.15265 | -0.038845 | 0.15274 | 0.038906 | 9.5827e-05 | 6.1075e-05 | 0.22856 | 0.22856 | 0.22856 | 0.99471 | -0.1007 | 0.99539 | -0.087683 | 31.3955
31 | 0.014146 | 0.0035468 | -0.014142 | -0.0035442 | 4.6174e-06 | 2.5983e-06 | 0.021162 | 0.021162 | 0.021162 | 0.99471 | -0.1007 | 0.99436 | -0.10755 | 5.8138
32 | 0.12451 | 0.031784 | -0.12435 | -0.031683 | 0.0001578 | 0.00010037 | 0.1865 | 0.1865 | 0.1865 | 0.99455 | -0.10387 | 0.99317 | -0.13014 | 25.6176
33 | -0.20899 | -0.05304 | 0.20933 | 0.053255 | 0.00033664 | 0.00021497 | 0.31265 | 0.31265 | 0.31265 | 0.99539 | -0.087683 | 0.99715 | -0.054255 | 42.9468
34 | -0.21677 | -0.05512 | 0.21733 | 0.055483 | 0.00056819 | 0.00036288 | 0.32376 | 0.32375 | 0.32376 | 0.99715 | -0.054255 | 1 | 0 | 44.4719
35 | 0.12435 | 0.031683 | -0.12405 | -0.031489 | 0.00030636 | 0.00019486 | 0.1865 | 0.1865 | 0.1865 | 0.99317 | -0.13014 | 0.9905 | -0.18133 | 25.6176
36 | 0.032111 | 0.0080616 | -0.032102 | -0.0080561 | 8.8425e-06 | 5.5289e-06 | 0.048245 | 0.048245 | 0.048245 | 0.9905 | -0.18133 | 0.9902 | -0.18711 | 13.254
37 | 0.091936 | 0.023427 | -0.091781 | -0.023328 | 0.00015506 | 9.8961e-05 | 0.13825 | 0.13825 | 0.13825 | 0.9905 | -0.18133 | 0.98867 | -0.21635 | 37.9813
38 | 0.15232 | 0.038998 | -0.15204 | -0.038824 | 0.00027263 | 0.00017374 | 0.22694 | 0.22694 | 0.22694 | 1 | 0 | 0.99805 | -0.037027 | 31.1732
39 | 0.12859 | 0.032895 | -0.12814 | -0.032607 | 0.00045047 | 0.00028787 | 0.19159 | 0.19159 | 0.19159 | 1 | 0 | 0.99617 | -0.072653 | 52.6337
40 | 0.15204 | 0.038824 | -0.15189 | -0.038726 | 0.00015307 | 9.7552e-05 | 0.22694 | 0.22694 | 0.22694 | 0.99805 | -0.037027 | 0.99695 | -0.057879 | 31.1733
41 | 0.12814 | 0.032607 | -0.12794 | -0.032478 | 0.00020121 | 0.00012858 | 0.19159 | 0.19159 | 0.19159 | 0.99617 | -0.072653 | 0.99447 | -0.10529 | 52.6337
42 | 0.0083712 | 0.0020982 | -0.0083699 | -0.0020976 | 1.2799e-06 | 5.3929e-07 | 0.012552 | 0.012552 | 0.012552 | 0.99239 | -0.14583 | 0.99222 | -0.14904 | 3.4484
43 | -0.0044498 | -0.0011152 | 0.00445 | 0.0011152 | 1.553e-07 | -2.0707e-08 | 0.0066736 | 0.0066735 | 0.0066736 | 0.99218 | -0.14977 | 0.99222 | -0.14904 | 1.8334
44 | -0.023238 | -0.0058286 | 0.023247 | 0.0058338 | 8.4859e-06 | 5.1892e-06 | 0.034816 | 0.034816 | 0.034816 | 0.99324 | -0.12863 | 0.99364 | -0.12098 | 9.5647
45 | 0.023238 | 0.0058286 | -0.02323 | -0.0058234 | 8.5146e-06 | 5.207e-06 | 0.034816 | 0.034816 | 0.034816 | 0.99324 | -0.12863 | 0.99284 | -0.13632 | 9.5648
46 | 0.11121 | 0.028364 | -0.11083 | -0.028122 | 0.00037873 | 0.00024192 | 0.16672 | 0.16672 | 0.16672 | 0.99364 | -0.12098 | 0.98994 | -0.19176 | 45.8024
47 | -0.13446 | -0.034198 | 0.13487 | 0.03446 | 0.00041014 | 0.00026214 | 0.20154 | 0.20154 | 0.20154 | 0.99364 | -0.12098 | 0.99695 | -0.057879 | 55.367
48 | 0.011273 | 0.0028267 | -0.011271 | -0.0028256 | 2.0525e-06 | 1.0657e-06 | 0.016895 | 0.016895 | 0.016895 | 0.99284 | -0.13632 | 0.99265 | -0.14014 | 4.6416
49 | 0.11083 | 0.028122 | -0.1107 | -0.028036 | 0.00013518 | 8.6351e-05 | 0.16672 | 0.16672 | 0.16672 | 0.98994 | -0.19176 | 0.98862 | -0.21716 | 45.8024
50 | -0.013024 | -0.0032641 | 0.013026 | 0.0032652 | 1.9317e-06 | 1.0712e-06 | 0.019803 | 0.019803 | 0.019803 | 0.97862 | -0.41228 | 0.97877 | -0.40917 | 5.4405
51 | -0.018014 | -0.0045151 | 0.018018 | 0.0045176 | 4.2052e-06 | 2.5033e-06 | 0.027387 | 0.027386 | 0.027387 | 0.97877 | -0.40917 | 0.97902 | -0.40427 | 7.5238
52 | 0.004988 | 0.0012499 | -0.0049875 | -0.0012499 | 5.1696e-07 | 2.959e-08 | 0.0075831 | 0.0075832 | 0.0075832 | 0.97877 | -0.40917 | 0.97866 | -0.41134 | 2.0833
53 | -0.031077 | -0.0077905 | 0.031098 | 0.0078038 | 2.1209e-05 | 1.3255e-05 | 0.047235 | 0.047235 | 0.047235 | 0.97902 | -0.40427 | 0.97975 | -0.38996 | 12.9766
54 | 0.0049875 | 0.0012499 | -0.0049871 | -0.0012499 | 4.0362e-07 | 2.3156e-08 | 0.0075832 | 0.0075833 | 0.0075833 | 0.97866 | -0.41134 | 0.97858 | -0.41304 | 2.0833
55 | -0.031098 | -0.0078038 | 0.031116 | 0.0078147 | 1.7468e-05 | 1.0916e-05 | 0.047235 | 0.047235 | 0.047235 | 0.97975 | -0.38996 | 0.98035 | -0.37818 | 12.9766
56 | -0.039701 | -0.0099662 | 0.039729 | 0.0099839 | 2.8032e-05 | 1.7681e-05 | 0.060265 | 0.060265 | 0.060265 | 0.98035 | -0.37818 | 0.98111 | -0.36339 | 16.5562
57 | -0.039729 | -0.0099839 | 0.039785 | 0.010019 | 5.6431e-05 | 3.5592e-05 | 0.060265 | 0.060264 | 0.060265 | 0.98111 | -0.36339 | 0.98263 | -0.33368 | 16.5562
58 | -0.060264 | -0.015156 | 0.060328 | 0.015197 | 6.4174e-05 | 4.0811e-05 | 0.091277 | 0.091277 | 0.091277 | 0.98263 | -0.33368 | 0.98377 | -0.31141 | 25.0762
59 | 0.020479 | 0.0051368 | -0.020473 | -0.0051331 | 6.1143e-06 | 3.6985e-06 | 0.031013 | 0.031013 | 0.031013 | 0.98263 | -0.33368 | 0.98231 | -0.33995 | 8.52
60 | 0.091424 | 0.023136 | -0.091234 | -0.023015 | 0.00019008 | 0.00012131 | 0.13793 | 0.13793 | 0.13793 | 0.98684 | -0.25158 | 0.9846 | -0.295 | 37.8939
61 | 0.010949 | 0.0027478 | -0.010946 | -0.0027467 | 2.1456e-06 | 1.1051e-06 | 0.01651 | 0.01651 | 0.01651 | 0.98684 | -0.25158 | 0.98663 | -0.25569 | 4.5358
62 | -0.10237 | -0.025884 | 0.10254 | 0.025992 | 0.00016933 | 0.00010813 | 0.15444 | 0.15444 | 0.15444 | 0.98684 | -0.25158 | 0.98862 | -0.21716 | 42.4296
63 | 0.082567 | 0.020843 | -0.082504 | -0.020802 | 6.3369e-05 | 4.0419e-05 | 0.12484 | 0.12484 | 0.12484 | 0.9846 | -0.295 | 0.98378 | -0.31104 | 34.2958
64 | 0.010946 | 0.0027467 | -0.010934 | -0.0027403 | 1.2411e-05 | 6.3945e-06 | 0.01651 | 0.016511 | 0.016511 | 0.98663 | -0.25569 | 0.98541 | -0.2795 | 4.5359
65 | 0.028482 | 0.0071489 | -0.028466 | -0.0071387 | 1.6505e-05 | 1.0255e-05 | 0.042805 | 0.042805 | 0.042805 | 0.9902 | -0.18711 | 0.98957 | -0.19926 | 11.7597
66 | 0.088092 | 0.022404 | -0.08804 | -0.022371 | 5.1692e-05 | 3.2983e-05 | 0.1327 | 0.1327 | 0.1327 | 0.98867 | -0.21635 | 0.98804 | -0.22854 | 36.4562
67 | 0.011271 | 0.0028256 | -0.011267 | -0.0028238 | 3.4648e-06 | 1.7992e-06 | 0.016895 | 0.016896 | 0.016896 | 0.99265 | -0.14014 | 0.99231 | -0.1466 | 4.6417
68 | 0.0060547 | 0.0015174 | -0.0060543 | -0.0015173 | 4.1661e-07 | 9.7338e-08 | 0.0091429 | 0.009143 | 0.009143 | 0.98541 | -0.2795 | 0.98533 | -0.28094 | 2.5118
69 | -0.013933 | -0.0034926 | 0.013936 | 0.0034939 | 2.2951e-06 | 1.2902e-06 | 0.020966 | 0.020966 | 0.020966 | 0.98889 | -0.21245 | 0.98907 | -0.20899 | 5.7599
70 | 0.013933 | 0.0034926 | -0.01393 | -0.0034909 | 2.9712e-06 | 1.6704e-06 | 0.020966 | 0.020966 | 0.020966 | 0.98889 | -0.21245 | 0.98866 | -0.21693 | 5.76
71 | -0.017344 | -0.0043482 | 0.017345 | 0.0043485 | 4.9576e-07 | 2.9237e-07 | 0.026094 | 0.026094 | 0.026094 | 0.98907 | -0.20899 | 0.9891 | -0.20839 | 7.1688
72 | 0.0096093 | 0.002408 | -0.009609 | -0.0024078 | 3.0847e-07 | 1.4699e-07 | 0.014463 | 0.014463 | 0.014463 | 0.98866 | -0.21693 | 0.98863 | -0.2176 | 3.9733
73 | -0.095334 | -0.024195 | 0.095592 | 0.024359 | 0.00025729 | 0.00016423 | 0.14321 | 0.14321 | 0.14321 | 0.9913 | -0.16599 | 0.99422 | -0.11004 | 39.344
74 | 0.095334 | 0.024195 | -0.095233 | -0.02413 | 0.00010159 | 6.4849e-05 | 0.14321 | 0.14321 | 0.14321 | 0.9913 | -0.16599 | 0.99014 | -0.18817 | 39.344
75 | -0.12791 | -0.032459 | 0.12794 | 0.032478 | 2.9284e-05 | 1.8714e-05 | 0.19159 | 0.19159 | 0.19159 | 0.99422 | -0.11004 | 0.99447 | -0.10529 | 52.6337
76 | 0.084526 | 0.021446 | -0.08427 | -0.021284 | 0.00025515 | 0.00016276 | 0.12712 | 0.12712 | 0.12712 | 0.99014 | -0.18817 | 0.98688 | -0.25114 | 34.9234
77 | 0.020654 | 0.0051822 | -0.020645 | -0.0051767 | 9.1081e-06 | 5.5134e-06 | 0.031242 | 0.031243 | 0.031243 | 0.98378 | -0.31104 | 0.9833 | -0.32029 | 8.5831
78 | 0.06185 | 0.01562 | -0.0618 | -0.015588 | 4.9837e-05 | 3.1703e-05 | 0.093594 | 0.093594 | 0.093594 | 0.98378 | -0.31104 | 0.98291 | -0.32787 | 25.7127
79 | -0.0075906 | -0.0019024 | 0.0075909 | 0.0019025 | 3.0389e-07 | 1.1703e-07 | 0.011503 | 0.011503 | 0.011503 | 0.98188 | -0.3484 | 0.98192 | -0.34756 | 3.1603
80 | -0.017035 | -0.0042693 | 0.017041 | 0.0042729 | 6.1832e-06 | 3.6441e-06 | 0.025814 | 0.025814 | 0.025814 | 0.98192 | -0.34756 | 0.98231 | -0.33995 | 7.0919
81 | -0.070949 | -0.017859 | 0.071041 | 0.017918 | 9.2395e-05 | 5.8861e-05 | 0.10734 | 0.10734 | 0.10734 | 0.98377 | -0.31141 | 0.98517 | -0.28421 | 29.4896
82 | 0.010621 | 0.0026619 | -0.01062 | -0.0026616 | 5.8561e-07 | 2.9797e-07 | 0.016065 | 0.016065 | 0.016065 | 0.98377 | -0.31141 | 0.98372 | -0.31257 | 4.4135
83 | -0.081737 | -0.020598 | 0.081866 | 0.020681 | 0.00012953 | 8.2609e-05 | 0.1235 | 0.1235 | 0.1235 | 0.98517 | -0.28421 | 0.98688 | -0.25114 | 33.9277
84 | 0.0075547 | 0.0018933 | -0.0075536 | -0.0018928 | 1.1779e-06 | 4.4853e-07 | 0.011428 | 0.011428 | 0.011428 | 0.98372 | -0.31257 | 0.98355 | -0.31585 | 3.1395
85 | 0.0038758 | 0.00097109 | -0.0038756 | -0.00097116 | 2.0916e-07 | -7.2002e-08 | 0.0058637 | 0.0058637 | 0.0058637 | 0.98355 | -0.31585 | 0.98349 | -0.31698 | 1.6109
86 | -0.016044 | -0.0040211 | 0.016047 | 0.0040233 | 3.8477e-06 | 2.2498e-06 | 0.024509 | 0.024509 | 0.024509 | 0.97406 | -0.50113 | 0.97431 | -0.49609 | 6.7332
87 | 0.010274 | 0.002575 | -0.010273 | -0.0025746 | 7.6816e-07 | 3.8812e-07 | 0.015695 | 0.015695 | 0.015695 | 0.97406 | -0.50113 | 0.97398 | -0.5027 | 4.3117
88 | -0.018118 | -0.0045424 | 0.018123 | 0.004545 | 4.4561e-06 | 2.6586e-06 | 0.027672 | 0.027672 | 0.027672 | 0.97431 | -0.49609 | 0.97458 | -0.49093 | 7.6021
89 | -0.023194 | -0.0058159 | 0.023194 | 0.0058164 | 7.0623e-07 | 4.3327e-07 | 0.035414 | 0.035414 | 0.035414 | 0.97458 | -0.49093 | 0.97461 | -0.49029 | 9.7291
90 | -0.026301 | -0.006595 | 0.026314 | 0.006603 | 1.2841e-05 | 7.9534e-06 | 0.040158 | 0.040158 | 0.040158 | 0.97461 | -0.49029 | 0.97513 | -0.48005 | 11.0323
91 | -0.026314 | -0.006603 | 0.026398 | 0.006655 | 8.4007e-05 | 5.2026e-05 | 0.040158 | 0.040157 | 0.040158 | 0.97513 | -0.48005 | 0.97853 | -0.41333 | 11.0323
92 | -0.026398 | -0.006655 | 0.026425 | 0.0066715 | 2.6649e-05 | 1.6501e-05 | 0.040157 | 0.040157 | 0.040157 | 0.97853 | -0.41333 | 0.97961 | -0.39226 | 11.0321
93 | -0.033963 | -0.0085607 | 0.033975 | 0.0085684 | 1.228e-05 | 7.7046e-06 | 0.051607 | 0.051607 | 0.051607 | 0.97961 | -0.39226 | 0.97999 | -0.3847 | 14.1777
94 | -0.038992 | -0.0098258 | 0.03903 | 0.0098494 | 3.7376e-05 | 2.3562e-05 | 0.059225 | 0.059225 | 0.059225 | 0.97999 | -0.3847 | 0.98102 | -0.36469 | 16.2705
95 | -0.0020039 | -0.00050223 | 0.002004 | 0.00050208 | 4.8651e-08 | -1.4795e-07 | 0.003032 | 0.0030319 | 0.003032 | 0.98346 | -0.31749 | 0.98349 | -0.31698 | 0.83296
96 | 0.019874 | 0.0049853 | -0.019865 | -0.0049801 | 8.6447e-06 | 5.2012e-06 | 0.029886 | 0.029886 | 0.029886 | 0.98957 | -0.19926 | 0.9891 | -0.20839 | 8.2104
97 | 0.082742 | 0.021043 | -0.08262 | -0.020965 | 0.00012178 | 7.767e-05 | 0.12472 | 0.12472 | 0.12472 | 0.98804 | -0.22854 | 0.98645 | -0.25913 | 34.264
98 | 0.07895 | 0.020045 | -0.078878 | -0.019999 | 7.2602e-05 | 4.6291e-05 | 0.11919 | 0.11919 | 0.11919 | 0.98645 | -0.25913 | 0.98546 | -0.27826 | 32.7432
99 | 0.074407 | 0.018879 | -0.074363 | -0.01885 | 4.4278e-05 | 2.8219e-05 | 0.11244 | 0.11244 | 0.11244 | 0.98546 | -0.27826 | 0.98482 | -0.29064 | 30.8888
100 | 0.071658 | 0.018172 | -0.07162 | -0.018148 | 3.7504e-05 | 2.3894e-05 | 0.10835 | 0.10835 | 0.10835 | 0.98482 | -0.29064 | 0.98426 | -0.30154 | 29.7658
101 | 0.069484 | 0.017613 | -0.069424 | -0.017575 | 5.9971e-05 | 3.8198e-05 | 0.10512 | 0.10512 | 0.10512 | 0.98426 | -0.30154 | 0.98333 | -0.31951 | 28.8785
102 | 0.066623 | 0.016873 | -0.066561 | -0.016834 | 6.1528e-05 | 3.9174e-05 | 0.10088 | 0.10088 | 0.10088 | 0.98333 | -0.31951 | 0.98234 | -0.33877 | 27.7142
103 | 0.0088253 | 0.0022119 | -0.0088234 | -0.002211 | 1.9775e-06 | 9.0135e-07 | 0.013452 | 0.013452 | 0.013452 | 0.97623 | -0.45815 | 0.97599 | -0.46285 | 3.6956
104 | 0.0024503 | 0.00061373 | -0.0024501 | -0.00061405 | 1.8296e-07 | -3.1977e-07 | 0.0037356 | 0.0037357 | 0.0037357 | 0.97599 | -0.46285 | 0.97591 | -0.46442 | 1.0263
105 | 0.00080519 | 0.00020179 | -0.00080519 | -0.0002018 | 3.1474e-10 | -6.7258e-09 | 0.0012291 | 0.0012291 | 0.0012291 | 0.9748 | -0.4862 | 0.9748 | -0.48621 | 0.33767
106 | 0.002769 | 0.000693 | -0.0027689 | -0.00069316 | 1.3475e-07 | -1.6222e-07 | 0.0042362 | 0.0042363 | 0.0042363 | 0.97257 | -0.5303 | 0.97252 | -0.53133 | 1.1638
107 | -0.0027683 | -0.00069381 | 0.0027689 | 0.00069316 | 5.3838e-07 | -6.4779e-07 | 0.0042366 | 0.0042363 | 0.0042366 | 0.97231 | -0.53541 | 0.97252 | -0.53133 | 1.1639
108 | -0.043577 | -0.010989 | 0.043624 | 0.011019 | 4.6717e-05 | 2.9539e-05 | 0.066122 | 0.066122 | 0.066122 | 0.98102 | -0.36469 | 0.98217 | -0.34231 | 18.1655
109 | -0.053551 | -0.013507 | 0.053588 | 0.01353 | 3.7065e-05 | 2.3532e-05 | 0.081162 | 0.081162 | 0.081162 | 0.98217 | -0.34231 | 0.98291 | -0.32787 | 22.2972
110 | 0.020645 | 0.0051767 | -0.020638 | -0.0051727 | 6.5884e-06 | 3.9884e-06 | 0.031243 | 0.031243 | 0.031243 | 0.9833 | -0.32029 | 0.98296 | -0.32699 | 8.5831
111 | 0.0096833 | 0.0024271 | -0.0096821 | -0.0024266 | 1.1801e-06 | 5.6965e-07 | 0.014659 | 0.014659 | 0.014659 | 0.98296 | -0.32699 | 0.98283 | -0.32955 | 4.0272
112 | 0.0030536 | 0.00076487 | -0.0030532 | -0.00076521 | 3.435e-07 | -3.3615e-07 | 0.0045959 | 0.0045961 | 0.0045961 | 0.98863 | -0.2176 | 0.98851 | -0.21996 | 1.2627

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.49989 | 0.12737

## res_load
| p_mw | q_mvar
0 | 0.0041392 | 0.0010374
1 | 0.0018882 | 0.00047323
2 | 0.0042062 | 0.0010542
3 | 0.00081394 | 0.00020399
4 | 0.0042952 | 0.0010765
5 | 0.0042422 | 0.0010632
6 | 0.0039119 | 0.00098043
7 | 0.0046905 | 0.0011755
8 | 0.008569 | 0.0021476
9 | 0.0030802 | 0.00077197
10 | 0.0034471 | 0.00086393
11 | 0.0037798 | 0.00094731
12 | 0.0028453 | 0.00071309
13 | 0.020898 | 0.0052376
14 | 0.014523 | 0.0036398
15 | 0.01397 | 0.0035012
16 | 0.014142 | 0.0035442
17 | 0.0074401 | 0.0018647
18 | 0.0022775 | 0.00057081
19 | 0.0044498 | 0.0011152
20 | 0.00392 | 0.00098244
21 | 0.011957 | 0.0029967
22 | 0.017022 | 0.004266
23 | 0.013024 | 0.0032641
24 | 0.013059 | 0.0032729
25 | 0.0049871 | 0.0012499
26 | 0.0085846 | 0.0021515
27 | 0.0086663 | 0.002172
28 | 0.0081568 | 0.0020443
29 | 0.0036197 | 0.00090719
30 | 0.0036886 | 0.00092444
31 | 0.011267 | 0.0028238
32 | 0.0048793 | 0.0012229
33 | 0.0034088 | 0.00085432
34 | 0.0043211 | 0.001083
35 | 0.032322 | 0.0081006
36 | 0.010707 | 0.0026835
37 | 0.0075906 | 0.0019024
38 | 0.0094436 | 0.0023668
39 | 0.0034319 | 0.00086012
40 | 0.010696 | 0.0026806
41 | 0.0030657 | 0.00076834
42 | 0.002404 | 0.00060249
43 | 0.0036777 | 0.00092172
44 | 0.0057698 | 0.0014461
45 | 0.002071 | 0.00051903
46 | 0.010273 | 0.0025746
47 | 0.0050709 | 0.0012709
48 | 0.0031069 | 0.00077866
49 | 0.007538 | 0.0018892
50 | 0.0050171 | 0.0012574
51 | 0.0020039 | 0.00050223
52 | 0.0018717 | 0.00046909
53 | 0.0060543 | 0.0015173
54 | 0.0085919 | 0.0021533
55 | 0.0052985 | 0.0013279
56 | 0.0036698 | 0.00091974
57 | 0.0044704 | 0.0011204
58 | 0.0027054 | 0.00067803
59 | 0.0025201 | 0.00063159
60 | 0.0021365 | 0.00053546
61 | 0.0028007 | 0.00070193
62 | 0.002044 | 0.00051227
63 | 0.0032069 | 0.00080372
64 | 0.0063731 | 0.0015972
65 | 0.0024501 | 0.00061405
66 | 0.0027239 | 0.00068267
67 | 0.00080519 | 0.0002018
68 | 0.0039246 | 0.00098359
69 | 0.0020117 | 0.00050418
70 | 0.0027683 | 0.00069381
71 | 0.0045475 | 0.0011397
72 | 0.0099268 | 0.0024879
73 | 0.0082124 | 0.0020582
74 | 0.010955 | 0.0027456
75 | 0.0096821 | 0.0024266
76 | 0.0065554 | 0.0016429
77 | 0.0030532 | 0.00076521

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1