## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2125-38_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2125-38_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2125-38_0_5_node_138 | 0.4 | n |  | TRUE
3 | bus_LV_2125-38_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2125-38_0_5_node_136 | 0.4 | n |  | TRUE
5 | bus_LV_2125-38_0_5_node_58 | 0.4 | n |  | TRUE
6 | bus_LV_2125-38_0_5_node_56 | 0.4 | n |  | TRUE
7 | bus_LV_2125-38_0_5_node_59 | 0.4 | n |  | TRUE
8 | bus_LV_2125-38_0_5_node_57 | 0.4 | n |  | TRUE
9 | bus_LV_2125-38_0_5_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_2125-38_0_5_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_2125-38_0_5_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2125-38_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2125-38_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2125-38_0_5_node_34 | 0.4 | n |  | TRUE
15 | bus_LV_2125-38_0_5_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_2125-38_0_5_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_2125-38_0_5_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2125-38_0_5_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2125-38_0_5_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2125-38_0_5_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_2125-38_0_5_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_2125-38_0_5_node_35 | 0.4 | n |  | TRUE
23 | bus_LV_2125-38_0_5_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_2125-38_0_5_node_37 | 0.4 | n |  | TRUE
25 | bus_LV_2125-38_0_5_node_26 | 0.4 | n |  | TRUE
26 | bus_LV_2125-38_0_5_node_36 | 0.4 | n |  | TRUE
27 | bus_LV_2125-38_0_5_node_17 | 0.4 | n |  | TRUE
28 | bus_LV_2125-38_0_5_node_18 | 0.4 | n |  | TRUE
29 | bus_LV_2125-38_0_5_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2125-38_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_2125-38_0_5_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2125-38_0_5_node_44 | 0.4 | n |  | TRUE
33 | bus_LV_2125-38_0_5_node_55 | 0.4 | n |  | TRUE
34 | bus_LV_2125-38_0_5_node_50 | 0.4 | n |  | TRUE
35 | bus_LV_2125-38_0_5_node_48 | 0.4 | n |  | TRUE
36 | bus_LV_2125-38_0_5_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_2125-38_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_2125-38_0_5_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_2125-38_0_5_node_25 | 0.4 | n |  | TRUE
40 | bus_LV_2125-38_0_5_node_53 | 0.4 | n |  | TRUE
41 | bus_LV_2125-38_0_5_node_30 | 0.4 | n |  | TRUE
42 | bus_LV_2125-38_0_5_node_89 | 0.4 | n |  | TRUE
43 | bus_LV_2125-38_0_5_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_2125-38_0_5_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_2125-38_0_5_node_27 | 0.4 | n |  | TRUE
46 | bus_LV_2125-38_0_5_node_88 | 0.4 | n |  | TRUE
47 | bus_LV_2125-38_0_5_node_117 | 0.4 | n |  | TRUE
48 | bus_LV_2125-38_0_5_node_87 | 0.4 | n |  | TRUE
49 | bus_LV_2125-38_0_5_node_70 | 0.4 | n |  | TRUE
50 | bus_LV_2125-38_0_5_node_68 | 0.4 | n |  | TRUE
51 | bus_LV_2125-38_0_5_node_31 | 0.4 | n |  | TRUE
52 | bus_LV_2125-38_0_5_node_32 | 0.4 | n |  | TRUE
53 | bus_LV_2125-38_0_5_node_90 | 0.4 | n |  | TRUE
54 | bus_LV_2125-38_0_5_node_33 | 0.4 | n |  | TRUE
55 | bus_LV_2125-38_0_5_node_100 | 0.4 | n |  | TRUE
56 | bus_LV_2125-38_0_5_node_49 | 0.4 | n |  | TRUE
57 | bus_LV_2125-38_0_5_node_91 | 0.4 | n |  | TRUE
58 | bus_LV_2125-38_0_5_node_92 | 0.4 | n |  | TRUE
59 | bus_LV_2125-38_0_5_node_47 | 0.4 | n |  | TRUE
60 | bus_LV_2125-38_0_5_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_2125-38_0_5_node_39 | 0.4 | n |  | TRUE
62 | bus_LV_2125-38_0_5_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_2125-38_0_5_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_2125-38_0_5_node_40 | 0.4 | n |  | TRUE
65 | bus_LV_2125-38_0_5_node_41 | 0.4 | n |  | TRUE
66 | bus_LV_2125-38_0_5_node_42 | 0.4 | n |  | TRUE
67 | bus_LV_2125-38_0_5_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_2125-38_0_5_node_101 | 0.4 | n |  | TRUE
69 | bus_LV_2125-38_0_5_node_45 | 0.4 | n |  | TRUE
70 | bus_LV_2125-38_0_5_node_46 | 0.4 | n |  | TRUE
71 | bus_LV_2125-38_0_5_node_134 | 0.4 | n |  | TRUE
72 | bus_LV_2125-38_0_5_node_102 | 0.4 | n |  | TRUE
73 | bus_LV_2125-38_0_5_node_60 | 0.4 | n |  | TRUE
74 | bus_LV_2125-38_0_5_node_126 | 0.4 | n |  | TRUE
75 | bus_LV_2125-38_0_5_node_77 | 0.4 | n |  | TRUE
76 | bus_LV_2125-38_0_5_node_135 | 0.4 | n |  | TRUE
77 | bus_LV_2125-38_0_5_node_61 | 0.4 | n |  | TRUE
78 | bus_LV_2125-38_0_5_node_62 | 0.4 | n |  | TRUE
79 | bus_LV_2125-38_0_5_node_63 | 0.4 | n |  | TRUE
80 | bus_LV_2125-38_0_5_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2125-38_0_5_node_65 | 0.4 | n |  | TRUE
82 | bus_LV_2125-38_0_5_node_71 | 0.4 | n |  | TRUE
83 | bus_LV_2125-38_0_5_node_116 | 0.4 | n |  | TRUE
84 | bus_LV_2125-38_0_5_node_114 | 0.4 | n |  | TRUE
85 | bus_LV_2125-38_0_5_node_66 | 0.4 | n |  | TRUE
86 | bus_LV_2125-38_0_5_node_67 | 0.4 | n |  | TRUE
87 | bus_LV_2125-38_0_5_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_2125-38_0_5_node_120 | 0.4 | n |  | TRUE
89 | bus_LV_2125-38_0_5_node_81 | 0.4 | n |  | TRUE
90 | bus_LV_2125-38_0_5_node_72 | 0.4 | n |  | TRUE
91 | bus_LV_2125-38_0_5_node_73 | 0.4 | n |  | TRUE
92 | bus_LV_2125-38_0_5_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_2125-38_0_5_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2125-38_0_5_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_2125-38_0_5_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_2125-38_0_5_node_115 | 0.4 | n |  | TRUE
97 | bus_LV_2125-38_0_5_node_82 | 0.4 | n |  | TRUE
98 | bus_LV_2125-38_0_5_node_113 | 0.4 | n |  | TRUE
99 | bus_LV_2125-38_0_5_node_78 | 0.4 | n |  | TRUE
100 | bus_LV_2125-38_0_5_node_79 | 0.4 | n |  | TRUE
101 | bus_LV_2125-38_0_5_node_80 | 0.4 | n |  | TRUE
102 | bus_LV_2125-38_0_5_node_83 | 0.4 | n |  | TRUE
103 | bus_LV_2125-38_0_5_node_85 | 0.4 | n |  | TRUE
104 | bus_LV_2125-38_0_5_node_86 | 0.4 | n |  | TRUE
105 | bus_LV_2125-38_0_5_node_133 | 0.4 | n |  | TRUE
106 | bus_LV_2125-38_0_5_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_2125-38_0_5_node_106 | 0.4 | n |  | TRUE
108 | bus_LV_2125-38_0_5_node_119 | 0.4 | n |  | TRUE
109 | bus_LV_2125-38_0_5_node_139 | 0.4 | n |  | TRUE
110 | bus_LV_2125-38_0_5_node_122 | 0.4 | n |  | TRUE
111 | bus_LV_2125-38_0_5_node_104 | 0.4 | n |  | TRUE
112 | bus_LV_2125-38_0_5_node_118 | 0.4 | n |  | TRUE
113 | bus_LV_2125-38_0_5_node_93 | 0.4 | n |  | TRUE
114 | bus_LV_2125-38_0_5_node_94 | 0.4 | n |  | TRUE
115 | bus_LV_2125-38_0_5_node_95 | 0.4 | n |  | TRUE
116 | bus_LV_2125-38_0_5_node_96 | 0.4 | n |  | TRUE
117 | bus_LV_2125-38_0_5_node_97 | 0.4 | n |  | TRUE
118 | bus_LV_2125-38_0_5_node_109 | 0.4 | n |  | TRUE
119 | bus_LV_2125-38_0_5_node_98 | 0.4 | n |  | TRUE
120 | bus_LV_2125-38_0_5_node_121 | 0.4 | n |  | TRUE
121 | bus_LV_2125-38_0_5_node_123 | 0.4 | n |  | TRUE
122 | bus_LV_2125-38_0_5_node_125 | 0.4 | n |  | TRUE
123 | bus_LV_2125-38_0_5_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_2125-38_0_5_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_2125-38_0_5_node_107 | 0.4 | n |  | TRUE
126 | bus_LV_2125-38_0_5_node_108 | 0.4 | n |  | TRUE
127 | bus_LV_2125-38_0_5_node_110 | 0.4 | n |  | TRUE
128 | bus_LV_2125-38_0_5_node_111 | 0.4 | n |  | TRUE
129 | bus_LV_2125-38_0_5_node_112 | 0.4 | n |  | TRUE
130 | bus_LV_2125-38_0_5_node_127 | 0.4 | n |  | TRUE
131 | bus_LV_2125-38_0_5_node_128 | 0.4 | n |  | TRUE
132 | bus_LV_2125-38_0_5_node_129 | 0.4 | n |  | TRUE
133 | bus_LV_2125-38_0_5_node_130 | 0.4 | n |  | TRUE
134 | bus_LV_2125-38_0_5_node_131 | 0.4 | n |  | TRUE
135 | bus_LV_2125-38_0_5_node_132 | 0.4 | n |  | TRUE
136 | bus_MV_31_0_node_82 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2125-38_0_5_load_0 | 0 | 0.015538 | 0.0038943 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2125-38_0_5_load_136 | 4 | 0.01699 | 0.0042582 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2125-38_0_5_load_58 | 5 | 0.0064799 | 0.001624 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2125-38_0_5_load_56 | 6 | 0.0028065 | 0.00070338 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2125-38_0_5_load_59 | 7 | 0.016266 | 0.0040766 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2125-38_0_5_load_4 | 9 | 0.0039415 | 0.00098784 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2125-38_0_5_load_5 | 10 | 0.0031358 | 0.0007859 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2125-38_0_5_load_6 | 11 | 0.0032207 | 0.00080718 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2125-38_0_5_load_7 | 12 | 0.0047977 | 0.0012024 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2125-38_0_5_load_8 | 13 | 0.0036443 | 0.00091334 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2125-38_0_5_load_34 | 14 | 0.0039709 | 0.00099519 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2125-38_0_5_load_16 | 15 | 0.0031382 | 0.0007865 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2125-38_0_5_load_15 | 16 | 0.0042674 | 0.0010695 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2125-38_0_5_load_9 | 17 | 0.0013056 | 0.00032722 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2125-38_0_5_load_10 | 18 | 0.0033793 | 0.00084693 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2125-38_0_5_load_12 | 20 | 0.0042016 | 0.001053 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2125-38_0_5_load_13 | 21 | 0.0027226 | 0.00068234 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2125-38_0_5_load_35 | 22 | 0.0035384 | 0.00088681 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2125-38_0_5_load_14 | 23 | 0.0033168 | 0.00083126 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2125-38_0_5_load_37 | 24 | 0.0023895 | 0.00059885 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2125-38_0_5_load_36 | 26 | 0.0031999 | 0.00080198 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2125-38_0_5_load_17 | 27 | 0.005838 | 0.0014632 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2125-38_0_5_load_18 | 28 | 0.002138 | 0.00053584 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2125-38_0_5_load_19 | 29 | 0.0036883 | 0.00092438 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2125-38_0_5_load_20 | 30 | 0.0059268 | 0.0014854 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2125-38_0_5_load_44 | 32 | 0.0034295 | 0.00085951 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2125-38_0_5_load_55 | 33 | 0.0019188 | 0.0004809 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2125-38_0_5_load_50 | 34 | 0.0020163 | 0.00050534 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2125-38_0_5_load_48 | 35 | 0.0013118 | 0.00032877 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2125-38_0_5_load_22 | 36 | 0.0050662 | 0.0012697 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2125-38_0_5_load_23 | 37 | 0.0038293 | 0.0009597 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2125-38_0_5_load_24 | 38 | 0.0048316 | 0.0012109 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2125-38_0_5_load_25 | 39 | 0.003795 | 0.00095112 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2125-38_0_5_load_30 | 41 | 0.0046747 | 0.0011716 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2125-38_0_5_load_89 | 42 | 0.0011198 | 0.00028064 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2125-38_0_5_load_29 | 44 | 0.0019648 | 0.00049243 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2125-38_0_5_load_27 | 45 | 0.0051989 | 0.001303 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2125-38_0_5_load_88 | 46 | 0.0039978 | 0.0010019 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2125-38_0_5_load_117 | 47 | 0.00094458 | 0.00023674 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2125-38_0_5_load_87 | 48 | 0.0036609 | 0.00091752 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2125-38_0_5_load_70 | 49 | 0.00093951 | 0.00023546 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2125-38_0_5_load_32 | 52 | 0.0012863 | 0.00032239 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2125-38_0_5_load_49 | 56 | 0.0060294 | 0.0015111 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2125-38_0_5_load_47 | 59 | 0.0029468 | 0.00073855 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2125-38_0_5_load_38 | 60 | 0.0034248 | 0.00085835 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2125-38_0_5_load_39 | 61 | 0.0047837 | 0.0011989 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2125-38_0_5_load_52 | 62 | 0.0047367 | 0.0011871 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2125-38_0_5_load_51 | 63 | 0.0059265 | 0.0014853 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2125-38_0_5_load_40 | 64 | 0.0018167 | 0.00045532 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2125-38_0_5_load_41 | 65 | 0.0012379 | 0.00031023 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2125-38_0_5_load_42 | 66 | 0.0025592 | 0.00064139 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2125-38_0_5_load_54 | 67 | 0.001571 | 0.00039374 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2125-38_0_5_load_101 | 68 | 0.0018866 | 0.00047282 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2125-38_0_5_load_45 | 69 | 0.0020378 | 0.00051071 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2125-38_0_5_load_46 | 70 | 0.0024049 | 0.00060272 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2125-38_0_5_load_134 | 71 | 0.0021031 | 0.00052709 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2125-38_0_5_load_102 | 72 | 0.0032517 | 0.00081495 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2125-38_0_5_load_60 | 73 | 0.0059268 | 0.0014854 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2125-38_0_5_load_126 | 74 | 0.0068687 | 0.0017215 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2125-38_0_5_load_77 | 75 | 0.021546 | 0.0054 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2125-38_0_5_load_135 | 76 | 0.023115 | 0.0057932 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2125-38_0_5_load_61 | 77 | 0.0061371 | 0.0015381 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2125-38_0_5_load_62 | 78 | 0.0065677 | 0.001646 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2125-38_0_5_load_63 | 79 | 0.0053032 | 0.0013291 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2125-38_0_5_load_65 | 81 | 0.0059241 | 0.0014847 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2125-38_0_5_load_71 | 82 | 0.020123 | 0.0050432 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2125-38_0_5_load_116 | 83 | 0.0074546 | 0.0018683 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2125-38_0_5_load_114 | 84 | 0.0038286 | 0.00095955 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2125-38_0_5_load_66 | 85 | 0.0011366 | 0.00028485 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2125-38_0_5_load_67 | 86 | 0.0012812 | 0.0003211 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2125-38_0_5_load_69 | 87 | 0.0011594 | 0.00029058 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2125-38_0_5_load_81 | 89 | 0.0010243 | 0.00025672 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2125-38_0_5_load_72 | 90 | 0.003837 | 0.00096163 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2125-38_0_5_load_73 | 91 | 0.0039408 | 0.00098766 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2125-38_0_5_load_74 | 92 | 0.0037068 | 0.00092902 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2125-38_0_5_load_75 | 93 | 0.0030983 | 0.0007765 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2125-38_0_5_load_76 | 94 | 0.002798 | 0.00070124 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2125-38_0_5_load_84 | 95 | 0.0029357 | 0.00073577 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2125-38_0_5_load_115 | 96 | 0.0039843 | 0.00099856 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2125-38_0_5_load_82 | 97 | 0.0047594 | 0.0011928 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2125-38_0_5_load_113 | 98 | 0.002527 | 0.00063333 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2125-38_0_5_load_78 | 99 | 0.0035565 | 0.00089135 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2125-38_0_5_load_79 | 100 | 0.00097234 | 0.00024369 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2125-38_0_5_load_80 | 101 | 0.0026143 | 0.00065521 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2125-38_0_5_load_83 | 102 | 0.0035259 | 0.00088367 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2125-38_0_5_load_85 | 103 | 0.0044148 | 0.0011064 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2125-38_0_5_load_86 | 104 | 0.0045804 | 0.001148 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2125-38_0_5_load_133 | 105 | 0.00058334 | 0.0001462 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2125-38_0_5_load_99 | 106 | 0.0031644 | 0.00079306 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2125-38_0_5_load_119 | 108 | 0.0019861 | 0.00049778 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2125-38_0_5_load_139 | 109 | 0.002997 | 0.00075111 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2125-38_0_5_load_122 | 110 | 0.0028783 | 0.00072136 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2125-38_0_5_load_104 | 111 | 0.0026039 | 0.00065259 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2125-38_0_5_load_118 | 112 | 0.0022819 | 0.0005719 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2125-38_0_5_load_93 | 113 | 0.0011735 | 0.00029412 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2125-38_0_5_load_95 | 115 | 0.0030548 | 0.00076561 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2125-38_0_5_load_96 | 116 | 0.0029808 | 0.00074705 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2125-38_0_5_load_97 | 117 | 0.002888 | 0.00072379 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2125-38_0_5_load_109 | 118 | 0.0041814 | 0.001048 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2125-38_0_5_load_98 | 119 | 0.0042545 | 0.0010663 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2125-38_0_5_load_121 | 120 | 0.001784 | 0.0004471 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2125-38_0_5_load_123 | 121 | 0.0014148 | 0.00035457 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2125-38_0_5_load_125 | 122 | 0.0038249 | 0.00095862 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2125-38_0_5_load_103 | 123 | 0.0025197 | 0.00063151 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2125-38_0_5_load_107 | 125 | 0.0025347 | 0.00063526 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2125-38_0_5_load_108 | 126 | 0.0021163 | 0.0005304 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2125-38_0_5_load_110 | 127 | 0.0021058 | 0.00052777 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2125-38_0_5_load_111 | 128 | 0.0018879 | 0.00047316 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2125-38_0_5_load_112 | 129 | 0.0020726 | 0.00051945 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2125-38_0_5_load_127 | 130 | 0.002092 | 0.0005243 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_2125-38_0_5_load_128 | 131 | 0.0004864 | 0.0001219 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_2125-38_0_5_load_129 | 132 | 0.00067413 | 0.00016895 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_2125-38_0_5_load_130 | 133 | 0.00049681 | 0.00012451 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_2125-38_0_5_load_131 | 134 | 0.0020469 | 0.00051301 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_2125-38_0_5_load_132 | 135 | 0.00064953 | 0.00016279 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 62 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2125-38_0_5_line_0 |  | 0 | 1 | 0.031294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2125-38_0_5_line_1 |  | 0 | 2 | 0.068861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2125-38_0_5_line_2 |  | 1 | 3 | 0.030548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2125-38_0_5_line_3 |  | 2 | 4 | 0.031344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2125-38_0_5_line_4 |  | 3 | 5 | 0.024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2125-38_0_5_line_5 |  | 3 | 6 | 0.050324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2125-38_0_5_line_6 |  | 4 | 76 | 0.014605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2125-38_0_5_line_7 |  | 5 | 7 | 0.0044265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_2125-38_0_5_line_8 |  | 6 | 8 | 0.043417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2125-38_0_5_line_9 |  | 7 | 73 | 0.024038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2125-38_0_5_line_10 |  | 8 | 31 | 0.01297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2125-38_0_5_line_11 |  | 9 | 10 | 0.0077887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2125-38_0_5_line_12 |  | 9 | 11 | 0.028287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2125-38_0_5_line_13 |  | 10 | 12 | 0.016074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2125-38_0_5_line_14 |  | 11 | 13 | 0.00051772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2125-38_0_5_line_15 |  | 12 | 14 | 0.017215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2125-38_0_5_line_16 |  | 13 | 15 | 0.030242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2125-38_0_5_line_17 |  | 15 | 16 | 0.0070517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2125-38_0_5_line_18 |  | 16 | 20 | 0.024684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2125-38_0_5_line_19 |  | 17 | 18 | 0.02299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2125-38_0_5_line_20 |  | 17 | 19 | 0.012924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2125-38_0_5_line_21 |  | 18 | 20 | 0.041895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2125-38_0_5_line_22 |  | 19 | 21 | 0.01464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2125-38_0_5_line_23 |  | 21 | 22 | 0.036183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2125-38_0_5_line_24 |  | 22 | 25 | 0.011986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2125-38_0_5_line_25 |  | 23 | 24 | 0.026058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2125-38_0_5_line_26 |  | 24 | 26 | 0.0069131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2125-38_0_5_line_27 |  | 25 | 41 | 0.021721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2125-38_0_5_line_28 |  | 25 | 38 | 0.011702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2125-38_0_5_line_29 |  | 26 | 60 | 0.018844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2125-38_0_5_line_30 |  | 27 | 28 | 0.020729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2125-38_0_5_line_31 |  | 27 | 29 | 0.0070948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_2125-38_0_5_line_32 |  | 28 | 30 | 0.010454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2125-38_0_5_line_33 |  | 29 | 31 | 0.022192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2125-38_0_5_line_34 |  | 30 | 32 | 0.0034584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2125-38_0_5_line_35 |  | 31 | 33 | 0.019998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2125-38_0_5_line_36 |  | 32 | 34 | 0.015176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
37 | LV_2125-38_0_5_line_37 |  | 33 | 35 | 0.019886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
38 | LV_2125-38_0_5_line_38 |  | 34 | 63 | 0.015654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_2125-38_0_5_line_39 |  | 35 | 70 | 0.0037655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_2125-38_0_5_line_40 |  | 36 | 37 | 0.0042182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2125-38_0_5_line_41 |  | 36 | 38 | 0.030047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2125-38_0_5_line_42 |  | 37 | 39 | 0.029226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2125-38_0_5_line_43 |  | 39 | 40 | 0.014782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2125-38_0_5_line_44 |  | 40 | 42 | 0.017581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2125-38_0_5_line_45 |  | 40 | 43 | 0.037245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2125-38_0_5_line_46 |  | 41 | 44 | 0.01912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2125-38_0_5_line_47 |  | 42 | 71 | 0.013773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2125-38_0_5_line_48 |  | 43 | 67 | 0.020369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2125-38_0_5_line_49 |  | 43 | 65 | 0.026416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2125-38_0_5_line_50 |  | 44 | 51 | 0.023858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2125-38_0_5_line_51 |  | 45 | 46 | 0.097875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2125-38_0_5_line_52 |  | 46 | 47 | 0.022416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2125-38_0_5_line_53 |  | 46 | 48 | 0.018231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2125-38_0_5_line_54 |  | 47 | 88 | 0.0091893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2125-38_0_5_line_55 |  | 48 | 104 | 0.0059316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2125-38_0_5_line_56 |  | 49 | 50 | 0.024407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2125-38_0_5_line_57 |  | 50 | 85 | 0.016551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2125-38_0_5_line_58 |  | 51 | 52 | 0.0079918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2125-38_0_5_line_59 |  | 52 | 53 | 0.0079759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
60 | LV_2125-38_0_5_line_60 |  | 53 | 57 | 0.009918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2125-38_0_5_line_61 |  | 53 | 58 | 0.038731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2125-38_0_5_line_62 |  | 54 | 55 | 0.013225 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2125-38_0_5_line_63 |  | 54 | 56 | 0.019271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2125-38_0_5_line_64 |  | 55 | 57 | 0.004985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_2125-38_0_5_line_65 |  | 56 | 59 | 0.03607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2125-38_0_5_line_66 |  | 57 | 106 | 0.055736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2125-38_0_5_line_67 |  | 58 | 107 | 0.013802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2125-38_0_5_line_68 |  | 58 | 108 | 0.017084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2125-38_0_5_line_69 |  | 59 | 69 | 0.012007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_2125-38_0_5_line_70 |  | 60 | 61 | 0.01523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2125-38_0_5_line_71 |  | 61 | 62 | 0.025789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2125-38_0_5_line_72 |  | 62 | 63 | 0.0079101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_2125-38_0_5_line_73 |  | 64 | 65 | 0.039623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2125-38_0_5_line_74 |  | 64 | 66 | 0.045784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2125-38_0_5_line_75 |  | 67 | 68 | 0.053668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2125-38_0_5_line_76 |  | 68 | 72 | 0.023908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2125-38_0_5_line_77 |  | 69 | 70 | 0.021806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_2125-38_0_5_line_78 |  | 71 | 105 | 0.0020597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2125-38_0_5_line_79 |  | 72 | 122 | 0.035313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2125-38_0_5_line_80 |  | 73 | 74 | 0.020967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2125-38_0_5_line_81 |  | 74 | 75 | 0.0084211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_2125-38_0_5_line_82 |  | 75 | 80 | 0.033464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_2125-38_0_5_line_83 |  | 77 | 78 | 0.0049787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2125-38_0_5_line_84 |  | 77 | 79 | 0.018168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2125-38_0_5_line_85 |  | 78 | 80 | 0.017171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_2125-38_0_5_line_86 |  | 79 | 81 | 0.011658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2125-38_0_5_line_87 |  | 80 | 82 | 0.017799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2125-38_0_5_line_88 |  | 81 | 83 | 0.0012869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_2125-38_0_5_line_89 |  | 83 | 84 | 0.010616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2125-38_0_5_line_90 |  | 84 | 98 | 0.017682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_2125-38_0_5_line_91 |  | 85 | 86 | 0.013539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2125-38_0_5_line_92 |  | 86 | 87 | 0.033657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2125-38_0_5_line_93 |  | 87 | 88 | 0.013826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2125-38_0_5_line_94 |  | 88 | 89 | 0.0088318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2125-38_0_5_line_95 |  | 89 | 100 | 0.01222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2125-38_0_5_line_96 |  | 90 | 91 | 0.0065093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
97 | LV_2125-38_0_5_line_97 |  | 90 | 92 | 0.025523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
98 | LV_2125-38_0_5_line_98 |  | 91 | 93 | 0.016334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_2125-38_0_5_line_99 |  | 92 | 94 | 0.0085064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_2125-38_0_5_line_100 |  | 93 | 95 | 0.027498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2125-38_0_5_line_101 |  | 94 | 96 | 0.020624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2125-38_0_5_line_102 |  | 95 | 97 | 0.017803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2125-38_0_5_line_103 |  | 96 | 98 | 0.006418 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
104 | LV_2125-38_0_5_line_104 |  | 97 | 102 | 0.0087226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2125-38_0_5_line_105 |  | 99 | 100 | 0.010623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2125-38_0_5_line_106 |  | 99 | 101 | 0.0043272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2125-38_0_5_line_107 |  | 102 | 103 | 0.025663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2125-38_0_5_line_108 |  | 103 | 104 | 0.013695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2125-38_0_5_line_109 |  | 105 | 135 | 0.012931 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2125-38_0_5_line_110 |  | 106 | 109 | 0.05878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2125-38_0_5_line_111 |  | 107 | 110 | 0.017218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2125-38_0_5_line_112 |  | 107 | 111 | 0.029658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2125-38_0_5_line_113 |  | 108 | 112 | 0.0093504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2125-38_0_5_line_114 |  | 109 | 121 | 0.077979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2125-38_0_5_line_115 |  | 110 | 120 | 0.00049714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2125-38_0_5_line_116 |  | 111 | 123 | 0.011255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2125-38_0_5_line_117 |  | 112 | 129 | 0.016157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2125-38_0_5_line_118 |  | 113 | 114 | 0.010918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2125-38_0_5_line_119 |  | 114 | 115 | 0.014876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2125-38_0_5_line_120 |  | 114 | 116 | 0.019058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2125-38_0_5_line_121 |  | 115 | 117 | 0.047324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2125-38_0_5_line_122 |  | 116 | 118 | 0.023419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2125-38_0_5_line_123 |  | 117 | 119 | 0.001304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2125-38_0_5_line_124 |  | 119 | 120 | 0.030054 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2125-38_0_5_line_125 |  | 123 | 124 | 0.025787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_2125-38_0_5_line_126 |  | 124 | 125 | 0.003878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_2125-38_0_5_line_127 |  | 124 | 126 | 0.018376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_2125-38_0_5_line_128 |  | 127 | 128 | 0.00032514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_2125-38_0_5_line_129 |  | 128 | 129 | 0.020537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_2125-38_0_5_line_130 |  | 130 | 131 | 0.010357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_2125-38_0_5_line_131 |  | 130 | 132 | 0.0016215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_2125-38_0_5_line_132 |  | 131 | 133 | 0.013503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_2125-38_0_5_line_133 |  | 133 | 134 | 0.0023029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_2125-38_0_5_line_134 |  | 134 | 135 | 0.011216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2125-38_0_5_trafo_52 | 0.63 MVA 20/0.4 kV | 136 | 62 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2570837.1311 | 1164031.0814 | 2570851.3153 | 1164024.8648 | 2570850.6538 | 1164009.0715
1 | 2570850.6538 | 1164009.0715 | 2570901.5668 | 1164055.4361
2 | 2570826.9387 | 1164045.4939 | 2570842.8334 | 1164044.5494 | 2570837.1311 | 1164031.0814
3 | 2570901.5668 | 1164055.4361 | 2570906.6718 | 1164065.8055 | 2570907.0435 | 1164085.5883
4 | 2570826.9387 | 1164045.4939 | 2570828.6854 | 1164069.4299
5 | 2570826.9387 | 1164045.4939 | 2570806.9606 | 1164046.1693 | 2570776.6436 | 1164047.186
6 | 2570911.4328 | 1164098.3656 | 2570907.2089 | 1164094.3952 | 2570907.0435 | 1164085.5883
7 | 2570829.0075 | 1164073.8447 | 2570828.6854 | 1164069.4299
8 | 2570733.2506 | 1164048.6412 | 2570776.6436 | 1164047.186
9 | 2570829.0075 | 1164073.8447 | 2570830.757 | 1164097.819
10 | 2570720.2736 | 1164049.5384 | 2570733.2506 | 1164048.6412
11 | 2570692.6926 | 1164329.9482 | 2570696.9379 | 1164336.4781
12 | 2570692.6926 | 1164329.9482 | 2570677.2746 | 1164306.2327
13 | 2570696.9379 | 1164336.4781 | 2570704.7027 | 1164348.4218 | 2570705.7973 | 1164349.8863
14 | 2570677.2746 | 1164306.2327 | 2570676.9925 | 1164305.7986
15 | 2570716.104 | 1164363.6752 | 2570705.7973 | 1164349.8863
16 | 2570662.5743 | 1164279.2295 | 2570675.0641 | 1164302.8325 | 2570676.9925 | 1164305.7986
17 | 2570662.5743 | 1164279.2295 | 2570659.2761 | 1164272.9967
18 | 2570647.8123 | 1164251.136 | 2570653.0262 | 1164261.1859 | 2570659.2761 | 1164272.9967
19 | 2570617.9314 | 1164193.5409 | 2570628.5189 | 1164213.9481
20 | 2570611.9798 | 1164182.0691 | 2570617.9314 | 1164193.5409
21 | 2570647.8123 | 1164251.136 | 2570628.5189 | 1164213.9481
22 | 2570611.9798 | 1164182.0691 | 2570605.2378 | 1164169.0741
23 | 2570605.2378 | 1164169.0741 | 2570588.5744 | 1164136.956
24 | 2570579.6012 | 1164129.3457 | 2570587.4782 | 1164134.8431 | 2570588.5744 | 1164136.956
25 | 2570674.8825 | 1164179.7251 | 2570666.7826 | 1164180.2664 | 2570648.8518 | 1164180.8562
26 | 2570681.7802 | 1164179.2642 | 2570674.8825 | 1164179.7251
27 | 2570579.6012 | 1164129.3457 | 2570579.6027 | 1164107.6247
28 | 2570579.6012 | 1164129.3457 | 2570576.9062 | 1164140.7327
29 | 2570681.7802 | 1164179.2642 | 2570700.5826 | 1164178.0077
30 | 2570722.9849 | 1164099.4801 | 2570722.5744 | 1164090.9259 | 2570721.8991 | 1164078.7797
31 | 2570721.5053 | 1164071.6958 | 2570721.8991 | 1164078.7797
32 | 2570722.9849 | 1164099.4801 | 2570723.486 | 1164109.9224
33 | 2570720.2736 | 1164049.5384 | 2570721.5053 | 1164071.6958
34 | 2570723.6518 | 1164113.3768 | 2570723.486 | 1164109.9224
35 | 2570720.2736 | 1164049.5384 | 2570700.3005 | 1164050.5308
36 | 2570724.3792 | 1164128.5351 | 2570723.6518 | 1164113.3768
37 | 2570680.4388 | 1164051.5178 | 2570700.3005 | 1164050.5308
38 | 2570724.3792 | 1164128.5351 | 2570725.1296 | 1164144.1711
39 | 2570680.4388 | 1164051.5178 | 2570676.6779 | 1164051.7046
40 | 2570566.862 | 1164168.9713 | 2570565.2668 | 1164172.8763
41 | 2570566.862 | 1164168.9713 | 2570574.8519 | 1164149.4125 | 2570576.9062 | 1164140.7327
42 | 2570549.664 | 1164197.4512 | 2570563.0391 | 1164178.3296 | 2570565.2668 | 1164172.8763
43 | 2570540.967 | 1164209.3872 | 2570542.6349 | 1164207.5003 | 2570549.664 | 1164197.4512
44 | 2570540.967 | 1164209.3872 | 2570550.439 | 1164224.1981
45 | 2570514.844 | 1164235.818 | 2570523.7928 | 1164228.8149 | 2570540.967 | 1164209.3872
46 | 2570579.6041 | 1164088.5044 | 2570579.6027 | 1164107.6247
47 | 2570557.8596 | 1164235.8012 | 2570550.439 | 1164224.1981
48 | 2570514.844 | 1164235.818 | 2570501.806 | 1164220.1679
49 | 2570514.844 | 1164235.818 | 2570505.918 | 1164242.7988 | 2570492.4594 | 1164249.6113
50 | 2570579.5668 | 1164064.6463 | 2570579.6056 | 1164067.87 | 2570579.6041 | 1164088.5044
51 | 2570806.9681 | 1164302.4706 | 2570882.0443 | 1164365.2644
52 | 2570806.9681 | 1164302.4706 | 2570807.0375 | 1164302.3657 | 2570816.2984 | 1164282.0905
53 | 2570795.8765 | 1164316.7611 | 2570799.6405 | 1164313.5518 | 2570806.9681 | 1164302.4706
54 | 2570820.1163 | 1164273.7319 | 2570816.2984 | 1164282.0905
55 | 2570791.3629 | 1164320.6096 | 2570795.8765 | 1164316.7611
56 | 2570866.6891 | 1164217.5545 | 2570874.9994 | 1164240.5035
57 | 2570866.6891 | 1164217.5545 | 2570850.7195 | 1164221.9011
58 | 2570579.5668 | 1164064.6463 | 2570575.5828 | 1164064.3435 | 2570572.0886 | 1164062.4041
59 | 2570568.9289 | 1164055.2827 | 2570569.7293 | 1164059.1918 | 2570572.0886 | 1164062.4041
60 | 2570573.9132 | 1164047.1874 | 2570571.2963 | 1164049.2235 | 2570569.564 | 1164052.0446 | 2570568.9289 | 1164055.2827
61 | 2570568.9289 | 1164055.2827 | 2570565.8582 | 1164055.3756 | 2570562.673 | 1164055.5246 | 2570530.1234 | 1164057.0076
62 | 2570578.7482 | 1164046.1187 | 2570582.9819 | 1164047.3763 | 2570586.1677 | 1164050.44 | 2570587.582 | 1164054.613
63 | 2570587.582 | 1164054.613 | 2570590.1089 | 1164054.5116 | 2570606.8487 | 1164054.2175
64 | 2570578.7482 | 1164046.1187 | 2570576.2601 | 1164046.3199 | 2570573.9132 | 1164047.1874
65 | 2570606.8487 | 1164054.2175 | 2570636.6387 | 1164053.6942 | 2570642.9067 | 1164053.3827
66 | 2570573.9132 | 1164047.1874 | 2570572.6441 | 1164044.5368 | 2570571.5523 | 1164042.1075 | 2570561.3065 | 1164019.035 | 2570547.3864 | 1163998.4024
67 | 2570516.2862 | 1164057.3981 | 2570530.1234 | 1164057.0076
68 | 2570530.1234 | 1164057.0076 | 2570526.0501 | 1164040.4162
69 | 2570654.8991 | 1164052.7868 | 2570642.9067 | 1164053.3827
70 | 2570700.5826 | 1164178.0077 | 2570707.3515 | 1164177.5554 | 2570715.0325 | 1164174.0424
71 | 2570725.5088 | 1164152.0721 | 2570725.8573 | 1164159.3335 | 2570716.7122 | 1164173.2742 | 2570715.0325 | 1164174.0424
72 | 2570725.5088 | 1164152.0721 | 2570725.1296 | 1164144.1711
73 | 2570460.8743 | 1164272.228 | 2570466.079 | 1164264.5283 | 2570480.968 | 1164255.4281 | 2570492.4594 | 1164249.6113
74 | 2570435.2343 | 1164310.1591 | 2570460.8743 | 1164272.228
75 | 2570501.806 | 1164220.1679 | 2570467.4546 | 1164178.9341
76 | 2570452.1515 | 1164160.5659 | 2570459.7988 | 1164169.7444 | 2570467.4546 | 1164178.9341
77 | 2570654.8991 | 1164052.7868 | 2570676.6779 | 1164051.7046
78 | 2570557.8596 | 1164235.8012 | 2570558.9693 | 1164237.5364
79 | 2570429.5471 | 1164133.4358 | 2570452.1515 | 1164160.5659
80 | 2570830.757 | 1164097.819 | 2570832.2317 | 1164118.0272 | 2570832.4004 | 1164118.7118
81 | 2570834.4155 | 1164126.8882 | 2570832.4004 | 1164118.7118
82 | 2570845.7762 | 1164158.215 | 2570837.8414 | 1164140.7892 | 2570834.4155 | 1164126.8882
83 | 2570826.561 | 1164169.2335 | 2570830.88 | 1164166.7569
84 | 2570826.561 | 1164169.2335 | 2570818.9697 | 1164173.5866 | 2570810.8816 | 1164178.4105
85 | 2570845.7762 | 1164158.215 | 2570830.88 | 1164166.7569
86 | 2570810.8816 | 1164178.4105 | 2570800.869 | 1164184.3821
87 | 2570845.7762 | 1164158.215 | 2570851.7262 | 1164174.9902
88 | 2570800.869 | 1164184.3821 | 2570799.7638 | 1164185.0413
89 | 2570791.1637 | 1164191.1769 | 2570794.3886 | 1164188.2471 | 2570799.7638 | 1164185.0413
90 | 2570778.0762 | 1164203.0666 | 2570791.1637 | 1164191.1769
91 | 2570850.7195 | 1164221.9011 | 2570850.7195 | 1164221.9011 | 2570840.6237 | 1164230.9214
92 | 2570825.8879 | 1164261.1678 | 2570833.9765 | 1164243.5602 | 2570840.6237 | 1164230.9214 | 2570840.6237 | 1164230.9214
93 | 2570820.1163 | 1164273.7319 | 2570825.8879 | 1164261.1678
94 | 2570820.1163 | 1164273.7319 | 2570815.52 | 1164271.9089 | 2570813.0818 | 1164268.8814
95 | 2570805.417 | 1164259.3643 | 2570813.0818 | 1164268.8814
96 | 2570730.421 | 1164241.1482 | 2570725.1115 | 1164244.914
97 | 2570730.421 | 1164241.1482 | 2570748.0913 | 1164228.6157 | 2570751.084 | 1164226.1787
98 | 2570725.1115 | 1164244.914 | 2570725.1115 | 1164244.914 | 2570734.5621 | 1164258.2361
99 | 2570757.6801 | 1164220.8074 | 2570751.084 | 1164226.1787
100 | 2570750.4725 | 1164280.6643 | 2570734.5621 | 1164258.2361
101 | 2570757.6801 | 1164220.8074 | 2570766.0554 | 1164213.9873 | 2570773.3259 | 1164207.3822
102 | 2570760.9319 | 1164295.0679 | 2570757.168 | 1164290.1026 | 2570750.4725 | 1164280.6643
103 | 2570778.0762 | 1164203.0666 | 2570773.3259 | 1164207.3822
104 | 2570760.9319 | 1164295.0679 | 2570766.2011 | 1164302.0192
105 | 2570798.754 | 1164251.0911 | 2570805.417 | 1164259.3643
106 | 2570797.4243 | 1164246.9733 | 2570798.754 | 1164251.0911
107 | 2570766.2011 | 1164302.0192 | 2570781.7039 | 1164322.4705
108 | 2570791.3629 | 1164320.6096 | 2570784.6391 | 1164326.3426 | 2570781.7039 | 1164322.4705
109 | 2570565.9362 | 1164248.4302 | 2570558.9693 | 1164237.5364
110 | 2570547.3864 | 1163998.4024 | 2570605.7044 | 1163991.0473
111 | 2570516.2862 | 1164057.3981 | 2570516.4976 | 1164074.6152
112 | 2570516.2862 | 1164057.3981 | 2570486.6515 | 1164058.5673
113 | 2570522.8999 | 1164031.6713 | 2570524.895 | 1164035.7114 | 2570526.0501 | 1164040.4162
114 | 2570605.7044 | 1163991.0473 | 2570665.3357 | 1163940.7996
115 | 2570516.5037 | 1164075.1123 | 2570516.4976 | 1164074.6152
116 | 2570475.405 | 1164059.0111 | 2570486.6515 | 1164058.5673
117 | 2570522.8999 | 1164031.6713 | 2570515.7458 | 1164017.1844
118 | 2570497.2499 | 1164159.0878 | 2570503.6006 | 1164167.9685
119 | 2570497.2499 | 1164159.0878 | 2570504.173 | 1164157.4863 | 2570509.3333 | 1164151.6777
120 | 2570497.2499 | 1164159.0878 | 2570485.5581 | 1164144.0374
121 | 2570509.3333 | 1164151.6777 | 2570512.0787 | 1164148.5873 | 2570517.1233 | 1164137.2234 | 2570517.0488 | 1164115.8573 | 2570516.9192 | 1164106.4676
122 | 2570471.1912 | 1164125.5436 | 2570485.5581 | 1164144.0374
123 | 2570516.9012 | 1164105.1637 | 2570516.9192 | 1164106.4676
124 | 2570516.9012 | 1164105.1637 | 2570516.6441 | 1164086.5444 | 2570516.5037 | 1164075.1123
125 | 2570449.6385 | 1164060.0277 | 2570475.405 | 1164059.0111
126 | 2570449.6385 | 1164060.0277 | 2570445.7724 | 1164060.3319
127 | 2570449.6385 | 1164060.0277 | 2570448.9172 | 1164041.6658
128 | 2570503.77 | 1164000.3883 | 2570503.9938 | 1164000.6242
129 | 2570503.9938 | 1164000.6242 | 2570511.4502 | 1164008.4859 | 2570515.7458 | 1164017.1844
130 | 2570586.0754 | 1164279.9207 | 2570580.4952 | 1164271.1953
131 | 2570586.949 | 1164281.2868 | 2570586.0754 | 1164279.9207
132 | 2570580.4952 | 1164271.1953 | 2570573.22 | 1164259.8195
133 | 2570571.9793 | 1164257.8794 | 2570573.22 | 1164259.8195
134 | 2570571.9793 | 1164257.8794 | 2570565.9362 | 1164248.4302

## bus_geodata
| x | y | coords
0 | 2570850.6538 | 1164009.0715
1 | 2570837.1311 | 1164031.0814
2 | 2570901.5668 | 1164055.4361
3 | 2570826.9387 | 1164045.4939
4 | 2570907.0435 | 1164085.5883
5 | 2570828.6854 | 1164069.4299
6 | 2570776.6436 | 1164047.186
7 | 2570829.0075 | 1164073.8447
8 | 2570733.2506 | 1164048.6412
9 | 2570692.6926 | 1164329.9482
10 | 2570696.9379 | 1164336.4781
11 | 2570677.2746 | 1164306.2327
12 | 2570705.7973 | 1164349.8863
13 | 2570676.9925 | 1164305.7986
14 | 2570716.104 | 1164363.6752
15 | 2570662.5743 | 1164279.2295
16 | 2570659.2761 | 1164272.9967
17 | 2570617.9314 | 1164193.5409
18 | 2570628.5189 | 1164213.9481
19 | 2570611.9798 | 1164182.0691
20 | 2570647.8123 | 1164251.136
21 | 2570605.2378 | 1164169.0741
22 | 2570588.5744 | 1164136.956
23 | 2570648.8518 | 1164180.8562
24 | 2570674.8825 | 1164179.7251
25 | 2570579.6012 | 1164129.3457
26 | 2570681.7802 | 1164179.2642
27 | 2570721.8991 | 1164078.7797
28 | 2570722.9849 | 1164099.4801
29 | 2570721.5053 | 1164071.6958
30 | 2570723.486 | 1164109.9224
31 | 2570720.2736 | 1164049.5384
32 | 2570723.6518 | 1164113.3768
33 | 2570700.3005 | 1164050.5308
34 | 2570724.3792 | 1164128.5351
35 | 2570680.4388 | 1164051.5178
36 | 2570566.862 | 1164168.9713
37 | 2570565.2668 | 1164172.8763
38 | 2570576.9062 | 1164140.7327
39 | 2570549.664 | 1164197.4512
40 | 2570540.967 | 1164209.3872
41 | 2570579.6027 | 1164107.6247
42 | 2570550.439 | 1164224.1981
43 | 2570514.844 | 1164235.818
44 | 2570579.6041 | 1164088.5044
45 | 2570882.0443 | 1164365.2644
46 | 2570806.9681 | 1164302.4706
47 | 2570816.2984 | 1164282.0905
48 | 2570795.8765 | 1164316.7611
49 | 2570874.9994 | 1164240.5035
50 | 2570866.6891 | 1164217.5545
51 | 2570579.5668 | 1164064.6463
52 | 2570572.0886 | 1164062.4041
53 | 2570568.9289 | 1164055.2827
54 | 2570587.582 | 1164054.613
55 | 2570578.7482 | 1164046.1187
56 | 2570606.8487 | 1164054.2175
57 | 2570573.9132 | 1164047.1874
58 | 2570530.1234 | 1164057.0076
59 | 2570642.9067 | 1164053.3827
60 | 2570700.5826 | 1164178.0077
61 | 2570715.0325 | 1164174.0424
62 | 2570725.5088 | 1164152.0721
63 | 2570725.1296 | 1164144.1711
64 | 2570460.8743 | 1164272.228
65 | 2570492.4594 | 1164249.6113
66 | 2570435.2343 | 1164310.1591
67 | 2570501.806 | 1164220.1679
68 | 2570467.4546 | 1164178.9341
69 | 2570654.8991 | 1164052.7868
70 | 2570676.6779 | 1164051.7046
71 | 2570557.8596 | 1164235.8012
72 | 2570452.1515 | 1164160.5659
73 | 2570830.757 | 1164097.819
74 | 2570832.4004 | 1164118.7118
75 | 2570834.4155 | 1164126.8882
76 | 2570911.4328 | 1164098.3656
77 | 2570826.561 | 1164169.2335
78 | 2570830.88 | 1164166.7569
79 | 2570810.8816 | 1164178.4105
80 | 2570845.7762 | 1164158.215
81 | 2570800.869 | 1164184.3821
82 | 2570851.7262 | 1164174.9902
83 | 2570799.7638 | 1164185.0413
84 | 2570791.1637 | 1164191.1769
85 | 2570850.7195 | 1164221.9011
86 | 2570840.6237 | 1164230.9214
87 | 2570825.8879 | 1164261.1678
88 | 2570820.1163 | 1164273.7319
89 | 2570813.0818 | 1164268.8814
90 | 2570730.421 | 1164241.1482
91 | 2570725.1115 | 1164244.914
92 | 2570751.084 | 1164226.1787
93 | 2570734.5621 | 1164258.2361
94 | 2570757.6801 | 1164220.8074
95 | 2570750.4725 | 1164280.6643
96 | 2570773.3259 | 1164207.3822
97 | 2570760.9319 | 1164295.0679
98 | 2570778.0762 | 1164203.0666
99 | 2570798.754 | 1164251.0911
100 | 2570805.417 | 1164259.3643
101 | 2570797.4243 | 1164246.9733
102 | 2570766.2011 | 1164302.0192
103 | 2570781.7039 | 1164322.4705
104 | 2570791.3629 | 1164320.6096
105 | 2570558.9693 | 1164237.5364
106 | 2570547.3864 | 1163998.4024
107 | 2570516.2862 | 1164057.3981
108 | 2570526.0501 | 1164040.4162
109 | 2570605.7044 | 1163991.0473
110 | 2570516.4976 | 1164074.6152
111 | 2570486.6515 | 1164058.5673
112 | 2570522.8999 | 1164031.6713
113 | 2570503.6006 | 1164167.9685
114 | 2570497.2499 | 1164159.0878
115 | 2570509.3333 | 1164151.6777
116 | 2570485.5581 | 1164144.0374
117 | 2570516.9192 | 1164106.4676
118 | 2570471.1912 | 1164125.5436
119 | 2570516.9012 | 1164105.1637
120 | 2570516.5037 | 1164075.1123
121 | 2570665.3357 | 1163940.7996
122 | 2570429.5471 | 1164133.4358
123 | 2570475.405 | 1164059.0111
124 | 2570449.6385 | 1164060.0277
125 | 2570445.7724 | 1164060.3319
126 | 2570448.9172 | 1164041.6658
127 | 2570503.77 | 1164000.3883
128 | 2570503.9938 | 1164000.6242
129 | 2570515.7458 | 1164017.1844
130 | 2570586.0754 | 1164279.9207
131 | 2570580.4952 | 1164271.1953
132 | 2570586.949 | 1164281.2868
133 | 2570573.22 | 1164259.8195
134 | 2570571.9793 | 1164257.8794
135 | 2570565.9362 | 1164248.4302
136 | 2570720.2736 | 1164049.5384

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98089 | -0.36614 | 0.015538 | 0.0038943
1 | 0.98251 | -0.33465 | 0 | 0
2 | 0.97833 | -0.41631 | 0 | 0
3 | 0.98408 | -0.304 | 0 | 0
4 | 0.97716 | -0.43923 | 0.01699 | 0.0042582
5 | 0.98306 | -0.32379 | 0.0064799 | 0.001624
6 | 0.98687 | -0.2501 | 0.0028065 | 0.00070338
7 | 0.98288 | -0.32732 | 0.016266 | 0.0040766
8 | 0.9893 | -0.2033 | 0 | 0
9 | 0.97053 | -0.56892 | 0.0039415 | 0.00098784
10 | 0.97045 | -0.57063 | 0.0031358 | 0.0007859
11 | 0.97095 | -0.56062 | 0.0032207 | 0.00080718
12 | 0.97032 | -0.57324 | 0.0047977 | 0.0012024
13 | 0.97096 | -0.56044 | 0.0036443 | 0.00091334
14 | 0.97025 | -0.57451 | 0.0039709 | 0.00099519
15 | 0.9716 | -0.54775 | 0.0031382 | 0.0007865
16 | 0.97177 | -0.54439 | 0.0042674 | 0.0010695
17 | 0.97462 | -0.48829 | 0.0013056 | 0.00032722
18 | 0.97381 | -0.50421 | 0.0033793 | 0.00084693
19 | 0.97509 | -0.47904 | 0 | 0
20 | 0.97247 | -0.53067 | 0.0042016 | 0.001053
21 | 0.97562 | -0.46858 | 0.0027226 | 0.00068234
22 | 0.97703 | -0.44097 | 0.0035384 | 0.00088681
23 | 0.99916 | -0.016101 | 0.0033168 | 0.00083126
24 | 0.99924 | -0.014592 | 0.0023895 | 0.00059885
25 | 0.97754 | -0.43107 | 0 | 0
26 | 0.99928 | -0.013904 | 0.0031999 | 0.00080198
27 | 0.99279 | -0.1365 | 0.005838 | 0.0014632
28 | 0.99479 | -0.098475 | 0.002138 | 0.00053584
29 | 0.99211 | -0.14937 | 0.0036883 | 0.00092438
30 | 0.9958 | -0.079257 | 0.0059268 | 0.0014854
31 | 0.99002 | -0.18936 | 0 | 0
32 | 0.99614 | -0.072818 | 0.0034295 | 0.00085951
33 | 0.98926 | -0.20402 | 0.0019188 | 0.0004809
34 | 0.99764 | -0.044388 | 0.0020163 | 0.00050534
35 | 0.98851 | -0.21844 | 0.0013118 | 0.00032877
36 | 0.97597 | -0.46193 | 0.0050662 | 0.0012697
37 | 0.97584 | -0.46455 | 0.0038293 | 0.0009597
38 | 0.97706 | -0.44045 | 0.0048316 | 0.0012109
39 | 0.97501 | -0.48073 | 0.003795 | 0.00095112
40 | 0.97465 | -0.48789 | 0 | 0
41 | 0.97935 | -0.39579 | 0.0046747 | 0.0011716
42 | 0.97448 | -0.49119 | 0.0011198 | 0.00028064
43 | 0.97409 | -0.49893 | 0 | 0
44 | 0.98102 | -0.36322 | 0.0019648 | 0.00049243
45 | 0.97327 | -0.5157 | 0.0051989 | 0.001303
46 | 0.97375 | -0.50634 | 0.0039978 | 0.0010019
47 | 0.97346 | -0.51196 | 0.00094458 | 0.00023674
48 | 0.97414 | -0.49869 | 0.0036609 | 0.00091752
49 | 0.97313 | -0.51856 | 0.00093951 | 0.00023546
50 | 0.97315 | -0.51814 | 0 | 0
51 | 0.98315 | -0.3219 | 0 | 0
52 | 0.98386 | -0.30809 | 0.0012863 | 0.00032239
53 | 0.98422 | -0.30112 | 0 | 0
54 | 0.98517 | -0.28275 | 0 | 0
55 | 0.98472 | -0.29154 | 0 | 0
56 | 0.98583 | -0.26995 | 0.0060294 | 0.0015111
57 | 0.98455 | -0.29486 | 0 | 0
58 | 0.98267 | -0.33136 | 0 | 0
59 | 0.98712 | -0.24506 | 0.0029468 | 0.00073855
60 | 0.99943 | -0.010974 | 0.0034248 | 0.00085835
61 | 0.9996 | -0.0076972 | 0.0047837 | 0.0011989
62 | 1 | 0 | -0.46224 | -0.11864
63 | 0.9992 | -0.015013 | 0.0059265 | 0.0014853
64 | 0.97379 | -0.50485 | 0.0018167 | 0.00045532
65 | 0.97395 | -0.50166 | 0.0012379 | 0.00031023
66 | 0.97368 | -0.507 | 0.0025592 | 0.00064139
67 | 0.97389 | -0.50288 | 0.001571 | 0.00039374
68 | 0.97344 | -0.51172 | 0.0018866 | 0.00047282
69 | 0.98756 | -0.23664 | 0.0020378 | 0.00051071
70 | 0.98837 | -0.22115 | 0.0024049 | 0.00060272
71 | 0.97437 | -0.4935 | 0.0021031 | 0.00052709
72 | 0.97328 | -0.51484 | 0.0032517 | 0.00081495
73 | 0.98199 | -0.34472 | 0.0059268 | 0.0014854
74 | 0.98124 | -0.35936 | 0.0068687 | 0.0017215
75 | 0.98095 | -0.36498 | 0.021546 | 0.0054
76 | 0.97685 | -0.44539 | 0.023115 | 0.0057932
77 | 0.97944 | -0.39458 | 0.0061371 | 0.0015381
78 | 0.97955 | -0.39234 | 0.0065677 | 0.001646
79 | 0.97904 | -0.40227 | 0.0053032 | 0.0013291
80 | 0.97997 | -0.38409 | 0 | 0
81 | 0.97881 | -0.40693 | 0.0059241 | 0.0014847
82 | 0.97964 | -0.39059 | 0.020123 | 0.0050432
83 | 0.97878 | -0.40741 | 0.0074546 | 0.0018683
84 | 0.9786 | -0.411 | 0.0038286 | 0.00095955
85 | 0.97317 | -0.51786 | 0.0011366 | 0.00028485
86 | 0.97319 | -0.51734 | 0.0012812 | 0.0003211
87 | 0.9733 | -0.51526 | 0.0011594 | 0.00029058
88 | 0.97335 | -0.51411 | 0 | 0
89 | 0.97329 | -0.51543 | 0.0010243 | 0.00025672
90 | 0.97744 | -0.43377 | 0.003837 | 0.00096163
91 | 0.97736 | -0.43537 | 0.0039408 | 0.00098766
92 | 0.97778 | -0.42707 | 0.0037068 | 0.00092902
93 | 0.97717 | -0.43908 | 0.0030983 | 0.0007765
94 | 0.9779 | -0.4247 | 0.002798 | 0.00070124
95 | 0.97657 | -0.45081 | 0.0029357 | 0.00073577
96 | 0.97821 | -0.41867 | 0.0039843 | 0.00099856
97 | 0.97584 | -0.46507 | 0.0047594 | 0.0011928
98 | 0.97831 | -0.41668 | 0.002527 | 0.00063333
99 | 0.97315 | -0.51825 | 0.0035565 | 0.00089135
100 | 0.97321 | -0.51704 | 0.00097234 | 0.00024369
101 | 0.97313 | -0.51846 | 0.0026143 | 0.00065521
102 | 0.97553 | -0.4713 | 0.0035259 | 0.00088367
103 | 0.97468 | -0.488 | 0.0044148 | 0.0011064
104 | 0.97428 | -0.49581 | 0.0045804 | 0.001148
105 | 0.97435 | -0.49377 | 0.00058334 | 0.0001462
106 | 0.98416 | -0.30246 | 0.0031644 | 0.00079306
107 | 0.98225 | -0.33957 | 0 | 0
108 | 0.98251 | -0.33454 | 0.0019861 | 0.00049778
109 | 0.98392 | -0.30713 | 0.002997 | 0.00075111
110 | 0.98188 | -0.34679 | 0.0028783 | 0.00072136
111 | 0.98198 | -0.34481 | 0.0026039 | 0.00065259
112 | 0.98244 | -0.33595 | 0.0022819 | 0.0005719
113 | 0.98072 | -0.36963 | 0.0011735 | 0.00029412
114 | 0.98073 | -0.3694 | 0 | 0
115 | 0.98084 | -0.36715 | 0.0030548 | 0.00076561
116 | 0.9806 | -0.37188 | 0.0029808 | 0.00074705
117 | 0.98134 | -0.35739 | 0.002888 | 0.00072379
118 | 0.98051 | -0.37365 | 0.0041814 | 0.001048
119 | 0.98136 | -0.35705 | 0.0042545 | 0.0010663
120 | 0.98187 | -0.34698 | 0.001784 | 0.0004471
121 | 0.98382 | -0.30912 | 0.0014148 | 0.00035457
122 | 0.97316 | -0.51732 | 0.0038249 | 0.00095862
123 | 0.98191 | -0.34627 | 0.0025197 | 0.00063151
124 | 0.9818 | -0.34844 | 0 | 0
125 | 0.98179 | -0.34862 | 0.0025347 | 0.00063526
126 | 0.98176 | -0.34915 | 0.0021163 | 0.0005304
127 | 0.98227 | -0.33922 | 0.0021058 | 0.00052777
128 | 0.98227 | -0.33921 | 0.0018879 | 0.00047316
129 | 0.98235 | -0.33772 | 0.0020726 | 0.00051945
130 | 0.97414 | -0.49799 | 0.002092 | 0.0005243
131 | 0.97417 | -0.49746 | 0.0004864 | 0.0001219
132 | 0.97414 | -0.49801 | 0.00067413 | 0.00016895
133 | 0.97421 | -0.49665 | 0.00049681 | 0.00012451
134 | 0.97421 | -0.49649 | 0.0020469 | 0.00051301
135 | 0.97427 | -0.4953 | 0.00064953 | 0.00016279
136 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.055791 | -0.014038 | 0.055875 | 0.014092 | 8.41e-05 | 5.3428e-05 | 0.084655 | 0.084655 | 0.084655 | 0.98089 | -0.36614 | 0.98251 | -0.33465 | 23.2569
1 | 0.040253 | 0.010144 | -0.040156 | -0.010083 | 9.635e-05 | 6.0797e-05 | 0.061083 | 0.061084 | 0.061084 | 0.98089 | -0.36614 | 0.97833 | -0.41631 | 16.7812
2 | -0.055875 | -0.014092 | 0.055957 | 0.014144 | 8.2096e-05 | 5.2154e-05 | 0.084655 | 0.084655 | 0.084655 | 0.98251 | -0.33465 | 0.98408 | -0.304 | 23.2569
3 | 0.040156 | 0.010083 | -0.040112 | -0.010056 | 4.3857e-05 | 2.7675e-05 | 0.061084 | 0.061084 | 0.061084 | 0.97833 | -0.41631 | 0.97716 | -0.43923 | 16.7813
4 | 0.18396 | 0.046452 | -0.18379 | -0.046341 | 0.00017425 | 0.0001103 | 0.27829 | 0.27829 | 0.27829 | 0.98408 | -0.304 | 0.98306 | -0.32379 | 19.1133
5 | -0.23992 | -0.060596 | 0.24054 | 0.060991 | 0.00062147 | 0.00039518 | 0.36294 | 0.36294 | 0.36294 | 0.98408 | -0.304 | 0.98687 | -0.2501 | 24.9274
6 | 0.023122 | 0.0057974 | -0.023115 | -0.0057932 | 6.7904e-06 | 4.163e-06 | 0.035211 | 0.035211 | 0.035211 | 0.97716 | -0.43923 | 0.97685 | -0.44539 | 9.6733
7 | 0.17731 | 0.044717 | -0.17728 | -0.044698 | 2.9913e-05 | 1.892e-05 | 0.26848 | 0.26848 | 0.26848 | 0.98306 | -0.32379 | 0.98288 | -0.32732 | 18.4396
8 | -0.24335 | -0.061694 | 0.24389 | 0.062043 | 0.00054876 | 0.00034898 | 0.36717 | 0.36717 | 0.36717 | 0.98687 | -0.2501 | 0.9893 | -0.2033 | 25.218
9 | 0.16101 | 0.040622 | -0.16088 | -0.040537 | 0.00013401 | 8.4549e-05 | 0.24386 | 0.24386 | 0.24386 | 0.98288 | -0.32732 | 0.98199 | -0.34472 | 16.7484
10 | -0.24389 | -0.062043 | 0.24406 | 0.062147 | 0.00016393 | 0.00010425 | 0.36717 | 0.36717 | 0.36717 | 0.9893 | -0.2033 | 0.99002 | -0.18936 | 25.218
11 | 0.011907 | 0.0029845 | -0.011906 | -0.0029839 | 9.7335e-07 | 5.2671e-07 | 0.018255 | 0.018255 | 0.018255 | 0.97053 | -0.56892 | 0.97045 | -0.57063 | 5.0152
12 | -0.015848 | -0.0039723 | 0.015854 | 0.003976 | 6.2628e-06 | 3.6585e-06 | 0.024298 | 0.024298 | 0.024298 | 0.97053 | -0.56892 | 0.97095 | -0.56062 | 6.6754
13 | 0.0087699 | 0.002198 | -0.0087688 | -0.0021975 | 1.09e-06 | 4.9902e-07 | 0.013447 | 0.013447 | 0.013447 | 0.97045 | -0.57063 | 0.97032 | -0.57324 | 3.6943
14 | -0.019075 | -0.0047831 | 0.019075 | 0.0047832 | 1.6592e-07 | 9.9786e-08 | 0.029234 | 0.029234 | 0.029234 | 0.97095 | -0.56062 | 0.97096 | -0.56044 | 8.0313
15 | 0.0039711 | 0.00099513 | -0.0039709 | -0.00099519 | 2.3941e-07 | -5.9402e-08 | 0.0060898 | 0.0060899 | 0.0060899 | 0.97032 | -0.57324 | 0.97025 | -0.57451 | 1.673
16 | -0.02272 | -0.0056966 | 0.022733 | 0.005705 | 1.3749e-05 | 8.425e-06 | 0.034819 | 0.034819 | 0.034819 | 0.97096 | -0.56044 | 0.9716 | -0.54775 | 9.5657
17 | -0.025871 | -0.0064915 | 0.025876 | 0.0064941 | 4.1521e-06 | 2.57e-06 | 0.039625 | 0.039625 | 0.039625 | 0.9716 | -0.54775 | 0.97177 | -0.54439 | 10.886
18 | -0.030143 | -0.0075636 | 0.030163 | 0.0075759 | 1.9723e-05 | 1.2317e-05 | 0.046159 | 0.046159 | 0.046159 | 0.97177 | -0.54439 | 0.97247 | -0.53067 | 12.6811
19 | 0.037816 | 0.0095213 | -0.037787 | -0.0095032 | 2.8754e-05 | 1.8117e-05 | 0.057752 | 0.057752 | 0.057752 | 0.97462 | -0.48829 | 0.97381 | -0.50421 | 15.8659
20 | -0.039121 | -0.0098485 | 0.039139 | 0.0098594 | 1.7299e-05 | 1.091e-05 | 0.059745 | 0.059745 | 0.059745 | 0.97462 | -0.48829 | 0.97509 | -0.47904 | 16.4135
21 | 0.034408 | 0.0086562 | -0.034364 | -0.0086289 | 4.3448e-05 | 2.7286e-05 | 0.052588 | 0.052588 | 0.052588 | 0.97381 | -0.50421 | 0.97247 | -0.53067 | 14.4473
22 | -0.039139 | -0.0098594 | 0.039158 | 0.0098718 | 1.9596e-05 | 1.2359e-05 | 0.059745 | 0.059745 | 0.059745 | 0.97509 | -0.47904 | 0.97562 | -0.46858 | 16.4134
23 | -0.041881 | -0.010554 | 0.041936 | 0.010589 | 5.5399e-05 | 3.5003e-05 | 0.063897 | 0.063897 | 0.063897 | 0.97562 | -0.46858 | 0.97703 | -0.44097 | 17.5542
24 | -0.045475 | -0.011476 | 0.045496 | 0.01149 | 2.1577e-05 | 1.3659e-05 | 0.069286 | 0.069286 | 0.069286 | 0.97703 | -0.44097 | 0.97754 | -0.43107 | 19.0347
25 | -0.0033168 | -0.00083126 | 0.003317 | 0.00083107 | 2.3842e-07 | -1.8873e-07 | 0.0049396 | 0.0049394 | 0.0049396 | 0.99916 | -0.016101 | 0.99924 | -0.014592 | 1.357
26 | -0.0057065 | -0.0014299 | 0.0057067 | 0.00143 | 1.872e-07 | 2.9247e-08 | 0.0084977 | 0.0084977 | 0.0084977 | 0.99924 | -0.014592 | 0.99928 | -0.013904 | 2.3345
27 | -0.089536 | -0.022567 | 0.089687 | 0.022664 | 0.00015141 | 9.6627e-05 | 0.13634 | 0.13634 | 0.13634 | 0.97754 | -0.43107 | 0.97935 | -0.39579 | 37.4555
28 | 0.04404 | 0.011078 | -0.04402 | -0.011065 | 1.9729e-05 | 1.248e-05 | 0.067052 | 0.067052 | 0.067052 | 0.97754 | -0.43107 | 0.97706 | -0.44045 | 18.4209
29 | -0.0089066 | -0.0022319 | 0.0089078 | 0.0022325 | 1.243e-06 | 5.4862e-07 | 0.013263 | 0.013263 | 0.013263 | 0.99928 | -0.013904 | 0.99943 | -0.010974 | 3.6436
30 | -0.42117 | -0.10766 | 0.42195 | 0.10815 | 0.00077625 | 0.00049573 | 0.63201 | 0.63201 | 0.63201 | 0.99279 | -0.1365 | 0.99479 | -0.098475 | 43.4075
31 | 0.41533 | 0.10619 | -0.41508 | -0.10603 | 0.00025838 | 0.000165 | 0.62326 | 0.62326 | 0.62326 | 0.99279 | -0.1365 | 0.99211 | -0.14937 | 42.8065
32 | -0.42409 | -0.10869 | 0.42448 | 0.10894 | 0.00039546 | 0.00025255 | 0.63521 | 0.63521 | 0.63521 | 0.99479 | -0.098475 | 0.9958 | -0.079257 | 43.6271
33 | 0.41139 | 0.1051 | -0.41059 | -0.1046 | 0.00079389 | 0.00050695 | 0.61773 | 0.61773 | 0.61773 | 0.99211 | -0.14937 | 0.99002 | -0.18936 | 42.4266
34 | -0.43041 | -0.11043 | 0.43054 | 0.11051 | 0.00013449 | 8.5896e-05 | 0.64407 | 0.64407 | 0.64407 | 0.9958 | -0.079257 | 0.99614 | -0.072818 | 44.2354
35 | 0.16653 | 0.042449 | -0.16642 | -0.042375 | 0.0001177 | 7.4299e-05 | 0.25056 | 0.25056 | 0.25056 | 0.99002 | -0.18936 | 0.98926 | -0.20402 | 17.2087
36 | -0.43397 | -0.11137 | 0.43457 | 0.11175 | 0.0005996 | 0.00038296 | 0.64919 | 0.64919 | 0.64919 | 0.99614 | -0.072818 | 0.99764 | -0.044388 | 44.5872
37 | 0.1645 | 0.041894 | -0.16438 | -0.041822 | 0.00011436 | 7.2171e-05 | 0.24767 | 0.24767 | 0.24767 | 0.98926 | -0.20402 | 0.98851 | -0.21844 | 17.0105
38 | -0.43659 | -0.11226 | 0.43721 | 0.11266 | 0.00062424 | 0.0003987 | 0.6522 | 0.6522 | 0.6522 | 0.99764 | -0.044388 | 0.9992 | -0.015013 | 44.7937
39 | 0.16307 | 0.041493 | -0.16305 | -0.04148 | 2.1311e-05 | 1.3446e-05 | 0.2457 | 0.2457 | 0.2457 | 0.98851 | -0.21844 | 0.98837 | -0.22115 | 16.8749
40 | 0.034082 | 0.0085591 | -0.034078 | -0.0085564 | 4.2723e-06 | 2.6816e-06 | 0.05197 | 0.05197 | 0.05197 | 0.97597 | -0.46193 | 0.97584 | -0.46455 | 14.2774
41 | -0.039148 | -0.0098288 | 0.039188 | 0.0098541 | 4.0151e-05 | 2.5321e-05 | 0.059694 | 0.059694 | 0.059694 | 0.97597 | -0.46193 | 0.97706 | -0.44045 | 16.3994
42 | 0.030248 | 0.0075967 | -0.030225 | -0.0075821 | 2.3323e-05 | 1.4562e-05 | 0.046131 | 0.046131 | 0.046131 | 0.97584 | -0.46455 | 0.97501 | -0.48073 | 12.6733
43 | 0.02643 | 0.006631 | -0.026421 | -0.0066254 | 9.0201e-06 | 5.5885e-06 | 0.040339 | 0.040339 | 0.040339 | 0.97501 | -0.48073 | 0.97465 | -0.48789 | 11.0821
44 | 0.010256 | 0.0025707 | -0.010254 | -0.0025699 | 1.6163e-06 | 8.1539e-07 | 0.015658 | 0.015658 | 0.015658 | 0.97465 | -0.48789 | 0.97448 | -0.49119 | 4.3016
45 | 0.016165 | 0.0040547 | -0.016157 | -0.0040497 | 8.5081e-06 | 4.9813e-06 | 0.024681 | 0.024681 | 0.024681 | 0.97465 | -0.48789 | 0.97409 | -0.49893 | 6.7806
46 | -0.094362 | -0.023835 | 0.09451 | 0.023929 | 0.00014753 | 9.4176e-05 | 0.14344 | 0.14344 | 0.14344 | 0.97935 | -0.39579 | 0.98102 | -0.36322 | 39.4068
47 | 0.0091344 | 0.0022893 | -0.0091333 | -0.0022888 | 1.0048e-06 | 4.7151e-07 | 0.013948 | 0.013948 | 0.013948 | 0.97448 | -0.49119 | 0.97437 | -0.4935 | 3.8319
48 | 0.010541 | 0.0026431 | -0.01054 | -0.0026421 | 1.9809e-06 | 1.0142e-06 | 0.016104 | 0.016104 | 0.016104 | 0.97409 | -0.49893 | 0.97389 | -0.50288 | 4.4241
49 | 0.0056154 | 0.0014066 | -0.0056147 | -0.0014065 | 7.2888e-07 | 1.377e-07 | 0.0085778 | 0.0085779 | 0.0085779 | 0.97409 | -0.49893 | 0.97395 | -0.50166 | 2.3566
50 | -0.096474 | -0.024422 | 0.096666 | 0.024544 | 0.00019181 | 0.00012246 | 0.14642 | 0.14642 | 0.14642 | 0.98102 | -0.36322 | 0.98315 | -0.3219 | 40.2255
51 | -0.0051989 | -0.001303 | 0.0052012 | 0.0013032 | 2.3187e-06 | 2.6704e-07 | 0.0079484 | 0.007948 | 0.0079484 | 0.97327 | -0.5157 | 0.97375 | -0.50634 | 2.1836
52 | 0.013636 | 0.0034181 | -0.013632 | -0.0034161 | 3.6499e-06 | 2.0572e-06 | 0.020838 | 0.020838 | 0.020838 | 0.97375 | -0.50634 | 0.97346 | -0.51196 | 5.7247
53 | -0.022835 | -0.0057233 | 0.022843 | 0.0057284 | 8.3247e-06 | 5.1009e-06 | 0.034895 | 0.034895 | 0.034895 | 0.97375 | -0.50634 | 0.97414 | -0.49869 | 9.5865
54 | 0.012688 | 0.0031793 | -0.012686 | -0.0031786 | 1.2961e-06 | 7.1528e-07 | 0.019394 | 0.019394 | 0.019394 | 0.97346 | -0.51196 | 0.97335 | -0.51411 | 5.328
55 | -0.026504 | -0.0066459 | 0.026508 | 0.0066481 | 3.6461e-06 | 2.2597e-06 | 0.040487 | 0.040487 | 0.040487 | 0.97414 | -0.49869 | 0.97428 | -0.49581 | 11.1228
56 | -0.00093951 | -0.00023546 | 0.00093953 | 0.00023517 | 1.8888e-08 | -2.9115e-07 | 0.0014366 | 0.0014365 | 0.0014366 | 0.97313 | -0.51856 | 0.97315 | -0.51814 | 0.39467
57 | -0.00093953 | -0.00023517 | 0.00093954 | 0.00023498 | 1.2807e-08 | -1.9744e-07 | 0.0014365 | 0.0014364 | 0.0014365 | 0.97315 | -0.51814 | 0.97317 | -0.51786 | 0.39464
58 | -0.096666 | -0.024544 | 0.096731 | 0.024585 | 6.4251e-05 | 4.1019e-05 | 0.14642 | 0.14642 | 0.14642 | 0.98315 | -0.3219 | 0.98386 | -0.30809 | 40.2255
59 | -0.098017 | -0.024908 | 0.09805 | 0.024929 | 3.2919e-05 | 2.0866e-05 | 0.14837 | 0.14837 | 0.14837 | 0.98386 | -0.30809 | 0.98422 | -0.30112 | 20.38
60 | -0.14146 | -0.035845 | 0.1415 | 0.035872 | 4.2586e-05 | 2.6751e-05 | 0.21401 | 0.21401 | 0.21401 | 0.98422 | -0.30112 | 0.98455 | -0.29486 | 14.6985
61 | 0.043411 | 0.010917 | -0.043348 | -0.010877 | 6.2588e-05 | 3.9565e-05 | 0.065645 | 0.065645 | 0.065645 | 0.98422 | -0.30112 | 0.98267 | -0.33136 | 18.0344
62 | 0.14917 | 0.037825 | -0.14911 | -0.037786 | 6.3027e-05 | 3.9664e-05 | 0.22547 | 0.22547 | 0.22547 | 0.98517 | -0.28275 | 0.98472 | -0.29154 | 15.4853
63 | -0.14917 | -0.037825 | 0.14926 | 0.037883 | 9.1843e-05 | 5.7797e-05 | 0.22547 | 0.22547 | 0.22547 | 0.98517 | -0.28275 | 0.98583 | -0.26995 | 15.4853
64 | 0.14911 | 0.037786 | -0.14908 | -0.037771 | 2.3757e-05 | 1.4951e-05 | 0.22547 | 0.22547 | 0.22547 | 0.98472 | -0.29154 | 0.98455 | -0.29486 | 15.4853
65 | -0.15529 | -0.039394 | 0.15548 | 0.039512 | 0.00018606 | 0.00011724 | 0.23457 | 0.23457 | 0.23457 | 0.98583 | -0.26995 | 0.98712 | -0.24506 | 16.1103
66 | 0.0075799 | 0.0018988 | -0.0075772 | -0.0018977 | 2.743e-06 | 1.047e-06 | 0.011456 | 0.011456 | 0.011456 | 0.98455 | -0.29486 | 0.98416 | -0.30246 | 3.1473
67 | 0.033011 | 0.008286 | -0.032998 | -0.0082779 | 1.2935e-05 | 8.1036e-06 | 0.049992 | 0.049992 | 0.049992 | 0.98267 | -0.33136 | 0.98225 | -0.33957 | 13.734
68 | 0.010337 | 0.0025911 | -0.010336 | -0.0025903 | 1.5698e-06 | 7.8829e-07 | 0.015654 | 0.015654 | 0.015654 | 0.98267 | -0.33136 | 0.98251 | -0.33454 | 4.3004
69 | -0.15842 | -0.04025 | 0.15849 | 0.040291 | 6.4304e-05 | 4.054e-05 | 0.23901 | 0.23901 | 0.23901 | 0.98712 | -0.24506 | 0.98756 | -0.23664 | 16.4154
70 | -0.012333 | -0.0030908 | 0.012335 | 0.0030919 | 1.9256e-06 | 1.0328e-06 | 0.018362 | 0.018362 | 0.018362 | 0.99943 | -0.010974 | 0.9996 | -0.0076972 | 5.0444
71 | -0.017118 | -0.0042908 | 0.017125 | 0.0042945 | 6.28e-06 | 3.681e-06 | 0.025483 | 0.025483 | 0.025483 | 0.9996 | -0.0076972 | 1 | 0 | 7.0008
72 | 0.44346 | 0.11435 | -0.44314 | -0.11414 | 0.00032403 | 0.00020696 | 0.66102 | 0.66102 | 0.66102 | 1 | 0 | 0.9992 | -0.015013 | 45.3999
73 | -0.0043762 | -0.0010963 | 0.0043768 | 0.0010962 | 6.6438e-07 | -6.7814e-08 | 0.0066869 | 0.0066867 | 0.0066869 | 0.97379 | -0.50485 | 0.97395 | -0.50166 | 1.8371
74 | 0.0025594 | 0.00064098 | -0.0025592 | -0.00064139 | 2.626e-07 | -4.0145e-07 | 0.0039108 | 0.003911 | 0.003911 | 0.97379 | -0.50485 | 0.97368 | -0.507 | 1.0745
75 | 0.0089685 | 0.0022484 | -0.0089647 | -0.0022466 | 3.7792e-06 | 1.7512e-06 | 0.013703 | 0.013703 | 0.013703 | 0.97389 | -0.50288 | 0.97344 | -0.51172 | 3.7647
76 | 0.0070781 | 0.0017738 | -0.0070771 | -0.0017734 | 1.0495e-06 | 3.7454e-07 | 0.01082 | 0.01082 | 0.01082 | 0.97344 | -0.51172 | 0.97328 | -0.51484 | 2.9725
77 | -0.16053 | -0.040801 | 0.16065 | 0.040877 | 0.0001198 | 7.5554e-05 | 0.24208 | 0.24208 | 0.24208 | 0.98756 | -0.23664 | 0.98837 | -0.22115 | 16.6262
78 | 0.0070302 | 0.0017617 | -0.0070302 | -0.0017617 | 8.9031e-08 | 3.1326e-08 | 0.010736 | 0.010736 | 0.010736 | 0.97437 | -0.4935 | 0.97435 | -0.49377 | 2.9495
79 | 0.0038254 | 0.00095847 | -0.0038249 | -0.00095862 | 4.5295e-07 | -1.4891e-07 | 0.0058484 | 0.0058485 | 0.0058485 | 0.97328 | -0.51484 | 0.97316 | -0.51732 | 1.6067
80 | 0.15495 | 0.039052 | -0.15484 | -0.038984 | 0.00010844 | 6.834e-05 | 0.23488 | 0.23488 | 0.23488 | 0.98199 | -0.34472 | 0.98124 | -0.35936 | 16.1316
81 | 0.14797 | 0.037262 | -0.14793 | -0.037237 | 3.9776e-05 | 2.5031e-05 | 0.22446 | 0.22446 | 0.22446 | 0.98124 | -0.35936 | 0.98095 | -0.36498 | 15.4162
82 | 0.12639 | 0.031837 | -0.12627 | -0.031765 | 0.00011538 | 7.2157e-05 | 0.19178 | 0.19178 | 0.19178 | 0.98095 | -0.36498 | 0.97997 | -0.38409 | 13.1715
83 | -0.099523 | -0.025039 | 0.099533 | 0.025046 | 1.0676e-05 | 6.5817e-06 | 0.15123 | 0.15123 | 0.15123 | 0.97944 | -0.39458 | 0.97955 | -0.39234 | 10.387
84 | 0.093385 | 0.023501 | -0.093351 | -0.02348 | 3.4302e-05 | 2.1039e-05 | 0.14191 | 0.14191 | 0.14191 | 0.97944 | -0.39458 | 0.97904 | -0.40227 | 9.7467
85 | -0.1061 | -0.026692 | 0.10614 | 0.026718 | 4.1838e-05 | 2.5911e-05 | 0.16121 | 0.16121 | 0.16121 | 0.97955 | -0.39234 | 0.97997 | -0.38409 | 11.0722
86 | 0.088048 | 0.022151 | -0.088028 | -0.022139 | 1.9582e-05 | 1.1946e-05 | 0.13385 | 0.13385 | 0.13385 | 0.97904 | -0.40227 | 0.97881 | -0.40693 | 9.1931
87 | 0.020129 | 0.005047 | -0.020123 | -0.0050432 | 6.2356e-06 | 3.7666e-06 | 0.030565 | 0.030565 | 0.030565 | 0.97997 | -0.38409 | 0.97964 | -0.39059 | 8.397
88 | 0.082104 | 0.020655 | -0.082102 | -0.020653 | 1.8805e-06 | 1.1388e-06 | 0.12485 | 0.12485 | 0.12485 | 0.97881 | -0.40693 | 0.97878 | -0.40741 | 8.5746
89 | 0.074648 | 0.018785 | -0.074635 | -0.018777 | 1.2823e-05 | 7.6734e-06 | 0.11351 | 0.11351 | 0.11351 | 0.97878 | -0.40741 | 0.9786 | -0.411 | 7.7962
90 | 0.070806 | 0.017818 | -0.070787 | -0.017806 | 1.9225e-05 | 1.1415e-05 | 0.10769 | 0.10769 | 0.10769 | 0.9786 | -0.411 | 0.97831 | -0.41668 | 7.3964
91 | -0.0020761 | -0.00051983 | 0.0020762 | 0.00051969 | 5.1155e-08 | -1.3548e-07 | 0.0031743 | 0.0031742 | 0.0031743 | 0.97317 | -0.51786 | 0.97319 | -0.51734 | 0.87206
92 | -0.0033574 | -0.00084079 | 0.0033577 | 0.00084058 | 3.3256e-07 | -2.054e-07 | 0.0051332 | 0.005133 | 0.0051332 | 0.97319 | -0.51734 | 0.9733 | -0.51526 | 1.4102
93 | -0.0045171 | -0.0011312 | 0.0045173 | 0.0011311 | 2.4725e-07 | -1.3604e-08 | 0.0069056 | 0.0069055 | 0.0069056 | 0.9733 | -0.51526 | 0.97335 | -0.51411 | 1.8971
94 | 0.008169 | 0.0020475 | -0.0081685 | -0.0020472 | 5.1653e-07 | 2.2081e-07 | 0.012488 | 0.012488 | 0.012488 | 0.97335 | -0.51411 | 0.97329 | -0.51543 | 3.4309
95 | 0.0071442 | 0.0017905 | -0.0071436 | -0.0017903 | 5.4668e-07 | 1.9802e-07 | 0.010922 | 0.010922 | 0.010922 | 0.97329 | -0.51543 | 0.97321 | -0.51704 | 3.0007
96 | 0.053884 | 0.013553 | -0.053879 | -0.013551 | 4.1081e-06 | 2.3029e-06 | 0.082048 | 0.082048 | 0.082048 | 0.97744 | -0.43377 | 0.97736 | -0.43537 | 5.6352
97 | -0.057721 | -0.014515 | 0.057739 | 0.014526 | 1.8483e-05 | 1.0549e-05 | 0.087889 | 0.087889 | 0.087889 | 0.97744 | -0.43377 | 0.97778 | -0.42707 | 6.0364
98 | 0.049939 | 0.012563 | -0.04993 | -0.012559 | 8.8561e-06 | 4.8493e-06 | 0.076048 | 0.076049 | 0.076049 | 0.97736 | -0.43537 | 0.97717 | -0.43908 | 5.2231
99 | -0.061446 | -0.015455 | 0.061453 | 0.015459 | 6.9762e-06 | 4.0379e-06 | 0.09353 | 0.09353 | 0.09353 | 0.97778 | -0.42707 | 0.9779 | -0.4247 | 6.4238
100 | 0.046832 | 0.011782 | -0.046805 | -0.011766 | 2.6234e-05 | 1.6101e-05 | 0.071331 | 0.071331 | 0.071331 | 0.97717 | -0.43908 | 0.97657 | -0.45081 | 9.7982
101 | -0.064251 | -0.01616 | 0.064269 | 0.016171 | 1.8489e-05 | 1.0797e-05 | 0.097787 | 0.097787 | 0.097787 | 0.9779 | -0.4247 | 0.97821 | -0.41867 | 6.7162
102 | 0.04387 | 0.01103 | -0.04384 | -0.011011 | 2.9841e-05 | 1.8876e-05 | 0.066858 | 0.066858 | 0.066858 | 0.97657 | -0.45081 | 0.97584 | -0.46507 | 18.3675
103 | -0.068254 | -0.017169 | 0.06826 | 0.017173 | 6.4888e-06 | 3.8305e-06 | 0.10385 | 0.10385 | 0.10385 | 0.97821 | -0.41867 | 0.97831 | -0.41668 | 7.1324
104 | 0.03908 | 0.0098186 | -0.039069 | -0.0098113 | 1.1619e-05 | 7.3274e-06 | 0.0596 | 0.0596 | 0.0596 | 0.97584 | -0.46507 | 0.97553 | -0.4713 | 16.3737
105 | -0.0061709 | -0.0015465 | 0.0061713 | 0.0015466 | 3.5467e-07 | 9.5001e-08 | 0.0094358 | 0.0094357 | 0.0094358 | 0.97315 | -0.51825 | 0.97321 | -0.51704 | 2.5923
106 | 0.0026144 | 0.00065518 | -0.0026143 | -0.00065521 | 2.5931e-08 | -3.7165e-08 | 0.0039976 | 0.0039976 | 0.0039976 | 0.97315 | -0.51825 | 0.97313 | -0.51846 | 1.0982
107 | 0.035543 | 0.0089276 | -0.035514 | -0.0089098 | 2.8294e-05 | 1.7788e-05 | 0.054222 | 0.054222 | 0.054222 | 0.97553 | -0.4713 | 0.97468 | -0.488 | 14.8962
108 | 0.0311 | 0.0078033 | -0.031088 | -0.0077961 | 1.1579e-05 | 7.2397e-06 | 0.047482 | 0.047482 | 0.047482 | 0.97468 | -0.488 | 0.97428 | -0.49581 | 13.0446
109 | 0.0064468 | 0.0016155 | -0.0064463 | -0.0016153 | 4.7004e-07 | 1.3978e-07 | 0.0098454 | 0.0098454 | 0.0098454 | 0.97435 | -0.49377 | 0.97427 | -0.4953 | 2.7048
110 | 0.0044129 | 0.0011047 | -0.0044119 | -0.0011048 | 9.8117e-07 | -1.1878e-07 | 0.0066716 | 0.0066719 | 0.0066719 | 0.98416 | -0.30246 | 0.98392 | -0.30713 | 1.8329
111 | 0.02322 | 0.005827 | -0.023212 | -0.0058221 | 7.9906e-06 | 4.8961e-06 | 0.035179 | 0.035179 | 0.035179 | 0.98225 | -0.33957 | 0.98188 | -0.34679 | 9.6645
112 | 0.0097782 | 0.0024509 | -0.0097757 | -0.0024497 | 2.4404e-06 | 1.1866e-06 | 0.014813 | 0.014813 | 0.014813 | 0.98225 | -0.33957 | 0.98198 | -0.34481 | 4.0696
113 | 0.0083497 | 0.0020926 | -0.0083491 | -0.0020923 | 5.6071e-07 | 2.4045e-07 | 0.012646 | 0.012646 | 0.012646 | 0.98251 | -0.33454 | 0.98244 | -0.33595 | 3.4741
114 | 0.0014149 | 0.00035367 | -0.0014148 | -0.00035457 | 1.3387e-07 | -9.0461e-07 | 0.0021395 | 0.0021398 | 0.0021398 | 0.98392 | -0.30713 | 0.98382 | -0.30912 | 0.58787
115 | 0.020334 | 0.0051007 | -0.020333 | -0.0051006 | 1.7704e-07 | 1.0702e-07 | 0.030817 | 0.030817 | 0.030817 | 0.98188 | -0.34679 | 0.98187 | -0.34698 | 8.4661
116 | 0.0071718 | 0.0017971 | -0.0071713 | -0.0017969 | 4.9848e-07 | 1.7665e-07 | 0.010867 | 0.010868 | 0.010868 | 0.98198 | -0.34481 | 0.98191 | -0.34627 | 2.9856
117 | 0.0060672 | 0.0015204 | -0.0060667 | -0.0015203 | 5.1165e-07 | 1.2289e-07 | 0.0091894 | 0.0091895 | 0.0091895 | 0.98244 | -0.33595 | 0.98235 | -0.33772 | 2.5246
118 | -0.0011735 | -0.00029412 | 0.0011735 | 0.00029399 | 1.298e-08 | -1.2946e-07 | 0.0017806 | 0.0017805 | 0.0017806 | 0.98072 | -0.36963 | 0.98073 | -0.3694 | 0.48917
119 | -0.0083369 | -0.0020892 | 0.0083378 | 0.0020896 | 8.9254e-07 | 3.835e-07 | 0.012649 | 0.012649 | 0.012649 | 0.98073 | -0.3694 | 0.98084 | -0.36715 | 3.4751
120 | 0.0071634 | 0.0017952 | -0.0071625 | -0.0017949 | 8.4425e-07 | 2.9986e-07 | 0.010869 | 0.010869 | 0.010869 | 0.98073 | -0.3694 | 0.9806 | -0.37188 | 2.9859
121 | -0.011393 | -0.0028552 | 0.011398 | 0.002858 | 5.3012e-06 | 2.7951e-06 | 0.017284 | 0.017283 | 0.017284 | 0.98084 | -0.36715 | 0.98134 | -0.35739 | 4.7482
122 | 0.0041818 | 0.0010479 | -0.0041814 | -0.001048 | 3.5362e-07 | -6.9085e-08 | 0.0063456 | 0.0063457 | 0.0063457 | 0.9806 | -0.37188 | 0.98051 | -0.37365 | 1.7433
123 | -0.014286 | -0.0035818 | 0.014286 | 0.0035819 | 2.2947e-07 | 1.3039e-07 | 0.021662 | 0.021662 | 0.021662 | 0.98134 | -0.35739 | 0.98136 | -0.35705 | 5.9512
124 | -0.018541 | -0.0046482 | 0.01855 | 0.0046535 | 8.9075e-06 | 5.3209e-06 | 0.028113 | 0.028113 | 0.028113 | 0.98136 | -0.35705 | 0.98187 | -0.34698 | 7.7234
125 | 0.0046516 | 0.0011654 | -0.0046511 | -0.0011654 | 4.805e-07 | -1.8616e-08 | 0.007049 | 0.0070492 | 0.0070492 | 0.98191 | -0.34627 | 0.9818 | -0.34844 | 1.9366
126 | 0.0025347 | 0.00063522 | -0.0025347 | -0.00063526 | 2.1462e-08 | -3.5306e-08 | 0.0038416 | 0.0038416 | 0.0038416 | 0.9818 | -0.34844 | 0.98179 | -0.34862 | 1.0554
127 | 0.0021164 | 0.00053022 | -0.0021163 | -0.0005304 | 7.0899e-08 | -1.87e-07 | 0.0032076 | 0.0032076 | 0.0032076 | 0.9818 | -0.34844 | 0.98176 | -0.34915 | 0.88122
128 | -0.0021058 | -0.00052777 | 0.0021058 | 0.00052777 | 1.2414e-09 | -3.3215e-09 | 0.0031901 | 0.0031901 | 0.0031901 | 0.98227 | -0.33922 | 0.98227 | -0.33921 | 0.87639
129 | -0.0039938 | -0.0010009 | 0.003994 | 0.0010008 | 2.8188e-07 | -7.9573e-08 | 0.00605 | 0.0060499 | 0.00605 | 0.98227 | -0.33921 | 0.98235 | -0.33772 | 1.6621
130 | -0.0027661 | -0.00069324 | 0.0027662 | 0.00069315 | 6.934e-08 | -8.4567e-08 | 0.0042253 | 0.0042253 | 0.0042253 | 0.97414 | -0.49799 | 0.97417 | -0.49746 | 1.1608
131 | 0.00067413 | 0.00016893 | -0.00067413 | -0.00016895 | 6.4474e-10 | -1.9774e-08 | 0.0010297 | 0.0010297 | 0.0010297 | 0.97414 | -0.49799 | 0.97414 | -0.49801 | 0.2829
132 | -0.0032526 | -0.00081505 | 0.0032527 | 0.00081497 | 1.2499e-07 | -8.8133e-08 | 0.0049682 | 0.0049682 | 0.0049682 | 0.97417 | -0.49746 | 0.97421 | -0.49665 | 1.3649
133 | -0.0037495 | -0.00093948 | 0.0037496 | 0.00093947 | 2.8324e-08 | -1.0547e-08 | 0.005727 | 0.005727 | 0.005727 | 0.97421 | -0.49665 | 0.97421 | -0.49649 | 1.5733
134 | -0.0057965 | -0.0014525 | 0.0057968 | 0.0014525 | 3.2969e-07 | 7.1334e-08 | 0.0088535 | 0.0088534 | 0.0088535 | 0.97421 | -0.49649 | 0.97427 | -0.4953 | 2.4323

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46697 | 0.11983

## res_load
| p_mw | q_mvar
0 | 0.015538 | 0.0038943
1 | 0.01699 | 0.0042582
2 | 0.0064799 | 0.001624
3 | 0.0028065 | 0.00070338
4 | 0.016266 | 0.0040766
5 | 0.0039415 | 0.00098784
6 | 0.0031358 | 0.0007859
7 | 0.0032207 | 0.00080718
8 | 0.0047977 | 0.0012024
9 | 0.0036443 | 0.00091334
10 | 0.0039709 | 0.00099519
11 | 0.0031382 | 0.0007865
12 | 0.0042674 | 0.0010695
13 | 0.0013056 | 0.00032722
14 | 0.0033793 | 0.00084693
15 | 0.0042016 | 0.001053
16 | 0.0027226 | 0.00068234
17 | 0.0035384 | 0.00088681
18 | 0.0033168 | 0.00083126
19 | 0.0023895 | 0.00059885
20 | 0.0031999 | 0.00080198
21 | 0.005838 | 0.0014632
22 | 0.002138 | 0.00053584
23 | 0.0036883 | 0.00092438
24 | 0.0059268 | 0.0014854
25 | 0.0034295 | 0.00085951
26 | 0.0019188 | 0.0004809
27 | 0.0020163 | 0.00050534
28 | 0.0013118 | 0.00032877
29 | 0.0050662 | 0.0012697
30 | 0.0038293 | 0.0009597
31 | 0.0048316 | 0.0012109
32 | 0.003795 | 0.00095112
33 | 0.0046747 | 0.0011716
34 | 0.0011198 | 0.00028064
35 | 0.0019648 | 0.00049243
36 | 0.0051989 | 0.001303
37 | 0.0039978 | 0.0010019
38 | 0.00094458 | 0.00023674
39 | 0.0036609 | 0.00091752
40 | 0.00093951 | 0.00023546
41 | 0.0012863 | 0.00032239
42 | 0.0060294 | 0.0015111
43 | 0.0029468 | 0.00073855
44 | 0.0034248 | 0.00085835
45 | 0.0047837 | 0.0011989
46 | 0.0047367 | 0.0011871
47 | 0.0059265 | 0.0014853
48 | 0.0018167 | 0.00045532
49 | 0.0012379 | 0.00031023
50 | 0.0025592 | 0.00064139
51 | 0.001571 | 0.00039374
52 | 0.0018866 | 0.00047282
53 | 0.0020378 | 0.00051071
54 | 0.0024049 | 0.00060272
55 | 0.0021031 | 0.00052709
56 | 0.0032517 | 0.00081495
57 | 0.0059268 | 0.0014854
58 | 0.0068687 | 0.0017215
59 | 0.021546 | 0.0054
60 | 0.023115 | 0.0057932
61 | 0.0061371 | 0.0015381
62 | 0.0065677 | 0.001646
63 | 0.0053032 | 0.0013291
64 | 0.0059241 | 0.0014847
65 | 0.020123 | 0.0050432
66 | 0.0074546 | 0.0018683
67 | 0.0038286 | 0.00095955
68 | 0.0011366 | 0.00028485
69 | 0.0012812 | 0.0003211
70 | 0.0011594 | 0.00029058
71 | 0.0010243 | 0.00025672
72 | 0.003837 | 0.00096163
73 | 0.0039408 | 0.00098766
74 | 0.0037068 | 0.00092902
75 | 0.0030983 | 0.0007765
76 | 0.002798 | 0.00070124
77 | 0.0029357 | 0.00073577
78 | 0.0039843 | 0.00099856
79 | 0.0047594 | 0.0011928
80 | 0.002527 | 0.00063333
81 | 0.0035565 | 0.00089135
82 | 0.00097234 | 0.00024369
83 | 0.0026143 | 0.00065521
84 | 0.0035259 | 0.00088367
85 | 0.0044148 | 0.0011064
86 | 0.0045804 | 0.001148
87 | 0.00058334 | 0.0001462
88 | 0.0031644 | 0.00079306
89 | 0.0019861 | 0.00049778
90 | 0.002997 | 0.00075111
91 | 0.0028783 | 0.00072136
92 | 0.0026039 | 0.00065259
93 | 0.0022819 | 0.0005719
94 | 0.0011735 | 0.00029412
95 | 0.0030548 | 0.00076561
96 | 0.0029808 | 0.00074705
97 | 0.002888 | 0.00072379
98 | 0.0041814 | 0.001048
99 | 0.0042545 | 0.0010663
100 | 0.001784 | 0.0004471
101 | 0.0014148 | 0.00035457
102 | 0.0038249 | 0.00095862
103 | 0.0025197 | 0.00063151
104 | 0.0025347 | 0.00063526
105 | 0.0021163 | 0.0005304
106 | 0.0021058 | 0.00052777
107 | 0.0018879 | 0.00047316
108 | 0.0020726 | 0.00051945
109 | 0.002092 | 0.0005243
110 | 0.0004864 | 0.0001219
111 | 0.00067413 | 0.00016895
112 | 0.00049681 | 0.00012451
113 | 0.0020469 | 0.00051301
114 | 0.00064953 | 0.00016279

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1