## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2125-43_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2125-43_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2125-43_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2125-43_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2125-43_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2125-43_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_2125-43_0_5_node_47 | 0.4 | n |  | TRUE
7 | bus_LV_2125-43_0_5_node_12 | 0.4 | n |  | TRUE
8 | bus_LV_2125-43_0_5_node_132 | 0.4 | n |  | TRUE
9 | bus_LV_2125-43_0_5_node_13 | 0.4 | n |  | TRUE
10 | bus_LV_2125-43_0_5_node_130 | 0.4 | n |  | TRUE
11 | bus_LV_2125-43_0_5_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_2125-43_0_5_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_2125-43_0_5_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_2125-43_0_5_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_2125-43_0_5_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_2125-43_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_2125-43_0_5_node_30 | 0.4 | n |  | TRUE
18 | bus_LV_2125-43_0_5_node_29 | 0.4 | n |  | TRUE
19 | bus_LV_2125-43_0_5_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_2125-43_0_5_node_74 | 0.4 | n |  | TRUE
21 | bus_LV_2125-43_0_5_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_2125-43_0_5_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_2125-43_0_5_node_41 | 0.4 | n |  | TRUE
24 | bus_LV_2125-43_0_5_node_72 | 0.4 | n |  | TRUE
25 | bus_LV_2125-43_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2125-43_0_5_node_24 | 0.4 | n |  | TRUE
27 | bus_LV_2125-43_0_5_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2125-43_0_5_node_26 | 0.4 | n |  | TRUE
29 | bus_LV_2125-43_0_5_node_15 | 0.4 | n |  | TRUE
30 | bus_LV_2125-43_0_5_node_17 | 0.4 | n |  | TRUE
31 | bus_LV_2125-43_0_5_node_18 | 0.4 | n |  | TRUE
32 | bus_LV_2125-43_0_5_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_2125-43_0_5_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_2125-43_0_5_node_19 | 0.4 | n |  | TRUE
35 | bus_LV_2125-43_0_5_node_20 | 0.4 | n |  | TRUE
36 | bus_LV_2125-43_0_5_node_21 | 0.4 | n |  | TRUE
37 | bus_LV_2125-43_0_5_node_23 | 0.4 | n |  | TRUE
38 | bus_LV_2125-43_0_5_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_2125-43_0_5_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_2125-43_0_5_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_2125-43_0_5_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_2125-43_0_5_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_2125-43_0_5_node_131 | 0.4 | n |  | TRUE
44 | bus_LV_2125-43_0_5_node_37 | 0.4 | n |  | TRUE
45 | bus_LV_2125-43_0_5_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_2125-43_0_5_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_2125-43_0_5_node_42 | 0.4 | n |  | TRUE
48 | bus_LV_2125-43_0_5_node_65 | 0.4 | n |  | TRUE
49 | bus_LV_2125-43_0_5_node_73 | 0.4 | n |  | TRUE
50 | bus_LV_2125-43_0_5_node_64 | 0.4 | n |  | TRUE
51 | bus_LV_2125-43_0_5_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_2125-43_0_5_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_2125-43_0_5_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_2125-43_0_5_node_50 | 0.4 | n |  | TRUE
55 | bus_LV_2125-43_0_5_node_51 | 0.4 | n |  | TRUE
56 | bus_LV_2125-43_0_5_node_59 | 0.4 | n |  | TRUE
57 | bus_LV_2125-43_0_5_node_57 | 0.4 | n |  | TRUE
58 | bus_LV_2125-43_0_5_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_2125-43_0_5_node_53 | 0.4 | n |  | TRUE
60 | bus_LV_2125-43_0_5_node_54 | 0.4 | n |  | TRUE
61 | bus_LV_2125-43_0_5_node_55 | 0.4 | n |  | TRUE
62 | bus_LV_2125-43_0_5_node_56 | 0.4 | n |  | TRUE
63 | bus_LV_2125-43_0_5_node_105 | 0.4 | n |  | TRUE
64 | bus_LV_2125-43_0_5_node_106 | 0.4 | n |  | TRUE
65 | bus_LV_2125-43_0_5_node_71 | 0.4 | n |  | TRUE
66 | bus_LV_2125-43_0_5_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_2125-43_0_5_node_61 | 0.4 | n |  | TRUE
68 | bus_LV_2125-43_0_5_node_62 | 0.4 | n |  | TRUE
69 | bus_LV_2125-43_0_5_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_2125-43_0_5_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_2125-43_0_5_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_2125-43_0_5_node_70 | 0.4 | n |  | TRUE
73 | bus_LV_2125-43_0_5_node_128 | 0.4 | n |  | TRUE
74 | bus_LV_2125-43_0_5_node_68 | 0.4 | n |  | TRUE
75 | bus_LV_2125-43_0_5_node_129 | 0.4 | n |  | TRUE
76 | bus_LV_2125-43_0_5_node_95 | 0.4 | n |  | TRUE
77 | bus_LV_2125-43_0_5_node_66 | 0.4 | n |  | TRUE
78 | bus_LV_2125-43_0_5_node_67 | 0.4 | n |  | TRUE
79 | bus_LV_2125-43_0_5_node_80 | 0.4 | n |  | TRUE
80 | bus_LV_2125-43_0_5_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_2125-43_0_5_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_2125-43_0_5_node_78 | 0.4 | n |  | TRUE
83 | bus_LV_2125-43_0_5_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_2125-43_0_5_node_110 | 0.4 | n |  | TRUE
85 | bus_LV_2125-43_0_5_node_122 | 0.4 | n |  | TRUE
86 | bus_LV_2125-43_0_5_node_120 | 0.4 | n |  | TRUE
87 | bus_LV_2125-43_0_5_node_93 | 0.4 | n |  | TRUE
88 | bus_LV_2125-43_0_5_node_92 | 0.4 | n |  | TRUE
89 | bus_LV_2125-43_0_5_node_116 | 0.4 | n |  | TRUE
90 | bus_LV_2125-43_0_5_node_109 | 0.4 | n |  | TRUE
91 | bus_LV_2125-43_0_5_node_123 | 0.4 | n |  | TRUE
92 | bus_LV_2125-43_0_5_node_119 | 0.4 | n |  | TRUE
93 | bus_LV_2125-43_0_5_node_81 | 0.4 | n |  | TRUE
94 | bus_LV_2125-43_0_5_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_2125-43_0_5_node_83 | 0.4 | n |  | TRUE
96 | bus_LV_2125-43_0_5_node_84 | 0.4 | n |  | TRUE
97 | bus_LV_2125-43_0_5_node_85 | 0.4 | n |  | TRUE
98 | bus_LV_2125-43_0_5_node_117 | 0.4 | n |  | TRUE
99 | bus_LV_2125-43_0_5_node_118 | 0.4 | n |  | TRUE
100 | bus_LV_2125-43_0_5_node_115 | 0.4 | n |  | TRUE
101 | bus_LV_2125-43_0_5_node_86 | 0.4 | n |  | TRUE
102 | bus_LV_2125-43_0_5_node_87 | 0.4 | n |  | TRUE
103 | bus_LV_2125-43_0_5_node_88 | 0.4 | n |  | TRUE
104 | bus_LV_2125-43_0_5_node_89 | 0.4 | n |  | TRUE
105 | bus_LV_2125-43_0_5_node_90 | 0.4 | n |  | TRUE
106 | bus_LV_2125-43_0_5_node_91 | 0.4 | n |  | TRUE
107 | bus_LV_2125-43_0_5_node_103 | 0.4 | n |  | TRUE
108 | bus_LV_2125-43_0_5_node_97 | 0.4 | n |  | TRUE
109 | bus_LV_2125-43_0_5_node_108 | 0.4 | n |  | TRUE
110 | bus_LV_2125-43_0_5_node_104 | 0.4 | n |  | TRUE
111 | bus_LV_2125-43_0_5_node_98 | 0.4 | n |  | TRUE
112 | bus_LV_2125-43_0_5_node_94 | 0.4 | n |  | TRUE
113 | bus_LV_2125-43_0_5_node_96 | 0.4 | n |  | TRUE
114 | bus_LV_2125-43_0_5_node_102 | 0.4 | n |  | TRUE
115 | bus_LV_2125-43_0_5_node_100 | 0.4 | n |  | TRUE
116 | bus_LV_2125-43_0_5_node_125 | 0.4 | n |  | TRUE
117 | bus_LV_2125-43_0_5_node_124 | 0.4 | n |  | TRUE
118 | bus_LV_2125-43_0_5_node_126 | 0.4 | n |  | TRUE
119 | bus_LV_2125-43_0_5_node_101 | 0.4 | n |  | TRUE
120 | bus_LV_2125-43_0_5_node_99 | 0.4 | n |  | TRUE
121 | bus_LV_2125-43_0_5_node_127 | 0.4 | n |  | TRUE
122 | bus_LV_2125-43_0_5_node_107 | 0.4 | n |  | TRUE
123 | bus_LV_2125-43_0_5_node_113 | 0.4 | n |  | TRUE
124 | bus_LV_2125-43_0_5_node_111 | 0.4 | n |  | TRUE
125 | bus_LV_2125-43_0_5_node_112 | 0.4 | n |  | TRUE
126 | bus_LV_2125-43_0_5_node_114 | 0.4 | n |  | TRUE
127 | bus_LV_2125-43_0_5_node_121 | 0.4 | n |  | TRUE
128 | bus_MV_30_0_node_68 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2125-43_0_5_load_0 | 0 | 0.040871 | 0.010243 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2125-43_0_5_load_4 | 4 | 0.017364 | 0.0043517 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2125-43_0_5_load_47 | 6 | 0.0030926 | 0.00077507 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2125-43_0_5_load_12 | 7 | 0.038655 | 0.0096879 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2125-43_0_5_load_132 | 8 | 0.030056 | 0.0075327 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2125-43_0_5_load_13 | 9 | 0.009779 | 0.0024508 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2125-43_0_5_load_130 | 10 | 0.0017544 | 0.0004397 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2125-43_0_5_load_6 | 11 | 0.0044628 | 0.0011185 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2125-43_0_5_load_7 | 12 | 0.0051745 | 0.0012969 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2125-43_0_5_load_9 | 14 | 0.0049854 | 0.0012495 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2125-43_0_5_load_10 | 15 | 0.0026348 | 0.00066035 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2125-43_0_5_load_11 | 16 | 0.0016123 | 0.00040407 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2125-43_0_5_load_30 | 17 | 0.0058571 | 0.0014679 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2125-43_0_5_load_29 | 18 | 0.010348 | 0.0025935 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2125-43_0_5_load_40 | 19 | 0.0032306 | 0.00080966 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2125-43_0_5_load_74 | 20 | 0.0043124 | 0.0010808 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2125-43_0_5_load_31 | 21 | 0.0051968 | 0.0013024 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2125-43_0_5_load_22 | 22 | 0.0071078 | 0.0017814 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2125-43_0_5_load_41 | 23 | 0.0019273 | 0.00048303 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2125-43_0_5_load_72 | 24 | 0.0056437 | 0.0014144 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2125-43_0_5_load_24 | 26 | 0.0060146 | 0.0015074 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2125-43_0_5_load_16 | 27 | 0.011027 | 0.0027637 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2125-43_0_5_load_26 | 28 | 0.0059458 | 0.0014901 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2125-43_0_5_load_15 | 29 | 0.0091957 | 0.0023047 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2125-43_0_5_load_17 | 30 | 0.0033555 | 0.00084098 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2125-43_0_5_load_18 | 31 | 0.025095 | 0.0062894 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2125-43_0_5_load_32 | 33 | 0.0013194 | 0.00033067 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2125-43_0_5_load_19 | 34 | 0.005425 | 0.0013596 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2125-43_0_5_load_20 | 35 | 0.014622 | 0.0036646 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2125-43_0_5_load_21 | 36 | 0.0037473 | 0.00093917 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2125-43_0_5_load_23 | 37 | 0.0036151 | 0.00090602 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2125-43_0_5_load_25 | 38 | 0.0050121 | 0.0012562 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2125-43_0_5_load_38 | 39 | 0.0031486 | 0.00078911 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2125-43_0_5_load_36 | 40 | 0.003097 | 0.00077619 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2125-43_0_5_load_33 | 41 | 0.004643 | 0.0011636 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2125-43_0_5_load_35 | 42 | 0.0032521 | 0.00081505 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2125-43_0_5_load_131 | 43 | 0.01181 | 0.00296 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2125-43_0_5_load_37 | 44 | 0.011705 | 0.0029336 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2125-43_0_5_load_39 | 45 | 0.0027579 | 0.00069119 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2125-43_0_5_load_43 | 46 | 0.0042214 | 0.001058 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2125-43_0_5_load_42 | 47 | 0.0018913 | 0.00047401 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2125-43_0_5_load_65 | 48 | 0.0032718 | 0.00081999 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2125-43_0_5_load_44 | 51 | 0.0010209 | 0.00025585 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2125-43_0_5_load_48 | 52 | 0.005545 | 0.0013897 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2125-43_0_5_load_49 | 53 | 0.0050423 | 0.0012637 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2125-43_0_5_load_50 | 54 | 0.0030583 | 0.00076648 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2125-43_0_5_load_51 | 55 | 0.0039771 | 0.00099676 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2125-43_0_5_load_59 | 56 | 0.0028511 | 0.00071454 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2125-43_0_5_load_57 | 57 | 0.0044118 | 0.0011057 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2125-43_0_5_load_52 | 58 | 0.0033364 | 0.00083619 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2125-43_0_5_load_53 | 59 | 0.0033774 | 0.00084644 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2125-43_0_5_load_54 | 60 | 0.0032225 | 0.00080763 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2125-43_0_5_load_55 | 61 | 0.0032273 | 0.00080883 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2125-43_0_5_load_56 | 62 | 0.0033353 | 0.0008359 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2125-43_0_5_load_105 | 63 | 0.0058111 | 0.0014564 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2125-43_0_5_load_106 | 64 | 0.0042862 | 0.0010742 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2125-43_0_5_load_71 | 65 | 0.0054725 | 0.0013715 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2125-43_0_5_load_63 | 66 | 0.0047237 | 0.0011839 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2125-43_0_5_load_61 | 67 | 0.0044603 | 0.0011178 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2125-43_0_5_load_62 | 68 | 0.0038868 | 0.00097414 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2125-43_0_5_load_58 | 69 | 0.0040206 | 0.0010077 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2125-43_0_5_load_75 | 71 | 0.0038292 | 0.0009597 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2125-43_0_5_load_128 | 73 | 0.003015 | 0.00075563 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2125-43_0_5_load_68 | 74 | 0.0036084 | 0.00090435 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2125-43_0_5_load_129 | 75 | 0.0041147 | 0.0010312 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2125-43_0_5_load_95 | 76 | 0.002786 | 0.00069823 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2125-43_0_5_load_66 | 77 | 0.0038971 | 0.00097671 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2125-43_0_5_load_67 | 78 | 0.0051598 | 0.0012932 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2125-43_0_5_load_76 | 80 | 0.0029204 | 0.00073191 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2125-43_0_5_load_78 | 82 | 0.0018099 | 0.0004536 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2125-43_0_5_load_122 | 85 | 0.0022167 | 0.00055557 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2125-43_0_5_load_120 | 86 | 0.003204 | 0.00080299 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2125-43_0_5_load_93 | 87 | 0.0014324 | 0.00035899 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2125-43_0_5_load_92 | 88 | 0.0022191 | 0.00055615 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2125-43_0_5_load_116 | 89 | 0.0010372 | 0.00025995 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2125-43_0_5_load_109 | 90 | 0.0016534 | 0.00041439 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2125-43_0_5_load_123 | 91 | 0.0033546 | 0.00084074 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2125-43_0_5_load_119 | 92 | 0.0036271 | 0.00090903 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2125-43_0_5_load_81 | 93 | 0.0027661 | 0.00069325 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2125-43_0_5_load_82 | 94 | 0.0032502 | 0.00081457 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2125-43_0_5_load_83 | 95 | 0.0028844 | 0.0007229 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2125-43_0_5_load_84 | 96 | 0.0033292 | 0.00083436 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2125-43_0_5_load_85 | 97 | 0.002702 | 0.00067719 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2125-43_0_5_load_118 | 99 | 0.0026182 | 0.00065619 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2125-43_0_5_load_115 | 100 | 0.0029984 | 0.00075147 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2125-43_0_5_load_86 | 101 | 0.0046243 | 0.001159 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2125-43_0_5_load_87 | 102 | 0.0037881 | 0.0009494 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2125-43_0_5_load_89 | 104 | 0.0028379 | 0.00071126 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2125-43_0_5_load_90 | 105 | 0.0040103 | 0.0010051 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2125-43_0_5_load_91 | 106 | 0.0030937 | 0.00077535 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2125-43_0_5_load_103 | 107 | 0.0045603 | 0.0011429 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2125-43_0_5_load_97 | 108 | 0.004451 | 0.0011155 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2125-43_0_5_load_108 | 109 | 0.0044031 | 0.0011035 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2125-43_0_5_load_104 | 110 | 0.005103 | 0.0012789 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2125-43_0_5_load_98 | 111 | 0.0013248 | 0.00033203 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2125-43_0_5_load_94 | 112 | 0.0037813 | 0.00094769 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2125-43_0_5_load_102 | 114 | 0.0033553 | 0.00084091 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2125-43_0_5_load_100 | 115 | 0.0024938 | 0.000625 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2125-43_0_5_load_125 | 116 | 0.0030769 | 0.00077113 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2125-43_0_5_load_124 | 117 | 0.0028233 | 0.0007076 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2125-43_0_5_load_126 | 118 | 0.0013584 | 0.00034045 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2125-43_0_5_load_101 | 119 | 0.0033456 | 0.00083849 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2125-43_0_5_load_99 | 120 | 0.0065539 | 0.0016426 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2125-43_0_5_load_127 | 121 | 0.0032776 | 0.00082144 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_2125-43_0_5_load_107 | 122 | 0.0031056 | 0.00077834 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_2125-43_0_5_load_113 | 123 | 0.003086 | 0.00077342 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_2125-43_0_5_load_111 | 124 | 0.0022091 | 0.00055366 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_2125-43_0_5_load_112 | 125 | 0.0030352 | 0.00076069 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_2125-43_0_5_load_114 | 126 | 0.0028548 | 0.00071548 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_2125-43_0_5_load_121 | 127 | 0.0038467 | 0.00096407 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 18 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2125-43_0_5_line_0 |  | 0 | 1 | 0.030544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2125-43_0_5_line_1 |  | 0 | 2 | 0.0050647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2125-43_0_5_line_2 |  | 1 | 3 | 0.006292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2125-43_0_5_line_3 |  | 1 | 4 | 0.062663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_2125-43_0_5_line_4 |  | 2 | 5 | 0.018347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2125-43_0_5_line_5 |  | 3 | 6 | 0.022861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2125-43_0_5_line_6 |  | 4 | 7 | 0.016267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2125-43_0_5_line_7 |  | 5 | 8 | 0.060111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2125-43_0_5_line_8 |  | 7 | 9 | 0.036939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2125-43_0_5_line_9 |  | 8 | 10 | 0.0015077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2125-43_0_5_line_10 |  | 9 | 25 | 0.030405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2125-43_0_5_line_11 |  | 10 | 43 | 0.014277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2125-43_0_5_line_12 |  | 11 | 12 | 0.01542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2125-43_0_5_line_13 |  | 11 | 13 | 0.046393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_2125-43_0_5_line_14 |  | 12 | 14 | 0.001832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_2125-43_0_5_line_15 |  | 13 | 15 | 0.020536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2125-43_0_5_line_16 |  | 13 | 16 | 0.013949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2125-43_0_5_line_17 |  | 14 | 17 | 0.020393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_2125-43_0_5_line_18 |  | 15 | 18 | 0.011318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
19 | LV_2125-43_0_5_line_19 |  | 16 | 19 | 0.0235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2125-43_0_5_line_20 |  | 16 | 20 | 0.093902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_2125-43_0_5_line_21 |  | 17 | 21 | 0.00094398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
22 | LV_2125-43_0_5_line_22 |  | 18 | 22 | 0.031272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2125-43_0_5_line_23 |  | 19 | 23 | 0.022509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2125-43_0_5_line_24 |  | 20 | 24 | 0.0091184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_2125-43_0_5_line_25 |  | 21 | 32 | 0.019187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_2125-43_0_5_line_26 |  | 22 | 35 | 0.0095351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2125-43_0_5_line_27 |  | 23 | 47 | 0.015684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2125-43_0_5_line_28 |  | 24 | 49 | 0.013514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_2125-43_0_5_line_29 |  | 25 | 26 | 0.007356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2125-43_0_5_line_30 |  | 25 | 27 | 0.013614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_2125-43_0_5_line_31 |  | 26 | 28 | 0.023089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2125-43_0_5_line_32 |  | 27 | 29 | 0.019395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
33 | LV_2125-43_0_5_line_33 |  | 29 | 30 | 0.019028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_2125-43_0_5_line_34 |  | 30 | 31 | 0.019564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_2125-43_0_5_line_35 |  | 31 | 32 | 0.0043038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
36 | LV_2125-43_0_5_line_36 |  | 32 | 33 | 0.032304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2125-43_0_5_line_37 |  | 33 | 39 | 0.010748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2125-43_0_5_line_38 |  | 34 | 35 | 0.025532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2125-43_0_5_line_39 |  | 34 | 36 | 0.0081539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2125-43_0_5_line_40 |  | 36 | 37 | 0.0013529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2125-43_0_5_line_41 |  | 37 | 38 | 0.013481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2125-43_0_5_line_42 |  | 39 | 40 | 0.022163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2125-43_0_5_line_43 |  | 40 | 44 | 0.019339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2125-43_0_5_line_44 |  | 41 | 42 | 0.032037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2125-43_0_5_line_45 |  | 42 | 43 | 0.10697 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2125-43_0_5_line_46 |  | 44 | 45 | 0.012447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2125-43_0_5_line_47 |  | 45 | 46 | 0.031176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2125-43_0_5_line_48 |  | 47 | 51 | 0.038631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2125-43_0_5_line_49 |  | 48 | 49 | 0.016571 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_2125-43_0_5_line_50 |  | 48 | 50 | 0.0085729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_2125-43_0_5_line_51 |  | 50 | 66 | 0.021433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_2125-43_0_5_line_52 |  | 52 | 53 | 0.024799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2125-43_0_5_line_53 |  | 52 | 54 | 0.025232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2125-43_0_5_line_54 |  | 54 | 55 | 0.0037776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2125-43_0_5_line_55 |  | 55 | 56 | 0.023312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2125-43_0_5_line_56 |  | 56 | 57 | 0.015681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2125-43_0_5_line_57 |  | 57 | 69 | 0.006022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2125-43_0_5_line_58 |  | 58 | 59 | 0.011773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_2125-43_0_5_line_59 |  | 58 | 60 | 0.0059534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_2125-43_0_5_line_60 |  | 59 | 61 | 0.0043824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_2125-43_0_5_line_61 |  | 60 | 62 | 0.0042377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_2125-43_0_5_line_62 |  | 61 | 66 | 0.0035843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
63 | LV_2125-43_0_5_line_63 |  | 62 | 67 | 0.0063486 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_2125-43_0_5_line_64 |  | 63 | 64 | 0.0057244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_2125-43_0_5_line_65 |  | 63 | 65 | 0.036421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_2125-43_0_5_line_66 |  | 64 | 122 | 0.022222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_2125-43_0_5_line_67 |  | 65 | 68 | 0.00038576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_2125-43_0_5_line_68 |  | 67 | 68 | 0.02199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_2125-43_0_5_line_69 |  | 69 | 70 | 0.034875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2125-43_0_5_line_70 |  | 70 | 71 | 0.026875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2125-43_0_5_line_71 |  | 70 | 72 | 0.061824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2125-43_0_5_line_72 |  | 71 | 73 | 0.020325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2125-43_0_5_line_73 |  | 72 | 74 | 0.016492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2125-43_0_5_line_74 |  | 73 | 79 | 0.015458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_2125-43_0_5_line_75 |  | 74 | 77 | 0.030183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2125-43_0_5_line_76 |  | 75 | 76 | 0.074411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2125-43_0_5_line_77 |  | 76 | 87 | 0.013987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2125-43_0_5_line_78 |  | 77 | 78 | 0.0041739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2125-43_0_5_line_79 |  | 79 | 86 | 0.020633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_2125-43_0_5_line_80 |  | 79 | 81 | 0.006406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_2125-43_0_5_line_81 |  | 80 | 81 | 0.015959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2125-43_0_5_line_82 |  | 80 | 82 | 0.013097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2125-43_0_5_line_83 |  | 81 | 83 | 0.042574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_2125-43_0_5_line_84 |  | 83 | 84 | 0.014569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_2125-43_0_5_line_85 |  | 83 | 85 | 0.013996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2125-43_0_5_line_86 |  | 84 | 89 | 0.014651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_2125-43_0_5_line_87 |  | 84 | 90 | 0.017515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_2125-43_0_5_line_88 |  | 85 | 91 | 0.01662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2125-43_0_5_line_89 |  | 86 | 92 | 0.0041691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
90 | LV_2125-43_0_5_line_90 |  | 87 | 88 | 0.020126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2125-43_0_5_line_91 |  | 88 | 91 | 0.049831 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2125-43_0_5_line_92 |  | 89 | 100 | 0.0091499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
93 | LV_2125-43_0_5_line_93 |  | 90 | 109 | 0.02168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
94 | LV_2125-43_0_5_line_94 |  | 92 | 127 | 0.030933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
95 | LV_2125-43_0_5_line_95 |  | 93 | 94 | 0.018251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2125-43_0_5_line_96 |  | 93 | 95 | 0.007504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2125-43_0_5_line_97 |  | 94 | 96 | 0.0018026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2125-43_0_5_line_98 |  | 95 | 97 | 0.016467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2125-43_0_5_line_99 |  | 96 | 98 | 0.027978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2125-43_0_5_line_100 |  | 98 | 99 | 0.015103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_2125-43_0_5_line_101 |  | 98 | 100 | 0.034978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
102 | LV_2125-43_0_5_line_102 |  | 99 | 117 | 0.016389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
103 | LV_2125-43_0_5_line_103 |  | 101 | 102 | 0.0079093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2125-43_0_5_line_104 |  | 101 | 103 | 0.021203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2125-43_0_5_line_105 |  | 102 | 104 | 0.014604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2125-43_0_5_line_106 |  | 103 | 105 | 0.029143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2125-43_0_5_line_107 |  | 103 | 106 | 0.0024411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2125-43_0_5_line_108 |  | 104 | 107 | 0.014525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2125-43_0_5_line_109 |  | 105 | 108 | 0.0075044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2125-43_0_5_line_110 |  | 106 | 109 | 0.042321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
111 | LV_2125-43_0_5_line_111 |  | 107 | 110 | 0.0079671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2125-43_0_5_line_112 |  | 108 | 111 | 0.01091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2125-43_0_5_line_113 |  | 111 | 120 | 0.0048044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2125-43_0_5_line_114 |  | 112 | 113 | 0.030927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2125-43_0_5_line_115 |  | 113 | 114 | 0.047783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2125-43_0_5_line_116 |  | 113 | 115 | 0.02625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2125-43_0_5_line_117 |  | 114 | 118 | 0.032369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2125-43_0_5_line_118 |  | 115 | 119 | 0.0075778 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2125-43_0_5_line_119 |  | 115 | 116 | 0.043862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2125-43_0_5_line_120 |  | 116 | 117 | 0.010036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2125-43_0_5_line_121 |  | 120 | 121 | 0.0076988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2125-43_0_5_line_122 |  | 122 | 123 | 0.012226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
123 | LV_2125-43_0_5_line_123 |  | 123 | 124 | 0.017331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
124 | LV_2125-43_0_5_line_124 |  | 124 | 125 | 0.0080438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_2125-43_0_5_line_125 |  | 125 | 126 | 0.024549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
126 | LV_2125-43_0_5_line_126 |  | 126 | 127 | 0.0022915 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2125-43_0_5_trafo_29 | 0.63 MVA 20/0.4 kV | 128 | 18 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2569759.1879 | 1162713.688 | 2569764.2639 | 1162714.6407 | 2569787.3583 | 1162725.164
1 | 2569791.6397 | 1162727.8649 | 2569787.5973 | 1162725.2729 | 2569787.3583 | 1162725.164
2 | 2569753.3629 | 1162716.1075 | 2569759.1879 | 1162713.688
3 | 2569759.1879 | 1162713.688 | 2569777.6446 | 1162673.2522 | 2569784.3126 | 1162656.3027
4 | 2569791.6397 | 1162727.8649 | 2569791.2296 | 1162733.1364 | 2569785.8431 | 1162745.0362
5 | 2569753.3629 | 1162716.1075 | 2569754.1201 | 1162721.9289 | 2569743.9098 | 1162735.5099
6 | 2569789.8055 | 1162641.017 | 2569788.9065 | 1162644.6254 | 2569784.3126 | 1162656.3027
7 | 2569785.8431 | 1162745.0362 | 2569781.0282 | 1162756.344 | 2569785.8573 | 1162764.546 | 2569798.5052 | 1162772.2973 | 2569820.0144 | 1162781.685
8 | 2569789.8055 | 1162641.017 | 2569798.7356 | 1162605.1739
9 | 2569821.3962 | 1162782.2881 | 2569820.0144 | 1162781.685
10 | 2569806.0861 | 1162575.6705 | 2569798.7356 | 1162605.1739
11 | 2569821.3962 | 1162782.2881 | 2569830.7108 | 1162786.3534 | 2569834.5969 | 1162787.7029
12 | 2569896.1854 | 1162540.2432 | 2569891.6926 | 1162554.9939
13 | 2569909.7076 | 1162495.8645 | 2569906.1806 | 1162507.4437 | 2569897.9283 | 1162534.5211 | 2569896.1854 | 1162540.2432
14 | 2569891.1588 | 1162556.7464 | 2569891.6926 | 1162554.9939
15 | 2569909.7076 | 1162495.8645 | 2569889.4925 | 1162492.2476
16 | 2569909.7076 | 1162495.8645 | 2569923.2243 | 1162499.3108
17 | 2569891.1588 | 1162556.7464 | 2569885.217 | 1162576.2546
18 | 2569889.4925 | 1162492.2476 | 2569878.3512 | 1162490.2541
19 | 2569945.9957 | 1162505.1166 | 2569923.2243 | 1162499.3108
20 | 2569923.2243 | 1162499.3108 | 2569952.5524 | 1162410.1061
21 | 2569885.217 | 1162576.2546 | 2569884.9419 | 1162577.1577
22 | 2569847.2715 | 1162490.7718 | 2569870.8486 | 1162488.9117 | 2569878.3512 | 1162490.2541
23 | 2569945.9957 | 1162505.1166 | 2569967.8067 | 1162510.6776
24 | 2569952.5524 | 1162410.1061 | 2569961.3971 | 1162412.3236
25 | 2569879.3516 | 1162595.512 | 2569884.9419 | 1162577.1577
26 | 2569837.7659 | 1162491.5217 | 2569847.2715 | 1162490.7718
27 | 2569967.8067 | 1162510.6776 | 2569983.0044 | 1162514.5524
28 | 2569974.505 | 1162415.61 | 2569961.3971 | 1162412.3236
29 | 2569806.0861 | 1162575.6705 | 2569799.0056 | 1162573.6762
30 | 2569806.0861 | 1162575.6705 | 2569819.2268 | 1162579.2287
31 | 2569776.7816 | 1162567.4168 | 2569799.0056 | 1162573.6762
32 | 2569837.9472 | 1162584.2984 | 2569834.6606 | 1162583.4083 | 2569832.2442 | 1162582.7535 | 2569819.2268 | 1162579.2287
33 | 2569837.9472 | 1162584.2984 | 2569851.9893 | 1162588.1013 | 2569856.3136 | 1162589.2725
34 | 2569875.1974 | 1162594.3869 | 2569856.3136 | 1162589.2725
35 | 2569879.3516 | 1162595.512 | 2569875.1974 | 1162594.3869
36 | 2569879.3516 | 1162595.512 | 2569910.3472 | 1162604.6123
37 | 2569910.3472 | 1162604.6123 | 2569920.66 | 1162607.6401
38 | 2569837.7659 | 1162491.5217 | 2569832.0169 | 1162491.9753 | 2569812.6749 | 1162496.0419
39 | 2569804.6954 | 1162497.7195 | 2569812.6749 | 1162496.0419
40 | 2569804.6954 | 1162497.7195 | 2569803.3715 | 1162497.9979
41 | 2569790.1787 | 1162500.7716 | 2569803.3715 | 1162497.9979
42 | 2569941.9251 | 1162613.8835 | 2569920.66 | 1162607.6401
43 | 2569941.9251 | 1162613.8835 | 2569960.481 | 1162619.3315
44 | 2569925.3912 | 1162844.2626 | 2569931.6994 | 1162832.8362 | 2569939.0371 | 1162815.8797 | 2569939.2391 | 1162815.4125
45 | 2569834.5969 | 1162787.7029 | 2569925.3912 | 1162844.2626
46 | 2569960.481 | 1162619.3315 | 2569972.4241 | 1162622.838
47 | 2570002.5219 | 1162630.9609 | 2569976.5147 | 1162624.039 | 2569972.4241 | 1162622.838
48 | 2569983.0044 | 1162514.5524 | 2569994.6729 | 1162517.5274 | 2570009.2043 | 1162525.0474 | 2570016.6717 | 1162532.0359
49 | 2569974.505 | 1162415.61 | 2569979.3129 | 1162404.3024 | 2569982.7459 | 1162401.741
50 | 2569989.6164 | 1162396.6136 | 2569983.648 | 1162401.068 | 2569982.7459 | 1162401.741
51 | 2569989.6164 | 1162396.6136 | 2569988.7608 | 1162375.1975
52 | 2570002.2609 | 1162236.5391 | 2570008.2542 | 1162240.33 | 2570010.5265 | 1162244.3318 | 2570010.2569 | 1162248.6353 | 2570005.5865 | 1162256.0859
53 | 2570002.2609 | 1162236.5391 | 2569991.9152 | 1162229.9954 | 2569981.1057 | 1162222.7914
54 | 2569977.9622 | 1162220.6965 | 2569981.1057 | 1162222.7914
55 | 2569977.9622 | 1162220.6965 | 2569961.2532 | 1162209.5608 | 2569958.4829 | 1162207.8958
56 | 2569945.6694 | 1162199.0315 | 2569948.3208 | 1162201.7884 | 2569958.4829 | 1162207.8958
57 | 2569945.6694 | 1162199.0315 | 2569941.495 | 1162194.6911
58 | 2569987.9728 | 1162355.4732 | 2569988.4428 | 1162367.2371
59 | 2569987.9728 | 1162355.4732 | 2569987.7352 | 1162349.5246
60 | 2569988.4428 | 1162367.2371 | 2569988.6178 | 1162371.616
61 | 2569987.566 | 1162345.2903 | 2569987.7352 | 1162349.5246
62 | 2569988.7608 | 1162375.1975 | 2569988.6178 | 1162371.616
63 | 2569987.566 | 1162345.2903 | 2569987.3126 | 1162338.9467
64 | 2569966.2237 | 1162286.2806 | 2569961.2157 | 1162283.5076
65 | 2569966.2237 | 1162286.2806 | 2569986.4194 | 1162316.589
66 | 2569941.7754 | 1162272.743 | 2569961.2157 | 1162283.5076
67 | 2569986.4194 | 1162316.589 | 2569986.4348 | 1162316.9745
68 | 2569987.3126 | 1162338.9467 | 2569986.4348 | 1162316.9745
69 | 2569938.9073 | 1162160.9482 | 2569937.8591 | 1162173.4376 | 2569937.7937 | 1162184.8214 | 2569939.0639 | 1162192.1632 | 2569941.495 | 1162194.6911
70 | 2569938.9073 | 1162160.9482 | 2569913.1883 | 1162168.7444
71 | 2569938.9073 | 1162160.9482 | 2569961.7051 | 1162152.9965 | 2569972.2651 | 1162152.0876 | 2569982.7222 | 1162155.0923 | 2569997.611 | 1162161.8768
72 | 2569913.1883 | 1162168.7444 | 2569893.7372 | 1162174.6407
73 | 2569997.611 | 1162161.8768 | 2570011.686 | 1162170.4725
74 | 2569878.9437 | 1162179.1251 | 2569893.7372 | 1162174.6407
75 | 2570037.4456 | 1162186.2038 | 2570011.686 | 1162170.4725
76 | 2569860.7895 | 1162100.9259 | 2569932.966 | 1162082.8276
77 | 2569860.7895 | 1162100.9259 | 2569847.714 | 1162105.8915
78 | 2570037.4456 | 1162186.2038 | 2570041.0077 | 1162188.3792
79 | 2569878.9437 | 1162179.1251 | 2569880.2605 | 1162197.2387 | 2569880.6917 | 1162199.6724
80 | 2569872.8013 | 1162181.0013 | 2569878.9437 | 1162179.1251
81 | 2569872.8013 | 1162181.0013 | 2569871.274 | 1162165.1153
82 | 2569870.0205 | 1162152.0784 | 2569871.274 | 1162165.1153
83 | 2569872.8013 | 1162181.0013 | 2569831.9617 | 1162193.4241
84 | 2569817.9864 | 1162197.6744 | 2569831.9617 | 1162193.4241
85 | 2569831.9617 | 1162193.4241 | 2569831.3449 | 1162179.4419
86 | 2569817.9864 | 1162197.6744 | 2569807.4409 | 1162201.4516 | 2569804.1754 | 1162202.5635
87 | 2569817.9864 | 1162197.6744 | 2569821.6152 | 1162214.809
88 | 2569830.6125 | 1162162.8376 | 2569831.3449 | 1162179.4419
89 | 2569881.4191 | 1162203.7775 | 2569880.6917 | 1162199.6724
90 | 2569828.8995 | 1162113.0365 | 2569847.714 | 1162105.8915
91 | 2569830.6125 | 1162162.8376 | 2569828.8995 | 1162113.0365
92 | 2569795.5138 | 1162205.5126 | 2569804.1754 | 1162202.5635
93 | 2569827.9116 | 1162235.4524 | 2569824.0448 | 1162226.2806 | 2569821.6152 | 1162214.809
94 | 2569881.4191 | 1162203.7775 | 2569882.6654 | 1162210.8113 | 2569891.5964 | 1162228.7644 | 2569893.511 | 1162231.9741
95 | 2569766.1202 | 1162264.6705 | 2569765.6502 | 1162256.1233 | 2569764.8529 | 1162246.4658
96 | 2569766.5322 | 1162272.1633 | 2569766.1202 | 1162264.6705
97 | 2569764.7046 | 1162244.6693 | 2569764.8529 | 1162246.4658
98 | 2569767.4364 | 1162288.6055 | 2569766.5322 | 1162272.1633
99 | 2569762.4026 | 1162216.7864 | 2569764.7046 | 1162244.6693
100 | 2569762.4026 | 1162216.7864 | 2569758.4665 | 1162202.2056
101 | 2569762.4026 | 1162216.7864 | 2569795.5138 | 1162205.5126
102 | 2569753.8946 | 1162186.4779 | 2569755.189 | 1162190.0648 | 2569758.4665 | 1162202.2056
103 | 2569862.9342 | 1162290.7446 | 2569868.6668 | 1162296.1938
104 | 2569849.2855 | 1162274.567 | 2569859.4858 | 1162287.4667 | 2569862.9342 | 1162290.7446
105 | 2569879.7635 | 1162305.6614 | 2569873.3878 | 1162300.6813 | 2569868.6668 | 1162296.1938
106 | 2569849.2855 | 1162274.567 | 2569836.2905 | 1162284.8153 | 2569826.7311 | 1162293.0135
107 | 2569849.2855 | 1162274.567 | 2569847.977 | 1162272.5062
108 | 2569879.7635 | 1162305.6614 | 2569886.7087 | 1162311.0863 | 2569891.5799 | 1162314.07
109 | 2569821.0346 | 1162297.8987 | 2569826.7311 | 1162293.0135
110 | 2569827.9116 | 1162235.4524 | 2569835.7371 | 1162254.0136 | 2569844.3742 | 1162266.8322 | 2569847.977 | 1162272.5062
111 | 2569898.3738 | 1162318.2313 | 2569891.5799 | 1162314.07
112 | 2569821.0346 | 1162297.8987 | 2569821.0346 | 1162297.8987 | 2569811.3584 | 1162302.9381
113 | 2569806.8791 | 1162304.4193 | 2569808.8781 | 1162304.2298 | 2569811.3584 | 1162302.9381
114 | 2569749.4676 | 1162131.1638 | 2569763.5 | 1162135.1617 | 2569779.487 | 1162131.8016
115 | 2569749.4676 | 1162131.1638 | 2569712.4361 | 1162100.9663
116 | 2569749.4676 | 1162131.1638 | 2569725.209 | 1162141.1939
117 | 2569712.4361 | 1162100.9663 | 2569705.6648 | 1162095.4446 | 2569686.4358 | 1162081.707
118 | 2569725.209 | 1162141.1939 | 2569721.0507 | 1162142.9132 | 2569718.4846 | 1162144.613
119 | 2569750.488 | 1162177.0383 | 2569725.209 | 1162141.1939
120 | 2569753.8946 | 1162186.4779 | 2569750.488 | 1162177.0383
121 | 2569799.2147 | 1162305.1456 | 2569806.8791 | 1162304.4193
122 | 2569941.7754 | 1162272.743 | 2569931.0799 | 1162266.8206
123 | 2569916.5398 | 1162257.5139 | 2569921.1088 | 1162261.2995 | 2569931.0799 | 1162266.8206
124 | 2569916.5398 | 1162257.5139 | 2569910.3457 | 1162252.3821
125 | 2569894.6849 | 1162233.942 | 2569901.1303 | 1162244.7469 | 2569910.3457 | 1162252.3821
126 | 2569894.6849 | 1162233.942 | 2569893.511 | 1162231.9741

## bus_geodata
| x | y | coords
0 | 2569787.3583 | 1162725.164
1 | 2569759.1879 | 1162713.688
2 | 2569791.6397 | 1162727.8649
3 | 2569753.3629 | 1162716.1075
4 | 2569784.3126 | 1162656.3027
5 | 2569785.8431 | 1162745.0362
6 | 2569743.9098 | 1162735.5099
7 | 2569789.8055 | 1162641.017
8 | 2569820.0144 | 1162781.685
9 | 2569798.7356 | 1162605.1739
10 | 2569821.3962 | 1162782.2881
11 | 2569896.1854 | 1162540.2432
12 | 2569891.6926 | 1162554.9939
13 | 2569909.7076 | 1162495.8645
14 | 2569891.1588 | 1162556.7464
15 | 2569889.4925 | 1162492.2476
16 | 2569923.2243 | 1162499.3108
17 | 2569885.217 | 1162576.2546
18 | 2569878.3512 | 1162490.2541
19 | 2569945.9957 | 1162505.1166
20 | 2569952.5524 | 1162410.1061
21 | 2569884.9419 | 1162577.1577
22 | 2569847.2715 | 1162490.7718
23 | 2569967.8067 | 1162510.6776
24 | 2569961.3971 | 1162412.3236
25 | 2569806.0861 | 1162575.6705
26 | 2569799.0056 | 1162573.6762
27 | 2569819.2268 | 1162579.2287
28 | 2569776.7816 | 1162567.4168
29 | 2569837.9472 | 1162584.2984
30 | 2569856.3136 | 1162589.2725
31 | 2569875.1974 | 1162594.3869
32 | 2569879.3516 | 1162595.512
33 | 2569910.3472 | 1162604.6123
34 | 2569812.6749 | 1162496.0419
35 | 2569837.7659 | 1162491.5217
36 | 2569804.6954 | 1162497.7195
37 | 2569803.3715 | 1162497.9979
38 | 2569790.1787 | 1162500.7716
39 | 2569920.66 | 1162607.6401
40 | 2569941.9251 | 1162613.8835
41 | 2569939.2391 | 1162815.4125
42 | 2569925.3912 | 1162844.2626
43 | 2569834.5969 | 1162787.7029
44 | 2569960.481 | 1162619.3315
45 | 2569972.4241 | 1162622.838
46 | 2570002.5219 | 1162630.9609
47 | 2569983.0044 | 1162514.5524
48 | 2569982.7459 | 1162401.741
49 | 2569974.505 | 1162415.61
50 | 2569989.6164 | 1162396.6136
51 | 2570016.6717 | 1162532.0359
52 | 2570002.2609 | 1162236.5391
53 | 2570005.5865 | 1162256.0859
54 | 2569981.1057 | 1162222.7914
55 | 2569977.9622 | 1162220.6965
56 | 2569958.4829 | 1162207.8958
57 | 2569945.6694 | 1162199.0315
58 | 2569987.9728 | 1162355.4732
59 | 2569988.4428 | 1162367.2371
60 | 2569987.7352 | 1162349.5246
61 | 2569988.6178 | 1162371.616
62 | 2569987.566 | 1162345.2903
63 | 2569966.2237 | 1162286.2806
64 | 2569961.2157 | 1162283.5076
65 | 2569986.4194 | 1162316.589
66 | 2569988.7608 | 1162375.1975
67 | 2569987.3126 | 1162338.9467
68 | 2569986.4348 | 1162316.9745
69 | 2569941.495 | 1162194.6911
70 | 2569938.9073 | 1162160.9482
71 | 2569913.1883 | 1162168.7444
72 | 2569997.611 | 1162161.8768
73 | 2569893.7372 | 1162174.6407
74 | 2570011.686 | 1162170.4725
75 | 2569932.966 | 1162082.8276
76 | 2569860.7895 | 1162100.9259
77 | 2570037.4456 | 1162186.2038
78 | 2570041.0077 | 1162188.3792
79 | 2569878.9437 | 1162179.1251
80 | 2569871.274 | 1162165.1153
81 | 2569872.8013 | 1162181.0013
82 | 2569870.0205 | 1162152.0784
83 | 2569831.9617 | 1162193.4241
84 | 2569817.9864 | 1162197.6744
85 | 2569831.3449 | 1162179.4419
86 | 2569880.6917 | 1162199.6724
87 | 2569847.714 | 1162105.8915
88 | 2569828.8995 | 1162113.0365
89 | 2569804.1754 | 1162202.5635
90 | 2569821.6152 | 1162214.809
91 | 2569830.6125 | 1162162.8376
92 | 2569881.4191 | 1162203.7775
93 | 2569766.1202 | 1162264.6705
94 | 2569764.8529 | 1162246.4658
95 | 2569766.5322 | 1162272.1633
96 | 2569764.7046 | 1162244.6693
97 | 2569767.4364 | 1162288.6055
98 | 2569762.4026 | 1162216.7864
99 | 2569758.4665 | 1162202.2056
100 | 2569795.5138 | 1162205.5126
101 | 2569862.9342 | 1162290.7446
102 | 2569868.6668 | 1162296.1938
103 | 2569849.2855 | 1162274.567
104 | 2569879.7635 | 1162305.6614
105 | 2569826.7311 | 1162293.0135
106 | 2569847.977 | 1162272.5062
107 | 2569891.5799 | 1162314.07
108 | 2569821.0346 | 1162297.8987
109 | 2569827.9116 | 1162235.4524
110 | 2569898.3738 | 1162318.2313
111 | 2569811.3584 | 1162302.9381
112 | 2569779.487 | 1162131.8016
113 | 2569749.4676 | 1162131.1638
114 | 2569712.4361 | 1162100.9663
115 | 2569725.209 | 1162141.1939
116 | 2569750.488 | 1162177.0383
117 | 2569753.8946 | 1162186.4779
118 | 2569686.4358 | 1162081.707
119 | 2569718.4846 | 1162144.613
120 | 2569806.8791 | 1162304.4193
121 | 2569799.2147 | 1162305.1456
122 | 2569941.7754 | 1162272.743
123 | 2569931.0799 | 1162266.8206
124 | 2569916.5398 | 1162257.5139
125 | 2569910.3457 | 1162252.3821
126 | 2569894.6849 | 1162233.942
127 | 2569893.511 | 1162231.9741
128 | 2569909.7076 | 1162495.8645

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97812 | -0.42093 | 0.040871 | 0.010243
1 | 0.98075 | -0.36965 | 0 | 0
2 | 0.97788 | -0.42568 | 0 | 0
3 | 0.98073 | -0.37 | 0 | 0
4 | 0.98353 | -0.31559 | 0.017364 | 0.0043517
5 | 0.977 | -0.44293 | 0 | 0
6 | 0.98066 | -0.37129 | 0.0030926 | 0.00077507
7 | 0.98395 | -0.30732 | 0.038655 | 0.0096879
8 | 0.97412 | -0.49964 | 0.030056 | 0.0075327
9 | 0.98525 | -0.28217 | 0.009779 | 0.0024508
10 | 0.97409 | -0.50024 | 0.0017544 | 0.0004397
11 | 0.99317 | -0.12964 | 0.0044628 | 0.0011185
12 | 0.99221 | -0.14801 | 0.0051745 | 0.0012969
13 | 0.9961 | -0.073676 | 0 | 0
14 | 0.9921 | -0.15015 | 0.0049854 | 0.0012495
15 | 0.99861 | -0.026196 | 0.0026348 | 0.00066035
16 | 0.99528 | -0.089242 | 0.0016123 | 0.00040407
17 | 0.99088 | -0.17359 | 0.0058571 | 0.0014679
18 | 1 | 0 | -0.58127 | -0.14903
19 | 0.9951 | -0.092581 | 0.0032306 | 0.00080966
20 | 0.98995 | -0.19066 | 0.0043124 | 0.0010808
21 | 0.99082 | -0.17465 | 0.0051968 | 0.0013024
22 | 0.99888 | -0.021571 | 0.0071078 | 0.0017814
23 | 0.995 | -0.094499 | 0.0019273 | 0.00048303
24 | 0.98944 | -0.20039 | 0.0056437 | 0.0014144
25 | 0.98639 | -0.26018 | 0 | 0
26 | 0.9863 | -0.26176 | 0.0060146 | 0.0015074
27 | 0.98693 | -0.24962 | 0.011027 | 0.0027637
28 | 0.98618 | -0.26422 | 0.0059458 | 0.0014901
29 | 0.98776 | -0.23364 | 0.0091957 | 0.0023047
30 | 0.98861 | -0.21722 | 0.0033555 | 0.00084098
31 | 0.9895 | -0.20006 | 0.025095 | 0.0062894
32 | 0.98972 | -0.19581 | 0 | 0
33 | 0.98894 | -0.21091 | 0.0013194 | 0.00033067
34 | 0.99818 | -0.03492 | 0.005425 | 0.0013596
35 | 0.9986 | -0.026973 | 0.014622 | 0.0036646
36 | 0.99809 | -0.036686 | 0.0037473 | 0.00093917
37 | 0.99808 | -0.03689 | 0.0036151 | 0.00090602
38 | 0.99802 | -0.038072 | 0.0050121 | 0.0012562
39 | 0.9887 | -0.21569 | 0.0031486 | 0.00078911
40 | 0.98825 | -0.2243 | 0.003097 | 0.00077619
41 | 0.9729 | -0.52369 | 0.004643 | 0.0011636
42 | 0.97304 | -0.52095 | 0.0032521 | 0.00081505
43 | 0.97383 | -0.50541 | 0.01181 | 0.00296
44 | 0.98792 | -0.23075 | 0.011705 | 0.0029336
45 | 0.98784 | -0.23231 | 0.0027579 | 0.00069119
46 | 0.98772 | -0.23466 | 0.0042214 | 0.001058
47 | 0.99496 | -0.095304 | 0.0018913 | 0.00047401
48 | 0.9878 | -0.23181 | 0.0032718 | 0.00081999
49 | 0.9887 | -0.21449 | 0 | 0
50 | 0.98734 | -0.24065 | 0 | 0
51 | 0.99493 | -0.095999 | 0.0010209 | 0.00025585
52 | 0.97128 | -0.55381 | 0.005545 | 0.0013897
53 | 0.97117 | -0.55612 | 0.0050423 | 0.0012637
54 | 0.97153 | -0.54887 | 0.0030583 | 0.00076648
55 | 0.97158 | -0.54792 | 0.0039771 | 0.00099676
56 | 0.97196 | -0.54034 | 0.0028511 | 0.00071454
57 | 0.97226 | -0.53442 | 0.0044118 | 0.0011057
58 | 0.98517 | -0.28242 | 0.0033364 | 0.00083619
59 | 0.98577 | -0.27082 | 0.0033774 | 0.00084644
60 | 0.98487 | -0.28821 | 0.0032225 | 0.00080763
61 | 0.986 | -0.26644 | 0.0032273 | 0.00080883
62 | 0.98466 | -0.29226 | 0.0033353 | 0.0008359
63 | 0.98162 | -0.35113 | 0.0058111 | 0.0014564
64 | 0.98137 | -0.35606 | 0.0042862 | 0.0010742
65 | 0.98328 | -0.31892 | 0.0054725 | 0.0013715
66 | 0.98619 | -0.26281 | 0.0047237 | 0.0011839
67 | 0.98435 | -0.29825 | 0.0044603 | 0.0011178
68 | 0.9833 | -0.31857 | 0.0038868 | 0.00097414
69 | 0.9724 | -0.53165 | 0.0040206 | 0.0010077
70 | 0.97335 | -0.51309 | 0 | 0
71 | 0.97439 | -0.49255 | 0.0038292 | 0.0009597
72 | 0.97261 | -0.5275 | 0 | 0
73 | 0.97525 | -0.47562 | 0.003015 | 0.00075563
74 | 0.97242 | -0.53135 | 0.0036084 | 0.00090435
75 | 0.97292 | -0.52164 | 0.0041147 | 0.0010312
76 | 0.9732 | -0.516 | 0.002786 | 0.00069823
77 | 0.97217 | -0.53639 | 0.0038971 | 0.00097671
78 | 0.97215 | -0.53679 | 0.0051598 | 0.0012932
79 | 0.9756 | -0.46876 | 0 | 0
80 | 0.97536 | -0.47345 | 0.0029204 | 0.00073191
81 | 0.97543 | -0.47206 | 0 | 0
82 | 0.97534 | -0.47388 | 0.0018099 | 0.0004536
83 | 0.97436 | -0.49308 | 0 | 0
84 | 0.97405 | -0.4992 | 0 | 0
85 | 0.97415 | -0.49722 | 0.0022167 | 0.00055557
86 | 0.97637 | -0.45359 | 0.003204 | 0.00080299
87 | 0.97329 | -0.51423 | 0.0014324 | 0.00035899
88 | 0.97345 | -0.51114 | 0.0022191 | 0.00055615
89 | 0.97391 | -0.50202 | 0.0010372 | 0.00025995
90 | 0.97385 | -0.5032 | 0.0016534 | 0.00041439
91 | 0.97394 | -0.50147 | 0.0033546 | 0.00084074
92 | 0.97653 | -0.45046 | 0.0036271 | 0.00090903
93 | 0.97296 | -0.52069 | 0.0027661 | 0.00069325
94 | 0.9731 | -0.51788 | 0.0032502 | 0.00081457
95 | 0.97292 | -0.52146 | 0.0028844 | 0.0007229
96 | 0.97312 | -0.51749 | 0.0033292 | 0.00083436
97 | 0.97288 | -0.52228 | 0.002702 | 0.00067719
98 | 0.97351 | -0.50981 | 0 | 0
99 | 0.97335 | -0.51298 | 0.0026182 | 0.00065619
100 | 0.97382 | -0.50373 | 0.0029984 | 0.00075147
101 | 0.97253 | -0.5293 | 0.0046243 | 0.001159
102 | 0.97241 | -0.53167 | 0.0037881 | 0.0009494
103 | 0.97294 | -0.52113 | 0 | 0
104 | 0.97224 | -0.53504 | 0.0028379 | 0.00071126
105 | 0.97241 | -0.53166 | 0.0040103 | 0.0010051
106 | 0.97303 | -0.51931 | 0.0030937 | 0.00077535
107 | 0.9721 | -0.53763 | 0.0045603 | 0.0011429
108 | 0.9723 | -0.53382 | 0.004451 | 0.0011155
109 | 0.97361 | -0.50798 | 0.0044031 | 0.0011035
110 | 0.97207 | -0.53838 | 0.005103 | 0.0012789
111 | 0.97218 | -0.53607 | 0.0013248 | 0.00033203
112 | 0.97213 | -0.53711 | 0.0037813 | 0.00094769
113 | 0.97224 | -0.53495 | 0 | 0
114 | 0.97203 | -0.53911 | 0.0033553 | 0.00084091
115 | 0.97245 | -0.53084 | 0.0024938 | 0.000625
116 | 0.97304 | -0.51925 | 0.0030769 | 0.00077113
117 | 0.9732 | -0.51603 | 0.0028233 | 0.0007076
118 | 0.97199 | -0.53992 | 0.0013584 | 0.00034045
119 | 0.97243 | -0.5313 | 0.0033456 | 0.00083849
120 | 0.97214 | -0.53694 | 0.0065539 | 0.0016426
121 | 0.97212 | -0.5374 | 0.0032776 | 0.00082144
122 | 0.9804 | -0.37476 | 0.0031056 | 0.00077834
123 | 0.97988 | -0.38489 | 0.003086 | 0.00077342
124 | 0.97916 | -0.39902 | 0.0022091 | 0.00055366
125 | 0.97883 | -0.40551 | 0.0030352 | 0.00076069
126 | 0.97783 | -0.425 | 0.0028548 | 0.00071548
127 | 0.97774 | -0.42679 | 0.0038467 | 0.00096407
128 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.092593 | -0.023283 | 0.09282 | 0.023428 | 0.00022736 | 0.00014512 | 0.14089 | 0.14089 | 0.14089 | 0.97812 | -0.42093 | 0.98075 | -0.36965 | 38.7058
1 | 0.051722 | 0.01304 | -0.05171 | -0.013032 | 1.1767e-05 | 7.4673e-06 | 0.078712 | 0.078712 | 0.078712 | 0.97812 | -0.42093 | 0.97788 | -0.42568 | 21.6241
2 | 0.0030928 | 0.00077486 | -0.0030928 | -0.00077491 | 5.1954e-08 | -4.6147e-08 | 0.0046924 | 0.0046924 | 0.0046924 | 0.98075 | -0.36965 | 0.98073 | -0.37 | 1.2891
3 | -0.095913 | -0.024203 | 0.096162 | 0.024361 | 0.00024901 | 0.00015778 | 0.14558 | 0.14558 | 0.14558 | 0.98075 | -0.36965 | 0.98353 | -0.31559 | 19.9975
4 | 0.05171 | 0.013032 | -0.051667 | -0.013005 | 4.2626e-05 | 2.7051e-05 | 0.078712 | 0.078712 | 0.078712 | 0.97788 | -0.42568 | 0.977 | -0.44293 | 21.6241
5 | 0.0030928 | 0.00077491 | -0.0030926 | -0.00077507 | 1.8877e-07 | -1.6764e-07 | 0.0046924 | 0.0046925 | 0.0046925 | 0.98073 | -0.37 | 0.98066 | -0.37129 | 1.2892
6 | -0.11353 | -0.028713 | 0.11357 | 0.028741 | 4.5039e-05 | 2.7999e-05 | 0.17185 | 0.17185 | 0.17185 | 0.98353 | -0.31559 | 0.98395 | -0.30732 | 11.8029
7 | 0.051667 | 0.013005 | -0.051528 | -0.012917 | 0.00013966 | 8.8631e-05 | 0.078712 | 0.078712 | 0.078712 | 0.977 | -0.44293 | 0.97412 | -0.49964 | 21.6242
8 | -0.15223 | -0.038429 | 0.15241 | 0.038544 | 0.00018368 | 0.00011568 | 0.23031 | 0.23031 | 0.23031 | 0.98395 | -0.30732 | 0.98525 | -0.28217 | 15.8179
9 | 0.021472 | 0.005384 | -0.021471 | -0.0053837 | 6.0828e-07 | 3.7053e-07 | 0.0328 | 0.0328 | 0.0328 | 0.97412 | -0.49964 | 0.97409 | -0.50024 | 9.0111
10 | -0.16219 | -0.040995 | 0.16236 | 0.041103 | 0.00017121 | 0.00010802 | 0.24508 | 0.24508 | 0.24508 | 0.98525 | -0.28217 | 0.98639 | -0.26018 | 16.8322
11 | 0.019717 | 0.004944 | -0.019712 | -0.004941 | 4.8571e-06 | 2.9309e-06 | 0.03012 | 0.03012 | 0.03012 | 0.97409 | -0.50024 | 0.97383 | -0.50541 | 8.2748
12 | 0.27192 | 0.069124 | -0.27168 | -0.068971 | 0.00024035 | 0.00015303 | 0.40776 | 0.40776 | 0.40776 | 0.99317 | -0.12964 | 0.99221 | -0.14801 | 28.0052
13 | -0.27639 | -0.070242 | 0.27713 | 0.070718 | 0.00074705 | 0.0004757 | 0.41444 | 0.41444 | 0.41444 | 0.99317 | -0.12964 | 0.9961 | -0.073676 | 28.4644
14 | 0.26651 | 0.067674 | -0.26648 | -0.067656 | 2.748e-05 | 1.7492e-05 | 0.4 | 0.4 | 0.4 | 0.99221 | -0.14801 | 0.9921 | -0.15015 | 27.4722
15 | -0.53548 | -0.13719 | 0.53671 | 0.13798 | 0.0012352 | 0.00078946 | 0.80098 | 0.80098 | 0.80098 | 0.9961 | -0.073676 | 0.99861 | -0.026196 | 55.0126
16 | 0.25835 | 0.066477 | -0.25815 | -0.066352 | 0.0001954 | 0.00012433 | 0.38654 | 0.38654 | 0.38654 | 0.9961 | -0.073676 | 0.99528 | -0.089242 | 26.5484
17 | 0.26149 | 0.066407 | -0.2612 | -0.066219 | 0.00029456 | 0.00018747 | 0.39252 | 0.39252 | 0.39252 | 0.9921 | -0.15015 | 0.99088 | -0.17359 | 26.9587
18 | -0.53935 | -0.13864 | 0.54003 | 0.13908 | 0.00068745 | 0.00043938 | 0.80491 | 0.80491 | 0.80491 | 0.99861 | -0.026196 | 1 | 0 | 55.2823
19 | 0.008072 | 0.0020225 | -0.0080707 | -0.0020219 | 1.2834e-06 | 5.1605e-07 | 0.012068 | 0.012068 | 0.012068 | 0.99528 | -0.089242 | 0.9951 | -0.092581 | 3.3154
20 | 0.24847 | 0.063926 | -0.24725 | -0.063151 | 0.0012187 | 0.0007751 | 0.37207 | 0.37207 | 0.37207 | 0.99528 | -0.089242 | 0.98995 | -0.19066 | 25.5541
21 | 0.25534 | 0.064752 | -0.25533 | -0.064743 | 1.3031e-05 | 8.2911e-06 | 0.38372 | 0.38372 | 0.38372 | 0.99088 | -0.17359 | 0.99082 | -0.17465 | 26.3546
22 | 0.039587 | 0.0099425 | -0.039546 | -0.0099168 | 4.0702e-05 | 2.5639e-05 | 0.058913 | 0.058913 | 0.058913 | 1 | 0 | 0.99888 | -0.021571 | 16.1849
23 | 0.0048401 | 0.0012123 | -0.0048397 | -0.0012123 | 4.4212e-07 | -9.4254e-09 | 0.0072373 | 0.0072374 | 0.0072374 | 0.9951 | -0.092581 | 0.995 | -0.094499 | 1.9883
24 | 0.24293 | 0.06207 | -0.24282 | -0.061997 | 0.00011425 | 7.2654e-05 | 0.36559 | 0.36559 | 0.36559 | 0.98995 | -0.19066 | 0.98944 | -0.20039 | 25.1089
25 | 0.25013 | 0.063441 | -0.24988 | -0.063279 | 0.00025419 | 0.00016169 | 0.37592 | 0.37592 | 0.37592 | 0.99082 | -0.17465 | 0.98972 | -0.19581 | 25.8186
26 | 0.032438 | 0.0081354 | -0.03243 | -0.0081302 | 8.3502e-06 | 5.2193e-06 | 0.048325 | 0.048325 | 0.048325 | 0.99888 | -0.021571 | 0.9986 | -0.026973 | 13.276
27 | 0.0029123 | 0.00072925 | -0.0029122 | -0.00072939 | 1.1156e-07 | -1.3231e-07 | 0.0043551 | 0.0043552 | 0.0043552 | 0.995 | -0.094499 | 0.99496 | -0.095304 | 1.1965
28 | 0.23718 | 0.060583 | -0.23702 | -0.06048 | 0.00016155 | 0.0001027 | 0.3571 | 0.3571 | 0.3571 | 0.98944 | -0.20039 | 0.9887 | -0.21449 | 24.526
29 | 0.011962 | 0.0029982 | -0.011961 | -0.0029977 | 8.9827e-07 | 4.81e-07 | 0.018045 | 0.018045 | 0.018045 | 0.98639 | -0.26018 | 0.9863 | -0.26176 | 4.9575
30 | -0.17432 | -0.044101 | 0.17441 | 0.044157 | 8.8362e-05 | 5.5856e-05 | 0.26312 | 0.26312 | 0.26312 | 0.98639 | -0.26018 | 0.98693 | -0.24962 | 18.0715
31 | 0.0059465 | 0.0014903 | -0.0059458 | -0.0014901 | 6.9686e-07 | 1.5136e-07 | 0.0089713 | 0.0089714 | 0.0089714 | 0.9863 | -0.26176 | 0.98618 | -0.26422 | 2.4647
32 | -0.18544 | -0.046921 | 0.18558 | 0.047011 | 0.00014229 | 9.0076e-05 | 0.27975 | 0.27975 | 0.27975 | 0.98693 | -0.24962 | 0.98776 | -0.23364 | 19.2134
33 | -0.19478 | -0.049316 | 0.19493 | 0.049413 | 0.00015377 | 9.7439e-05 | 0.2936 | 0.2936 | 0.2936 | 0.98776 | -0.23364 | 0.98861 | -0.21722 | 20.1648
34 | -0.19829 | -0.050254 | 0.19845 | 0.050358 | 0.00016359 | 0.00010369 | 0.29865 | 0.29865 | 0.29865 | 0.98861 | -0.21722 | 0.9895 | -0.20006 | 20.5117
35 | -0.22354 | -0.056647 | 0.22359 | 0.056676 | 4.5657e-05 | 2.8999e-05 | 0.33639 | 0.33639 | 0.33639 | 0.9895 | -0.20006 | 0.98972 | -0.19581 | 23.1036
36 | 0.02629 | 0.0066029 | -0.026271 | -0.0065912 | 1.893e-05 | 1.1701e-05 | 0.039531 | 0.039531 | 0.039531 | 0.98972 | -0.19581 | 0.98894 | -0.21091 | 10.8601
37 | 0.024951 | 0.0062605 | -0.024946 | -0.006257 | 5.6818e-06 | 3.4985e-06 | 0.037546 | 0.037546 | 0.037546 | 0.98894 | -0.21091 | 0.9887 | -0.21569 | 10.3147
38 | -0.017801 | -0.0044616 | 0.017808 | 0.0044656 | 6.7421e-06 | 3.981e-06 | 0.026536 | 0.026536 | 0.026536 | 0.99818 | -0.03492 | 0.9986 | -0.026973 | 7.2902
39 | 0.012376 | 0.0031019 | -0.012375 | -0.0031014 | 1.0408e-06 | 5.5951e-07 | 0.018449 | 0.018449 | 0.018449 | 0.99818 | -0.03492 | 0.99809 | -0.036686 | 5.0685
40 | 0.0086275 | 0.0021622 | -0.0086274 | -0.0021622 | 8.3935e-08 | 3.6037e-08 | 0.012862 | 0.012862 | 0.012862 | 0.99809 | -0.036686 | 0.99808 | -0.03689 | 3.5336
41 | 0.0050124 | 0.0012562 | -0.0050121 | -0.0012562 | 2.8231e-07 | 4.5058e-09 | 0.0074728 | 0.0074729 | 0.0074729 | 0.99808 | -0.03689 | 0.99802 | -0.038072 | 2.053
42 | 0.021797 | 0.0054679 | -0.021788 | -0.0054624 | 8.9452e-06 | 5.4408e-06 | 0.032807 | 0.032807 | 0.032807 | 0.9887 | -0.21569 | 0.98825 | -0.2243 | 9.0129
43 | 0.018691 | 0.0046863 | -0.018685 | -0.0046828 | 5.7443e-06 | 3.4286e-06 | 0.028144 | 0.028144 | 0.028144 | 0.98825 | -0.2243 | 0.98792 | -0.23075 | 7.7319
44 | -0.004643 | -0.0011636 | 0.0046436 | 0.0011636 | 6.0583e-07 | -1.0159e-08 | 0.0071013 | 0.0071011 | 0.0071013 | 0.9729 | -0.52369 | 0.97304 | -0.52095 | 1.9509
45 | -0.0078957 | -0.0019787 | 0.0079015 | 0.0019811 | 5.848e-06 | 2.4129e-06 | 0.012074 | 0.012074 | 0.012074 | 0.97304 | -0.52095 | 0.97383 | -0.50541 | 3.3171
46 | 0.0069802 | 0.0017492 | -0.0069797 | -0.0017491 | 5.1595e-07 | 1.7084e-07 | 0.010514 | 0.010514 | 0.010514 | 0.98792 | -0.23075 | 0.98784 | -0.23231 | 2.8884
47 | 0.0042218 | 0.0010579 | -0.0042214 | -0.001058 | 4.7281e-07 | -9.6473e-08 | 0.0063594 | 0.0063595 | 0.0063595 | 0.98784 | -0.23231 | 0.98772 | -0.23466 | 1.7471
48 | 0.0010209 | 0.00025537 | -0.0010209 | -0.00025585 | 3.3767e-08 | -4.8009e-07 | 0.0015266 | 0.0015268 | 0.0015268 | 0.99496 | -0.095304 | 0.99493 | -0.095999 | 0.41945
49 | -0.23682 | -0.060354 | 0.23702 | 0.06048 | 0.0001981 | 0.00012594 | 0.3571 | 0.3571 | 0.3571 | 0.9878 | -0.23181 | 0.9887 | -0.21449 | 24.526
50 | 0.23355 | 0.059534 | -0.23345 | -0.059471 | 9.9679e-05 | 6.3356e-05 | 0.35217 | 0.35217 | 0.35217 | 0.9878 | -0.23181 | 0.98734 | -0.24065 | 24.1875
51 | 0.23345 | 0.059471 | -0.2332 | -0.059312 | 0.00024921 | 0.0001584 | 0.35217 | 0.35217 | 0.35217 | 0.98734 | -0.24065 | 0.98619 | -0.26281 | 24.1876
52 | 0.0050429 | 0.0012638 | -0.0050423 | -0.0012637 | 5.5507e-07 | 4.8357e-08 | 0.0077257 | 0.0077259 | 0.0077259 | 0.97128 | -0.55381 | 0.97117 | -0.55612 | 2.1225
53 | -0.010588 | -0.0026535 | 0.01059 | 0.0026548 | 2.4895e-06 | 1.2809e-06 | 0.016221 | 0.016221 | 0.016221 | 0.97128 | -0.55381 | 0.97153 | -0.54887 | 4.4562
54 | -0.013649 | -0.0034212 | 0.013649 | 0.0034216 | 6.1906e-07 | 3.4942e-07 | 0.020905 | 0.020905 | 0.020905 | 0.97153 | -0.54887 | 0.97158 | -0.54792 | 5.7431
55 | -0.017626 | -0.0044183 | 0.017633 | 0.0044221 | 6.3709e-06 | 3.7885e-06 | 0.026996 | 0.026996 | 0.026996 | 0.97158 | -0.54792 | 0.97196 | -0.54034 | 7.4164
56 | -0.020484 | -0.0051367 | 0.02049 | 0.0051402 | 5.7833e-06 | 3.5069e-06 | 0.03136 | 0.03136 | 0.03136 | 0.97196 | -0.54034 | 0.97226 | -0.53442 | 8.6155
57 | -0.024901 | -0.0062459 | 0.024905 | 0.0062479 | 3.2802e-06 | 2.0247e-06 | 0.038113 | 0.038112 | 0.038113 | 0.97226 | -0.53442 | 0.9724 | -0.53165 | 10.4705
58 | -0.22166 | -0.056339 | 0.22178 | 0.056418 | 0.00012392 | 7.8711e-05 | 0.33508 | 0.33508 | 0.33508 | 0.98517 | -0.28242 | 0.98577 | -0.27082 | 23.0134
59 | 0.21832 | 0.055503 | -0.21826 | -0.055464 | 6.0793e-05 | 3.8605e-05 | 0.33004 | 0.33004 | 0.33004 | 0.98517 | -0.28242 | 0.98487 | -0.28821 | 22.6673
60 | -0.22516 | -0.057264 | 0.22521 | 0.057294 | 4.7543e-05 | 3.0204e-05 | 0.34017 | 0.34017 | 0.34017 | 0.98577 | -0.27082 | 0.986 | -0.26644 | 23.3636
61 | 0.21504 | 0.054657 | -0.21499 | -0.05463 | 4.2006e-05 | 2.6668e-05 | 0.32517 | 0.32517 | 0.32517 | 0.98487 | -0.28821 | 0.98466 | -0.29226 | 22.3329
62 | -0.22843 | -0.058103 | 0.22847 | 0.058129 | 4.0006e-05 | 2.5421e-05 | 0.34504 | 0.34504 | 0.34504 | 0.986 | -0.26644 | 0.98619 | -0.26281 | 23.6981
63 | 0.21166 | 0.053794 | -0.2116 | -0.053755 | 6.0995e-05 | 3.8714e-05 | 0.32013 | 0.32013 | 0.32013 | 0.98466 | -0.29226 | 0.98435 | -0.29825 | 21.9868
64 | 0.19146 | 0.048511 | -0.19141 | -0.048482 | 4.5262e-05 | 2.8679e-05 | 0.29041 | 0.29041 | 0.29041 | 0.98162 | -0.35113 | 0.98137 | -0.35606 | 19.946
65 | -0.19727 | -0.049967 | 0.19757 | 0.050161 | 0.00030571 | 0.00019381 | 0.29922 | 0.29922 | 0.29922 | 0.98162 | -0.35113 | 0.98328 | -0.31892 | 20.551
66 | 0.18712 | 0.047408 | -0.18696 | -0.047302 | 0.00016793 | 0.00010635 | 0.28392 | 0.28392 | 0.28392 | 0.98137 | -0.35606 | 0.9804 | -0.37476 | 19.4997
67 | -0.20305 | -0.051533 | 0.20305 | 0.051535 | 3.4197e-06 | 2.169e-06 | 0.3075 | 0.3075 | 0.3075 | 0.98328 | -0.31892 | 0.9833 | -0.31857 | 21.1198
68 | 0.20714 | 0.052637 | -0.20694 | -0.052509 | 0.00020246 | 0.00012846 | 0.31339 | 0.31339 | 0.31339 | 0.98435 | -0.29825 | 0.9833 | -0.31857 | 21.5237
69 | -0.028925 | -0.0072556 | 0.028951 | 0.0072716 | 2.5625e-05 | 1.5967e-05 | 0.044265 | 0.044265 | 0.044265 | 0.9724 | -0.53165 | 0.97335 | -0.51309 | 12.1607
70 | -0.04163 | -0.010453 | 0.04167 | 0.010479 | 4.0828e-05 | 2.5795e-05 | 0.063649 | 0.063649 | 0.063649 | 0.97335 | -0.51309 | 0.97439 | -0.49255 | 17.4859
71 | 0.012679 | 0.0031813 | -0.01267 | -0.0031765 | 8.7112e-06 | 4.8073e-06 | 0.019384 | 0.019384 | 0.019384 | 0.97335 | -0.51309 | 0.97261 | -0.5275 | 5.3253
72 | -0.0455 | -0.011438 | 0.045536 | 0.011462 | 3.6812e-05 | 2.3306e-05 | 0.069496 | 0.069496 | 0.069496 | 0.97439 | -0.49255 | 0.97525 | -0.47562 | 19.0924
73 | 0.01267 | 0.0031765 | -0.012668 | -0.0031752 | 2.3238e-06 | 1.2826e-06 | 0.019384 | 0.019384 | 0.019384 | 0.97261 | -0.5275 | 0.97242 | -0.53135 | 5.3253
74 | -0.048551 | -0.012217 | 0.048567 | 0.012227 | 1.5913e-05 | 9.7985e-06 | 0.074097 | 0.074096 | 0.074097 | 0.97525 | -0.47562 | 0.9756 | -0.46876 | 10.1781
75 | 0.0090591 | 0.0022709 | -0.009057 | -0.0022699 | 2.1752e-06 | 1.0178e-06 | 0.013863 | 0.013863 | 0.013863 | 0.97242 | -0.53135 | 0.97217 | -0.53639 | 3.8085
76 | -0.0041147 | -0.0010312 | 0.0041158 | 0.001031 | 1.1051e-06 | -2.1707e-07 | 0.0062932 | 0.0062929 | 0.0062932 | 0.97292 | -0.52164 | 0.9732 | -0.516 | 1.7289
77 | -0.0069018 | -0.0017293 | 0.0069024 | 0.0017295 | 5.8407e-07 | 2e-07 | 0.010553 | 0.010553 | 0.010553 | 0.9732 | -0.516 | 0.97329 | -0.51423 | 2.8991
78 | 0.0051599 | 0.0012932 | -0.0051598 | -0.0012932 | 9.763e-08 | 1.0732e-08 | 0.0078978 | 0.0078978 | 0.0078978 | 0.97217 | -0.53639 | 0.97215 | -0.53679 | 2.1697
79 | -0.16121 | -0.040552 | 0.16133 | 0.040626 | 0.000117 | 7.3849e-05 | 0.24594 | 0.24594 | 0.24594 | 0.9756 | -0.46876 | 0.97637 | -0.45359 | 16.8914
80 | 0.11264 | 0.028325 | -0.11263 | -0.028314 | 1.7734e-05 | 1.103e-05 | 0.17184 | 0.17184 | 0.17184 | 0.9756 | -0.46876 | 0.97543 | -0.47206 | 11.8023
81 | -0.0047303 | -0.0011854 | 0.0047306 | 0.0011854 | 3.1167e-07 | 2.7102e-10 | 0.0072165 | 0.0072164 | 0.0072165 | 0.97536 | -0.47345 | 0.97543 | -0.47206 | 1.9826
82 | 0.0018099 | 0.00045346 | -0.0018099 | -0.0004536 | 3.7446e-08 | -1.3949e-07 | 0.0027612 | 0.0027612 | 0.0027612 | 0.97536 | -0.47345 | 0.97534 | -0.47388 | 0.75858
83 | 0.1079 | 0.027129 | -0.10779 | -0.027062 | 0.00010817 | 6.7106e-05 | 0.16463 | 0.16463 | 0.16463 | 0.97543 | -0.47206 | 0.97436 | -0.49308 | 11.3068
84 | 0.09165 | 0.023014 | -0.091623 | -0.022998 | 2.6763e-05 | 1.6403e-05 | 0.13998 | 0.13998 | 0.13998 | 0.97436 | -0.49308 | 0.97405 | -0.4992 | 9.6141
85 | 0.016137 | 0.0040474 | -0.016134 | -0.0040455 | 3.1879e-06 | 1.866e-06 | 0.024645 | 0.024645 | 0.024645 | 0.97436 | -0.49308 | 0.97415 | -0.49722 | 6.7707
86 | 0.041867 | 0.010504 | -0.041862 | -0.010501 | 5.6196e-06 | 2.8672e-06 | 0.063963 | 0.063963 | 0.063963 | 0.97405 | -0.4992 | 0.97391 | -0.50202 | 4.3931
87 | 0.049756 | 0.012494 | -0.049746 | -0.012488 | 9.4887e-06 | 5.2009e-06 | 0.076018 | 0.076018 | 0.076018 | 0.97405 | -0.4992 | 0.97385 | -0.5032 | 5.221
88 | 0.013917 | 0.00349 | -0.013915 | -0.0034884 | 2.8169e-06 | 1.596e-06 | 0.021259 | 0.02126 | 0.02126 | 0.97415 | -0.49722 | 0.97394 | -0.50147 | 5.8405
89 | -0.16453 | -0.041429 | 0.16456 | 0.041445 | 2.4589e-05 | 1.5528e-05 | 0.25082 | 0.25082 | 0.25082 | 0.97637 | -0.45359 | 0.97653 | -0.45046 | 17.2267
90 | -0.0083348 | -0.0020885 | 0.008336 | 0.002089 | 1.2254e-06 | 5.3411e-07 | 0.012742 | 0.012742 | 0.012742 | 0.97329 | -0.51423 | 0.97345 | -0.51114 | 3.5007
91 | -0.010555 | -0.0026451 | 0.01056 | 0.0026476 | 4.8644e-06 | 2.4934e-06 | 0.016134 | 0.016134 | 0.016134 | 0.97345 | -0.51114 | 0.97394 | -0.50147 | 4.4325
92 | 0.040825 | 0.010241 | -0.040821 | -0.01024 | 3.3378e-06 | 1.6808e-06 | 0.062379 | 0.062379 | 0.062379 | 0.97391 | -0.50202 | 0.97382 | -0.50373 | 4.2843
93 | 0.048093 | 0.012074 | -0.048082 | -0.012068 | 1.0978e-05 | 5.9469e-06 | 0.073492 | 0.073492 | 0.073492 | 0.97385 | -0.5032 | 0.97361 | -0.50798 | 5.0475
94 | -0.16818 | -0.042354 | 0.16837 | 0.042474 | 0.00019057 | 0.00012041 | 0.25635 | 0.25635 | 0.25635 | 0.97653 | -0.45046 | 0.97774 | -0.42679 | 17.6063
95 | -0.0083528 | -0.0020932 | 0.008354 | 0.0020937 | 1.1168e-06 | 4.8808e-07 | 0.012774 | 0.012774 | 0.012774 | 0.97296 | -0.52069 | 0.9731 | -0.51788 | 3.5095
96 | 0.0055867 | 0.0014 | -0.0055865 | -0.0014 | 2.0543e-07 | 3.8282e-08 | 0.0085441 | 0.0085441 | 0.0085441 | 0.97296 | -0.52069 | 0.97292 | -0.52146 | 2.3473
97 | -0.011604 | -0.0029083 | 0.011604 | 0.0029084 | 2.1284e-07 | 1.1382e-07 | 0.017744 | 0.017744 | 0.017744 | 0.9731 | -0.51788 | 0.97312 | -0.51749 | 4.8748
98 | 0.0027021 | 0.00067705 | -0.002702 | -0.00067719 | 1.0547e-07 | -1.3699e-07 | 0.0041326 | 0.0041327 | 0.0041327 | 0.97292 | -0.52146 | 0.97288 | -0.52228 | 1.1354
99 | -0.014933 | -0.0037428 | 0.014939 | 0.0037459 | 5.4707e-06 | 3.1535e-06 | 0.022835 | 0.022835 | 0.022835 | 0.97312 | -0.51749 | 0.97351 | -0.50981 | 6.2734
100 | 0.022873 | 0.0057371 | -0.022869 | -0.0057352 | 3.4616e-06 | 1.8399e-06 | 0.034963 | 0.034963 | 0.034963 | 0.97351 | -0.50981 | 0.97335 | -0.51298 | 4.8026
101 | -0.037812 | -0.009483 | 0.037823 | 0.0094883 | 1.0954e-05 | 5.2706e-06 | 0.057798 | 0.057797 | 0.057798 | 0.97351 | -0.50981 | 0.97382 | -0.50373 | 3.9696
102 | 0.020251 | 0.0050791 | -0.020248 | -0.0050776 | 2.9455e-06 | 1.4778e-06 | 0.03096 | 0.030961 | 0.030961 | 0.97335 | -0.51298 | 0.9732 | -0.51603 | 4.2528
103 | 0.016295 | 0.0040853 | -0.016293 | -0.0040842 | 1.8437e-06 | 1.0818e-06 | 0.024932 | 0.024932 | 0.024932 | 0.97253 | -0.5293 | 0.97241 | -0.53167 | 6.8495
104 | -0.020919 | -0.0052442 | 0.020927 | 0.0052492 | 8.1458e-06 | 4.9501e-06 | 0.032008 | 0.032007 | 0.032008 | 0.97253 | -0.5293 | 0.97294 | -0.52113 | 8.7933
105 | 0.012505 | 0.0031348 | -0.012503 | -0.0031337 | 2.0053e-06 | 1.1022e-06 | 0.019135 | 0.019135 | 0.019135 | 0.97241 | -0.53167 | 0.97224 | -0.53504 | 5.257
106 | 0.019631 | 0.0049243 | -0.019621 | -0.0049184 | 9.8522e-06 | 5.9437e-06 | 0.030025 | 0.030025 | 0.030025 | 0.97294 | -0.52113 | 0.97241 | -0.53166 | 8.2486
107 | -0.040558 | -0.010173 | 0.040561 | 0.010176 | 3.5225e-06 | 2.2241e-06 | 0.062032 | 0.062032 | 0.062032 | 0.97294 | -0.52113 | 0.97303 | -0.51931 | 17.0418
108 | 0.0096647 | 0.0024224 | -0.0096635 | -0.0024219 | 1.1918e-06 | 5.8265e-07 | 0.014792 | 0.014792 | 0.014792 | 0.97224 | -0.53504 | 0.9721 | -0.53763 | 4.0637
109 | 0.015611 | 0.0039133 | -0.015609 | -0.0039123 | 1.6059e-06 | 9.3469e-07 | 0.023888 | 0.023888 | 0.023888 | 0.97241 | -0.53166 | 0.9723 | -0.53382 | 6.5627
110 | -0.043655 | -0.010951 | 0.043679 | 0.010965 | 2.358e-05 | 1.3513e-05 | 0.066763 | 0.066763 | 0.066763 | 0.97303 | -0.51931 | 0.97361 | -0.50798 | 6.1139
111 | 0.0051031 | 0.0012789 | -0.005103 | -0.0012789 | 1.823e-07 | 1.7906e-08 | 0.0078115 | 0.0078115 | 0.0078115 | 0.9721 | -0.53763 | 0.97207 | -0.53838 | 2.146
112 | 0.011158 | 0.0027968 | -0.011157 | -0.0027962 | 1.193e-06 | 6.2823e-07 | 0.017076 | 0.017076 | 0.017076 | 0.9723 | -0.53382 | 0.97218 | -0.53607 | 4.6913
113 | 0.009832 | 0.0024642 | -0.0098315 | -0.002464 | 4.0801e-07 | 2.0156e-07 | 0.015049 | 0.015049 | 0.015049 | 0.97218 | -0.53607 | 0.97214 | -0.53694 | 4.1343
114 | -0.0037813 | -0.00094769 | 0.0037817 | 0.00094756 | 3.8852e-07 | -1.3483e-07 | 0.005788 | 0.0057879 | 0.005788 | 0.97213 | -0.53711 | 0.97224 | -0.53495 | 1.5901
115 | 0.0047147 | 0.001181 | -0.0047137 | -0.001181 | 9.3295e-07 | 4.6585e-09 | 0.0072156 | 0.0072158 | 0.0072158 | 0.97224 | -0.53495 | 0.97203 | -0.53911 | 1.9824
116 | -0.0084964 | -0.0021286 | 0.0084981 | 0.0021293 | 1.6645e-06 | 7.3967e-07 | 0.013003 | 0.013003 | 0.013003 | 0.97224 | -0.53495 | 0.97245 | -0.53084 | 3.5724
117 | 0.0013585 | 0.00034008 | -0.0013584 | -0.00034045 | 5.2491e-08 | -3.6763e-07 | 0.0020794 | 0.0020796 | 0.0020796 | 0.97203 | -0.53911 | 0.97199 | -0.53992 | 0.57131
118 | 0.0033457 | 0.00083844 | -0.0033456 | -0.00083849 | 7.4478e-08 | -4.6345e-08 | 0.0051195 | 0.0051195 | 0.0051195 | 0.97245 | -0.53084 | 0.97243 | -0.5313 | 1.4065
119 | -0.014338 | -0.0035927 | 0.014345 | 0.0035973 | 7.9165e-06 | 4.5221e-06 | 0.021939 | 0.021938 | 0.021939 | 0.97245 | -0.53084 | 0.97304 | -0.51925 | 6.0271
120 | -0.017422 | -0.0043684 | 0.017425 | 0.00437 | 2.6715e-06 | 1.5851e-06 | 0.026644 | 0.026644 | 0.026644 | 0.97304 | -0.51925 | 0.9732 | -0.51603 | 7.3197
121 | 0.0032777 | 0.00082139 | -0.0032776 | -0.00082144 | 7.2667e-08 | -4.8944e-08 | 0.005017 | 0.005017 | 0.005017 | 0.97214 | -0.53694 | 0.97212 | -0.5374 | 1.3783
122 | 0.18385 | 0.046523 | -0.18376 | -0.046467 | 8.9348e-05 | 5.6566e-05 | 0.2792 | 0.2792 | 0.2792 | 0.9804 | -0.37476 | 0.97988 | -0.38489 | 19.176
123 | 0.18068 | 0.045693 | -0.18055 | -0.045616 | 0.00012244 | 7.7491e-05 | 0.27452 | 0.27452 | 0.27452 | 0.97988 | -0.38489 | 0.97916 | -0.39902 | 18.8541
124 | 0.17834 | 0.045062 | -0.17829 | -0.045027 | 5.5447e-05 | 3.5082e-05 | 0.27116 | 0.27116 | 0.27116 | 0.97916 | -0.39902 | 0.97883 | -0.40551 | 18.6236
125 | 0.17525 | 0.044266 | -0.17509 | -0.044163 | 0.00016351 | 0.00010341 | 0.26655 | 0.26655 | 0.26655 | 0.97883 | -0.40551 | 0.97783 | -0.425 | 18.3067
126 | 0.17224 | 0.043448 | -0.17222 | -0.043438 | 1.4769e-05 | 9.3374e-06 | 0.2622 | 0.2622 | 0.2622 | 0.97783 | -0.425 | 0.97774 | -0.42679 | 18.0083

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.59162 | 0.15162

## res_load
| p_mw | q_mvar
0 | 0.040871 | 0.010243
1 | 0.017364 | 0.0043517
2 | 0.0030926 | 0.00077507
3 | 0.038655 | 0.0096879
4 | 0.030056 | 0.0075327
5 | 0.009779 | 0.0024508
6 | 0.0017544 | 0.0004397
7 | 0.0044628 | 0.0011185
8 | 0.0051745 | 0.0012969
9 | 0.0049854 | 0.0012495
10 | 0.0026348 | 0.00066035
11 | 0.0016123 | 0.00040407
12 | 0.0058571 | 0.0014679
13 | 0.010348 | 0.0025935
14 | 0.0032306 | 0.00080966
15 | 0.0043124 | 0.0010808
16 | 0.0051968 | 0.0013024
17 | 0.0071078 | 0.0017814
18 | 0.0019273 | 0.00048303
19 | 0.0056437 | 0.0014144
20 | 0.0060146 | 0.0015074
21 | 0.011027 | 0.0027637
22 | 0.0059458 | 0.0014901
23 | 0.0091957 | 0.0023047
24 | 0.0033555 | 0.00084098
25 | 0.025095 | 0.0062894
26 | 0.0013194 | 0.00033067
27 | 0.005425 | 0.0013596
28 | 0.014622 | 0.0036646
29 | 0.0037473 | 0.00093917
30 | 0.0036151 | 0.00090602
31 | 0.0050121 | 0.0012562
32 | 0.0031486 | 0.00078911
33 | 0.003097 | 0.00077619
34 | 0.004643 | 0.0011636
35 | 0.0032521 | 0.00081505
36 | 0.01181 | 0.00296
37 | 0.011705 | 0.0029336
38 | 0.0027579 | 0.00069119
39 | 0.0042214 | 0.001058
40 | 0.0018913 | 0.00047401
41 | 0.0032718 | 0.00081999
42 | 0.0010209 | 0.00025585
43 | 0.005545 | 0.0013897
44 | 0.0050423 | 0.0012637
45 | 0.0030583 | 0.00076648
46 | 0.0039771 | 0.00099676
47 | 0.0028511 | 0.00071454
48 | 0.0044118 | 0.0011057
49 | 0.0033364 | 0.00083619
50 | 0.0033774 | 0.00084644
51 | 0.0032225 | 0.00080763
52 | 0.0032273 | 0.00080883
53 | 0.0033353 | 0.0008359
54 | 0.0058111 | 0.0014564
55 | 0.0042862 | 0.0010742
56 | 0.0054725 | 0.0013715
57 | 0.0047237 | 0.0011839
58 | 0.0044603 | 0.0011178
59 | 0.0038868 | 0.00097414
60 | 0.0040206 | 0.0010077
61 | 0.0038292 | 0.0009597
62 | 0.003015 | 0.00075563
63 | 0.0036084 | 0.00090435
64 | 0.0041147 | 0.0010312
65 | 0.002786 | 0.00069823
66 | 0.0038971 | 0.00097671
67 | 0.0051598 | 0.0012932
68 | 0.0029204 | 0.00073191
69 | 0.0018099 | 0.0004536
70 | 0.0022167 | 0.00055557
71 | 0.003204 | 0.00080299
72 | 0.0014324 | 0.00035899
73 | 0.0022191 | 0.00055615
74 | 0.0010372 | 0.00025995
75 | 0.0016534 | 0.00041439
76 | 0.0033546 | 0.00084074
77 | 0.0036271 | 0.00090903
78 | 0.0027661 | 0.00069325
79 | 0.0032502 | 0.00081457
80 | 0.0028844 | 0.0007229
81 | 0.0033292 | 0.00083436
82 | 0.002702 | 0.00067719
83 | 0.0026182 | 0.00065619
84 | 0.0029984 | 0.00075147
85 | 0.0046243 | 0.001159
86 | 0.0037881 | 0.0009494
87 | 0.0028379 | 0.00071126
88 | 0.0040103 | 0.0010051
89 | 0.0030937 | 0.00077535
90 | 0.0045603 | 0.0011429
91 | 0.004451 | 0.0011155
92 | 0.0044031 | 0.0011035
93 | 0.005103 | 0.0012789
94 | 0.0013248 | 0.00033203
95 | 0.0037813 | 0.00094769
96 | 0.0033553 | 0.00084091
97 | 0.0024938 | 0.000625
98 | 0.0030769 | 0.00077113
99 | 0.0028233 | 0.0007076
100 | 0.0013584 | 0.00034045
101 | 0.0033456 | 0.00083849
102 | 0.0065539 | 0.0016426
103 | 0.0032776 | 0.00082144
104 | 0.0031056 | 0.00077834
105 | 0.003086 | 0.00077342
106 | 0.0022091 | 0.00055366
107 | 0.0030352 | 0.00076069
108 | 0.0028548 | 0.00071548
109 | 0.0038467 | 0.00096407

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1