## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2125-8_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2125-8_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2125-8_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2125-8_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2125-8_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_2125-8_0_4_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_2125-8_0_4_node_52 | 0.4 | n |  | TRUE
7 | bus_LV_2125-8_0_4_node_51 | 0.4 | n |  | TRUE
8 | bus_LV_2125-8_0_4_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_2125-8_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_2125-8_0_4_node_48 | 0.4 | n |  | TRUE
11 | bus_LV_2125-8_0_4_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_2125-8_0_4_node_24 | 0.4 | n |  | TRUE
13 | bus_LV_2125-8_0_4_node_54 | 0.4 | n |  | TRUE
14 | bus_LV_2125-8_0_4_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_2125-8_0_4_node_50 | 0.4 | n |  | TRUE
16 | bus_LV_2125-8_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2125-8_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_2125-8_0_4_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_2125-8_0_4_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_2125-8_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_2125-8_0_4_node_60 | 0.4 | n |  | TRUE
22 | bus_LV_2125-8_0_4_node_25 | 0.4 | n |  | TRUE
23 | bus_LV_2125-8_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_2125-8_0_4_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_2125-8_0_4_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_2125-8_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_2125-8_0_4_node_27 | 0.4 | n |  | TRUE
28 | bus_LV_2125-8_0_4_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_2125-8_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_2125-8_0_4_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_2125-8_0_4_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_2125-8_0_4_node_22 | 0.4 | n |  | TRUE
33 | bus_LV_2125-8_0_4_node_53 | 0.4 | n |  | TRUE
34 | bus_LV_2125-8_0_4_node_58 | 0.4 | n |  | TRUE
35 | bus_LV_2125-8_0_4_node_56 | 0.4 | n |  | TRUE
36 | bus_LV_2125-8_0_4_node_37 | 0.4 | n |  | TRUE
37 | bus_LV_2125-8_0_4_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_2125-8_0_4_node_46 | 0.4 | n |  | TRUE
39 | bus_LV_2125-8_0_4_node_35 | 0.4 | n |  | TRUE
40 | bus_LV_2125-8_0_4_node_36 | 0.4 | n |  | TRUE
41 | bus_LV_2125-8_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_2125-8_0_4_node_31 | 0.4 | n |  | TRUE
43 | bus_LV_2125-8_0_4_node_41 | 0.4 | n |  | TRUE
44 | bus_LV_2125-8_0_4_node_61 | 0.4 | n |  | TRUE
45 | bus_LV_2125-8_0_4_node_45 | 0.4 | n |  | TRUE
46 | bus_LV_2125-8_0_4_node_39 | 0.4 | n |  | TRUE
47 | bus_LV_2125-8_0_4_node_29 | 0.4 | n |  | TRUE
48 | bus_LV_2125-8_0_4_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_2125-8_0_4_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_2125-8_0_4_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_2125-8_0_4_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_2125-8_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_2125-8_0_4_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_2125-8_0_4_node_55 | 0.4 | n |  | TRUE
55 | bus_MV_31_0_node_164 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2125-8_0_4_load_0 | 0 | 0.0034599 | 0.00086714 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2125-8_0_4_load_1 | 1 | 0.065082 | 0.016311 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2125-8_0_4_load_52 | 6 | 0.011283 | 0.0028279 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2125-8_0_4_load_51 | 7 | 0.011241 | 0.0028172 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2125-8_0_4_load_48 | 10 | 0.0055748 | 0.0013972 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2125-8_0_4_load_24 | 12 | 0.003193 | 0.00080023 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2125-8_0_4_load_54 | 13 | 0.009333 | 0.0023391 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2125-8_0_4_load_50 | 15 | 0.0046566 | 0.0011671 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2125-8_0_4_load_8 | 16 | 0.0067437 | 0.0016901 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2125-8_0_4_load_60 | 21 | 0.073247 | 0.018357 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2125-8_0_4_load_25 | 22 | 0.002622 | 0.00065714 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2125-8_0_4_load_15 | 24 | 0.0085338 | 0.0021388 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2125-8_0_4_load_18 | 26 | 0.013235 | 0.003317 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2125-8_0_4_load_53 | 33 | 0.0009414 | 0.00023594 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2125-8_0_4_load_58 | 34 | 0.0047834 | 0.0011988 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2125-8_0_4_load_56 | 35 | 0.0041871 | 0.0010494 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2125-8_0_4_load_37 | 36 | 0.027178 | 0.0068115 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2125-8_0_4_load_34 | 37 | 0.019554 | 0.0049007 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2125-8_0_4_load_33 | 41 | 0.015281 | 0.0038298 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2125-8_0_4_load_61 | 44 | 0.021093 | 0.0052864 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2125-8_0_4_load_39 | 46 | 0.016145 | 0.0040464 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2125-8_0_4_load_29 | 47 | 0.027153 | 0.0068052 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2125-8_0_4_load_30 | 48 | 0.021035 | 0.005272 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2125-8_0_4_load_38 | 50 | 0.019087 | 0.0047838 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2125-8_0_4_load_47 | 51 | 0.0022251 | 0.00055766 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2125-8_0_4_load_43 | 52 | 0.033806 | 0.0084725 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2125-8_0_4_load_44 | 53 | 0.016049 | 0.0040221 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2125-8_0_4_load_55 | 54 | 0.082097 | 0.020575 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 54 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2125-8_0_4_line_0 |  | 0 | 1 | 0.01226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
1 | LV_2125-8_0_4_line_1 |  | 0 | 2 | 0.014469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
2 | LV_2125-8_0_4_line_2 |  | 1 | 3 | 0.027865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_2125-8_0_4_line_3 |  | 2 | 4 | 0.069741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_2125-8_0_4_line_4 |  | 3 | 5 | 0.002012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_2125-8_0_4_line_5 |  | 3 | 6 | 0.024352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_2125-8_0_4_line_6 |  | 4 | 7 | 0.0032562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_2125-8_0_4_line_7 |  | 5 | 11 | 0.05552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2125-8_0_4_line_8 |  | 5 | 12 | 0.029471 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_2125-8_0_4_line_9 |  | 6 | 13 | 0.016207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
10 | LV_2125-8_0_4_line_10 |  | 7 | 8 | 0.0040487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_2125-8_0_4_line_11 |  | 8 | 9 | 0.028519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_2125-8_0_4_line_12 |  | 9 | 10 | 0.016317 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_2125-8_0_4_line_13 |  | 10 | 14 | 0.05177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_2125-8_0_4_line_14 |  | 11 | 21 | 0.013593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2125-8_0_4_line_15 |  | 12 | 23 | 0.01798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_2125-8_0_4_line_16 |  | 13 | 54 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_2125-8_0_4_line_17 |  | 14 | 15 | 0.01993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2125-8_0_4_line_18 |  | 15 | 29 | 0.02353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2125-8_0_4_line_19 |  | 16 | 17 | 0.008349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2125-8_0_4_line_20 |  | 16 | 18 | 0.0027303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2125-8_0_4_line_21 |  | 17 | 19 | 0.038091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2125-8_0_4_line_22 |  | 18 | 20 | 0.037007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2125-8_0_4_line_23 |  | 19 | 21 | 0.00046694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2125-8_0_4_line_24 |  | 20 | 22 | 0.0028517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2125-8_0_4_line_25 |  | 23 | 27 | 0.067046 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
26 | LV_2125-8_0_4_line_26 |  | 24 | 25 | 0.026564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2125-8_0_4_line_27 |  | 25 | 26 | 0.0054008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2125-8_0_4_line_28 |  | 26 | 28 | 0.030065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2125-8_0_4_line_29 |  | 27 | 36 | 0.016694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2125-8_0_4_line_30 |  | 27 | 37 | 0.021005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2125-8_0_4_line_31 |  | 28 | 30 | 0.004991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2125-8_0_4_line_32 |  | 28 | 29 | 0.027903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2125-8_0_4_line_33 |  | 30 | 31 | 0.044749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2125-8_0_4_line_34 |  | 30 | 32 | 0.059494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2125-8_0_4_line_35 |  | 30 | 33 | 0.015875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2125-8_0_4_line_36 |  | 31 | 35 | 0.035308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2125-8_0_4_line_37 |  | 32 | 34 | 0.016656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2125-8_0_4_line_38 |  | 33 | 38 | 0.032027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2125-8_0_4_line_39 |  | 37 | 42 | 0.017965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2125-8_0_4_line_40 |  | 38 | 51 | 0.022384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2125-8_0_4_line_41 |  | 38 | 53 | 0.024743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2125-8_0_4_line_42 |  | 39 | 40 | 0.005208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2125-8_0_4_line_43 |  | 39 | 41 | 0.02191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2125-8_0_4_line_44 |  | 40 | 46 | 0.017289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2125-8_0_4_line_45 |  | 41 | 42 | 0.018142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2125-8_0_4_line_46 |  | 42 | 47 | 0.025502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2125-8_0_4_line_47 |  | 43 | 44 | 0.021812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2125-8_0_4_line_48 |  | 43 | 45 | 0.030795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2125-8_0_4_line_49 |  | 45 | 51 | 0.0047125 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2125-8_0_4_line_50 |  | 47 | 48 | 0.026946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2125-8_0_4_line_51 |  | 48 | 49 | 0.02324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2125-8_0_4_line_52 |  | 49 | 50 | 0.017565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2125-8_0_4_line_53 |  | 52 | 53 | 0.0040992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2125-8_0_4_trafo_55 | 0.63 MVA 20/0.4 kV | 55 | 54 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2570897.6125 | 1163151.8992 | 2570909.3947 | 1163148.5091
1 | 2570883.7078 | 1163155.9 | 2570897.6125 | 1163151.8992
2 | 2570936.1729 | 1163140.8043 | 2570909.3947 | 1163148.5091
3 | 2570883.7078 | 1163155.9 | 2570901.3389 | 1163223.3707
4 | 2570936.1729 | 1163140.8043 | 2570938.0925 | 1163140.1836
5 | 2570936.1729 | 1163140.8043 | 2570942.3015 | 1163164.3729
6 | 2570901.3389 | 1163223.3707 | 2570902.2282 | 1163226.5032
7 | 2570918.0248 | 1163111.9777 | 2570923.6697 | 1163110.3273 | 2570926.2081 | 1163118.8304 | 2570938.0828 | 1163116.0825 | 2570939.0566 | 1163119.4351 | 2570933.7491 | 1163121.1728 | 2570938.0925 | 1163140.1836
8 | 2570938.0925 | 1163140.1836 | 2570966.1362 | 1163131.1245
9 | 2570942.3015 | 1163164.3729 | 2570946.3803 | 1163180.0586
10 | 2570903.334 | 1163230.398 | 2570902.2282 | 1163226.5032
11 | 2570903.334 | 1163230.398 | 2570904.4906 | 1163235.1392 | 2570905.6472 | 1163239.8693 | 2570906.8743 | 1163244.9104 | 2570913.0454 | 1163257.0088
12 | 2570913.0454 | 1163257.0088 | 2570920.1112 | 1163267.213 | 2570921.1422 | 1163270.9797
13 | 2570934.8102 | 1163320.9133 | 2570921.1422 | 1163270.9797
14 | 2570918.0248 | 1163111.9777 | 2570914.377 | 1163098.8834
15 | 2570983.1365 | 1163125.2911 | 2570978.2359 | 1163127.2158 | 2570966.1362 | 1163131.1245
16 | 2570950.4177 | 1163195.5852 | 2570946.3803 | 1163180.0586
17 | 2570934.8102 | 1163320.9133 | 2570945.4998 | 1163320.2723 | 2570954.7181 | 1163320.0429
18 | 2570978.2405 | 1163319.4577 | 2570954.7181 | 1163320.0429
19 | 2570925.7285 | 1163073.6765 | 2570934.0064 | 1163072.5892
20 | 2570936.7135 | 1163072.2336 | 2570934.0064 | 1163072.5892
21 | 2570914.2517 | 1163098.4336 | 2570919.4183 | 1163096.0851 | 2570916.0156 | 1163084.6848 | 2570927.9878 | 1163081.4806 | 2570925.7285 | 1163073.6765
22 | 2570973.388 | 1163067.2867 | 2570967.586 | 1163068.1597 | 2570963.8503 | 1163068.6447 | 2570947.706 | 1163070.7796 | 2570936.7135 | 1163072.2336
23 | 2570914.377 | 1163098.8834 | 2570914.2517 | 1163098.4336
24 | 2570973.388 | 1163067.2867 | 2570973.8684 | 1163070.0977
25 | 2570983.1365 | 1163125.2911 | 2571001.6213 | 1163120.8772 | 2571014.8242 | 1163118.7567 | 2571017.1851 | 1163146.0147 | 2571024.4746 | 1163145.468
26 | 2570993.502 | 1163277.5181 | 2570992.9649 | 1163258.3332 | 2570992.386 | 1163250.9846
27 | 2570993.502 | 1163277.5181 | 2570994.5608 | 1163282.8141
28 | 2571002.4151 | 1163311.7701 | 2570997.372 | 1163296.887 | 2570996.6969 | 1163293.4996 | 2570994.5608 | 1163282.8141
29 | 2571024.4746 | 1163145.468 | 2571041.1293 | 1163144.3237
30 | 2571024.4746 | 1163145.468 | 2571026.1241 | 1163166.4078
31 | 2571006.5265 | 1163314.5628 | 2571004.6267 | 1163312.9378 | 2571002.4151 | 1163311.7701
32 | 2570978.2405 | 1163319.4577 | 2570987.0556 | 1163319.2482 | 2570989.0132 | 1163315.4146 | 2570992.2547 | 1163312.5641 | 2570997.2411 | 1163310.9836 | 2571002.4151 | 1163311.7701
33 | 2571006.5265 | 1163314.5628 | 2571008.3 | 1163316.9999 | 2571009.3707 | 1163319.8183 | 2571018.5541 | 1163327.6557 | 2571039.5593 | 1163344.0513
34 | 2571006.5265 | 1163314.5628 | 2571008.3 | 1163316.9999 | 2571009.3707 | 1163319.8183 | 2571009.6042 | 1163323.7525 | 2571008.4965 | 1163327.5265 | 2571006.1757 | 1163330.706 | 2571006.6744 | 1163340.364 | 2571006.8442 | 1163351.7134 | 2571006.9747 | 1163372.3454
35 | 2571006.5265 | 1163314.5628 | 2571016.6367 | 1163306.5542 | 2571018.8389 | 1163304.5509
36 | 2571039.5593 | 1163344.0513 | 2571045.0063 | 1163349.0386 | 2571063.5017 | 1163365.9801 | 2571065.5978 | 1163367.8974
37 | 2571006.9747 | 1163372.3454 | 2571009.1726 | 1163388.8556
38 | 2571043.9461 | 1163284.9891 | 2571034.9544 | 1163289.8906 | 2571018.8389 | 1163304.5509
39 | 2571027.5349 | 1163184.3174 | 2571026.1241 | 1163166.4078
40 | 2571043.9461 | 1163284.9891 | 2571052.9173 | 1163282.1999 | 2571060.5033 | 1163281.2183 | 2571065.8043 | 1163281.8659
41 | 2571043.9461 | 1163284.9891 | 2571041.6064 | 1163260.3568
42 | 2571067.8643 | 1163186.0901 | 2571067.4409 | 1163180.9006
43 | 2571067.4409 | 1163180.9006 | 2571045.6109 | 1163182.7697
44 | 2571067.8643 | 1163186.0901 | 2571085.0992 | 1163184.7236
45 | 2571027.5349 | 1163184.3174 | 2571045.6109 | 1163182.7697
46 | 2571027.5349 | 1163184.3174 | 2571029.5384 | 1163209.7403
47 | 2571100.6163 | 1163289.0954 | 2571098.7192 | 1163267.3713
48 | 2571070.482 | 1163282.4374 | 2571074.0535 | 1163282.876 | 2571100.6163 | 1163289.0954
49 | 2571070.482 | 1163282.4374 | 2571065.8043 | 1163281.8659
50 | 2571029.5384 | 1163209.7403 | 2571029.8443 | 1163213.6211 | 2571030.571 | 1163216.5857 | 2571031.6154 | 1163218.7262 | 2571034.6034 | 1163220.4571 | 2571037.6884 | 1163221.665 | 2571040.769 | 1163221.9614 | 2571048.5075 | 1163221.412
51 | 2571070.9828 | 1163224.3722 | 2571068.7218 | 1163224.083 | 2571066.1499 | 1163222.8615 | 2571062.7484 | 1163221.1437 | 2571059.2532 | 1163220.6492 | 2571048.5075 | 1163221.412
52 | 2571070.9828 | 1163224.3722 | 2571088.4964 | 1163223.0237
53 | 2571041.2187 | 1163256.276 | 2571041.6064 | 1163260.3568

## bus_geodata
| x | y | coords
0 | 2570897.6125 | 1163151.8992
1 | 2570909.3947 | 1163148.5091
2 | 2570883.7078 | 1163155.9
3 | 2570936.1729 | 1163140.8043
4 | 2570901.3389 | 1163223.3707
5 | 2570938.0925 | 1163140.1836
6 | 2570942.3015 | 1163164.3729
7 | 2570902.2282 | 1163226.5032
8 | 2570903.334 | 1163230.398
9 | 2570913.0454 | 1163257.0088
10 | 2570921.1422 | 1163270.9797
11 | 2570918.0248 | 1163111.9777
12 | 2570966.1362 | 1163131.1245
13 | 2570946.3803 | 1163180.0586
14 | 2570934.8102 | 1163320.9133
15 | 2570954.7181 | 1163320.0429
16 | 2570934.0064 | 1163072.5892
17 | 2570925.7285 | 1163073.6765
18 | 2570936.7135 | 1163072.2336
19 | 2570914.2517 | 1163098.4336
20 | 2570973.388 | 1163067.2867
21 | 2570914.377 | 1163098.8834
22 | 2570973.8684 | 1163070.0977
23 | 2570983.1365 | 1163125.2911
24 | 2570992.386 | 1163250.9846
25 | 2570993.502 | 1163277.5181
26 | 2570994.5608 | 1163282.8141
27 | 2571024.4746 | 1163145.468
28 | 2571002.4151 | 1163311.7701
29 | 2570978.2405 | 1163319.4577
30 | 2571006.5265 | 1163314.5627
31 | 2571039.5593 | 1163344.0513
32 | 2571006.9747 | 1163372.3454
33 | 2571018.8389 | 1163304.5509
34 | 2571009.1726 | 1163388.8556
35 | 2571065.5978 | 1163367.8974
36 | 2571041.1293 | 1163144.3237
37 | 2571026.1241 | 1163166.4078
38 | 2571043.9461 | 1163284.9891
39 | 2571067.4409 | 1163180.9006
40 | 2571067.8643 | 1163186.0901
41 | 2571045.6109 | 1163182.7697
42 | 2571027.5349 | 1163184.3174
43 | 2571100.6163 | 1163289.0954
44 | 2571098.7192 | 1163267.3713
45 | 2571070.482 | 1163282.4374
46 | 2571085.0992 | 1163184.7236
47 | 2571029.5384 | 1163209.7403
48 | 2571048.5075 | 1163221.412
49 | 2571070.9828 | 1163224.3722
50 | 2571088.4964 | 1163223.0237
51 | 2571065.8043 | 1163281.8659
52 | 2571041.2187 | 1163256.276
53 | 2571041.6064 | 1163260.3568
54 | 2570950.4177 | 1163195.5852
55 | 2570936.1729 | 1163140.8043

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9927 | -0.13896 | 0.0034599 | 0.00086714
1 | 0.99307 | -0.13193 | 0.065082 | 0.016311
2 | 0.99228 | -0.14705 | 0 | 0
3 | 0.99432 | -0.10796 | 0 | 0
4 | 0.99023 | -0.18613 | 0 | 0
5 | 0.99422 | -0.11001 | 0 | 0
6 | 0.99671 | -0.062332 | 0.011283 | 0.0028279
7 | 0.99014 | -0.18796 | 0.011241 | 0.0028172
8 | 0.99003 | -0.19003 | 0 | 0
9 | 0.98926 | -0.20463 | 0 | 0
10 | 0.98883 | -0.213 | 0.0055748 | 0.0013972
11 | 0.99001 | -0.19124 | 0 | 0
12 | 0.99321 | -0.12934 | 0.003193 | 0.00080023
13 | 0.99835 | -0.031285 | 0.009333 | 0.0023391
14 | 0.98619 | -0.26367 | 0 | 0
15 | 0.98416 | -0.30287 | 0.0046566 | 0.0011671
16 | 0.98858 | -0.21906 | 0.0067437 | 0.0016901
17 | 0.98865 | -0.21767 | 0 | 0
18 | 0.98857 | -0.21919 | 0 | 0
19 | 0.98898 | -0.2113 | 0 | 0
20 | 0.98848 | -0.22092 | 0 | 0
21 | 0.98898 | -0.21123 | 0.073247 | 0.018357
22 | 0.98848 | -0.22105 | 0.002622 | 0.00065714
23 | 0.9926 | -0.1409 | 0 | 0
24 | 0.97829 | -0.4173 | 0.0085338 | 0.0021388
25 | 0.9785 | -0.41317 | 0 | 0
26 | 0.97854 | -0.41233 | 0.013235 | 0.003317
27 | 0.98811 | -0.22755 | 0 | 0
28 | 0.97915 | -0.40042 | 0 | 0
29 | 0.98187 | -0.34738 | 0 | 0
30 | 0.97876 | -0.40797 | 0 | 0
31 | 0.97859 | -0.41138 | 0 | 0
32 | 0.9785 | -0.41315 | 0 | 0
33 | 0.97766 | -0.4294 | 0.0009414 | 0.00023594
34 | 0.97842 | -0.4146 | 0.0047834 | 0.0011988
35 | 0.97845 | -0.41407 | 0.0041871 | 0.0010494
36 | 0.98769 | -0.23565 | 0.027178 | 0.0068115
37 | 0.98581 | -0.27199 | 0.019554 | 0.0049007
38 | 0.97548 | -0.47223 | 0 | 0
39 | 0.98333 | -0.32049 | 0 | 0
40 | 0.98325 | -0.32201 | 0 | 0
41 | 0.98365 | -0.31412 | 0.015281 | 0.0038298
42 | 0.98418 | -0.30385 | 0 | 0
43 | 0.9743 | -0.49554 | 0 | 0
44 | 0.97387 | -0.50399 | 0.021093 | 0.0052864
45 | 0.9749 | -0.48362 | 0 | 0
46 | 0.98299 | -0.32704 | 0.016145 | 0.0040464
47 | 0.98259 | -0.33477 | 0.027153 | 0.0068052
48 | 0.98159 | -0.35431 | 0.021035 | 0.005272
49 | 0.98118 | -0.36234 | 0 | 0
50 | 0.98087 | -0.36841 | 0.019087 | 0.0047838
51 | 0.975 | -0.4818 | 0.0022251 | 0.00055766
52 | 0.97421 | -0.49739 | 0.033806 | 0.0084725
53 | 0.97433 | -0.49485 | 0.016049 | 0.0040221
54 | 1 | 0 | -0.45457 | -0.1159
55 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.13157 | -0.033653 | 0.13161 | 0.033681 | 4.4813e-05 | 2.8046e-05 | 0.19745 | 0.19745 | 0.19745 | 0.9927 | -0.13896 | 0.99307 | -0.13193 | 13.5615
1 | 0.12811 | 0.032786 | -0.12806 | -0.032755 | 5.0144e-05 | 3.1344e-05 | 0.19227 | 0.19227 | 0.19227 | 0.9927 | -0.13896 | 0.99228 | -0.14705 | 13.2053
2 | -0.19669 | -0.049992 | 0.19692 | 0.050136 | 0.00022729 | 0.00014402 | 0.29497 | 0.29497 | 0.29497 | 0.99307 | -0.13193 | 0.99432 | -0.10796 | 20.2591
3 | 0.12806 | 0.032755 | -0.12781 | -0.032604 | 0.0002417 | 0.00015109 | 0.19227 | 0.19227 | 0.19227 | 0.99228 | -0.14705 | 0.99023 | -0.18613 | 13.2054
4 | 0.23309 | 0.059126 | -0.23306 | -0.059112 | 2.2984e-05 | 1.4605e-05 | 0.34907 | 0.34907 | 0.34907 | 0.99432 | -0.10796 | 0.99422 | -0.11001 | 23.9744
5 | -0.43001 | -0.10926 | 0.43095 | 0.10987 | 0.00094697 | 0.00060479 | 0.64404 | 0.64404 | 0.64404 | 0.99432 | -0.10796 | 0.99671 | -0.062332 | 44.2334
6 | 0.12781 | 0.032604 | -0.1278 | -0.032596 | 1.1285e-05 | 7.055e-06 | 0.19227 | 0.19227 | 0.19227 | 0.99023 | -0.18613 | 0.99014 | -0.18796 | 13.2054
7 | 0.083016 | 0.020961 | -0.082695 | -0.020756 | 0.0003217 | 0.00020517 | 0.1243 | 0.1243 | 0.1243 | 0.99422 | -0.11001 | 0.99001 | -0.19124 | 34.1494
8 | 0.15005 | 0.03815 | -0.14991 | -0.038063 | 0.00013958 | 8.7802e-05 | 0.22476 | 0.22476 | 0.22476 | 0.99422 | -0.11001 | 0.99321 | -0.12934 | 15.4371
9 | -0.44224 | -0.11269 | 0.4429 | 0.11312 | 0.00066364 | 0.00042388 | 0.66088 | 0.66088 | 0.66088 | 0.99671 | -0.062332 | 0.99835 | -0.031285 | 45.3903
10 | 0.11656 | 0.029779 | -0.11655 | -0.029772 | 1.1674e-05 | 7.2633e-06 | 0.17538 | 0.17538 | 0.17538 | 0.99014 | -0.18796 | 0.99003 | -0.19003 | 12.0451
11 | 0.11655 | 0.029772 | -0.11647 | -0.029721 | 8.2235e-05 | 5.1165e-05 | 0.17538 | 0.17538 | 0.17538 | 0.99003 | -0.19003 | 0.98926 | -0.20463 | 12.0452
12 | 0.11647 | 0.029721 | -0.11642 | -0.029692 | 4.705e-05 | 2.9274e-05 | 0.17538 | 0.17538 | 0.17538 | 0.98926 | -0.20463 | 0.98883 | -0.213 | 12.0452
13 | 0.11085 | 0.028294 | -0.11058 | -0.028122 | 0.00027068 | 0.00017191 | 0.16699 | 0.16699 | 0.16699 | 0.98883 | -0.213 | 0.98619 | -0.26367 | 22.9381
14 | 0.082695 | 0.020756 | -0.082616 | -0.020706 | 7.8761e-05 | 5.0233e-05 | 0.1243 | 0.1243 | 0.1243 | 0.99001 | -0.19124 | 0.98898 | -0.21123 | 34.1494
15 | 0.14671 | 0.037262 | -0.14663 | -0.037211 | 8.1572e-05 | 5.1276e-05 | 0.21998 | 0.21998 | 0.21998 | 0.99321 | -0.12934 | 0.9926 | -0.1409 | 15.1086
16 | -0.45223 | -0.11546 | 0.45292 | 0.1159 | 0.00068485 | 0.00043746 | 0.67479 | 0.67479 | 0.67479 | 0.99835 | -0.031285 | 1 | 0 | 46.3457
17 | 0.11058 | 0.028122 | -0.11037 | -0.027989 | 0.00020841 | 0.00013313 | 0.16699 | 0.16699 | 0.16699 | 0.98619 | -0.26367 | 0.98416 | -0.30287 | 45.8762
18 | 0.10571 | 0.026822 | -0.10549 | -0.026678 | 0.00022574 | 0.00014418 | 0.15995 | 0.15995 | 0.15995 | 0.98416 | -0.30287 | 0.98187 | -0.34738 | 43.942
19 | -0.009366 | -0.0023469 | 0.0093666 | 0.0023472 | 6.2223e-07 | 2.9118e-07 | 0.014098 | 0.014098 | 0.014098 | 0.98858 | -0.21906 | 0.98865 | -0.21767 | 3.873
20 | 0.0026223 | 0.00065675 | -0.0026222 | -0.00065678 | 1.595e-08 | -2.4798e-08 | 0.0039469 | 0.0039469 | 0.0039469 | 0.98858 | -0.21906 | 0.98857 | -0.21919 | 1.0843
21 | -0.0093666 | -0.0023472 | 0.0093694 | 0.0023485 | 2.8388e-06 | 1.3282e-06 | 0.014098 | 0.014097 | 0.014098 | 0.98865 | -0.21767 | 0.98898 | -0.2113 | 3.8729
22 | 0.0026222 | 0.00065678 | -0.002622 | -0.00065711 | 2.162e-07 | -3.3607e-07 | 0.0039469 | 0.0039471 | 0.0039471 | 0.98857 | -0.21919 | 0.98848 | -0.22092 | 1.0844
23 | -0.0093694 | -0.0023485 | 0.0093695 | 0.0023485 | 3.4799e-08 | 1.628e-08 | 0.014097 | 0.014097 | 0.014097 | 0.98898 | -0.2113 | 0.98898 | -0.21123 | 3.8729
24 | 0.002622 | 0.00065711 | -0.002622 | -0.00065714 | 1.6661e-08 | -2.5893e-08 | 0.0039471 | 0.0039471 | 0.0039471 | 0.98848 | -0.22092 | 0.98848 | -0.22105 | 1.0844
25 | 0.14663 | 0.037211 | -0.14602 | -0.036823 | 0.00060834 | 0.00038761 | 0.21998 | 0.21998 | 0.21998 | 0.9926 | -0.1409 | 0.98811 | -0.22755 | 30.2172
26 | -0.0085338 | -0.0021388 | 0.0085355 | 0.0021395 | 1.6784e-06 | 7.4055e-07 | 0.01298 | 0.01298 | 0.01298 | 0.97829 | -0.4173 | 0.9785 | -0.41317 | 3.566
27 | -0.0085355 | -0.0021395 | 0.0085358 | 0.0021397 | 3.4123e-07 | 1.5055e-07 | 0.01298 | 0.01298 | 0.01298 | 0.9785 | -0.41317 | 0.97854 | -0.41233 | 3.566
28 | -0.021771 | -0.0054566 | 0.021783 | 0.0054642 | 1.2357e-05 | 7.5303e-06 | 0.033106 | 0.033106 | 0.033106 | 0.97854 | -0.41233 | 0.97915 | -0.40042 | 9.095
29 | 0.027189 | 0.006818 | -0.027178 | -0.0068115 | 1.0496e-05 | 6.5034e-06 | 0.040946 | 0.040946 | 0.040946 | 0.98811 | -0.22755 | 0.98769 | -0.23565 | 11.2488
30 | 0.11883 | 0.030005 | -0.11858 | -0.029844 | 0.00025248 | 0.00016132 | 0.17904 | 0.17904 | 0.17904 | 0.98811 | -0.22755 | 0.98581 | -0.27199 | 49.1857
31 | 0.083434 | 0.021043 | -0.083404 | -0.021024 | 3.0113e-05 | 1.921e-05 | 0.12684 | 0.12684 | 0.12684 | 0.97915 | -0.40042 | 0.97876 | -0.40797 | 34.8471
32 | -0.10522 | -0.026507 | 0.10549 | 0.026678 | 0.0002677 | 0.00017097 | 0.15995 | 0.15995 | 0.15995 | 0.97915 | -0.40042 | 0.98187 | -0.34738 | 43.942
33 | 0.0041884 | 0.0010492 | -0.0041877 | -0.0010493 | 6.8038e-07 | -1.2686e-07 | 0.0063674 | 0.0063676 | 0.0063676 | 0.97876 | -0.40797 | 0.97859 | -0.41138 | 1.7493
34 | 0.0047849 | 0.0011988 | -0.0047837 | -0.0011988 | 1.1806e-06 | 8.0982e-09 | 0.0072744 | 0.0072747 | 0.0072747 | 0.97876 | -0.40797 | 0.9785 | -0.41315 | 1.9985
35 | 0.074431 | 0.018776 | -0.074355 | -0.018727 | 7.6287e-05 | 4.8624e-05 | 0.1132 | 0.1132 | 0.1132 | 0.97876 | -0.40797 | 0.97766 | -0.4294 | 31.0994
36 | 0.0041877 | 0.0010493 | -0.0041871 | -0.0010494 | 5.3686e-07 | -9.9932e-08 | 0.0063676 | 0.0063678 | 0.0063678 | 0.97859 | -0.41138 | 0.97845 | -0.41407 | 1.7494
37 | 0.0047837 | 0.0011988 | -0.0047834 | -0.0011988 | 3.3055e-07 | 2.3493e-09 | 0.0072747 | 0.0072748 | 0.0072748 | 0.9785 | -0.41315 | 0.97842 | -0.4146 | 1.9986
38 | 0.073413 | 0.018491 | -0.073263 | -0.018396 | 0.00015003 | 9.5621e-05 | 0.11177 | 0.11177 | 0.11177 | 0.97766 | -0.4294 | 0.97548 | -0.47223 | 30.7058
39 | 0.099028 | 0.024943 | -0.098878 | -0.024847 | 0.00015061 | 9.6163e-05 | 0.14952 | 0.14952 | 0.14952 | 0.98581 | -0.27199 | 0.98418 | -0.30385 | 41.0771
40 | 0.023351 | 0.0058642 | -0.02334 | -0.0058576 | 1.0653e-05 | 6.5386e-06 | 0.035624 | 0.035624 | 0.035624 | 0.97548 | -0.47223 | 0.975 | -0.4818 | 9.7869
41 | 0.049912 | 0.012531 | -0.049858 | -0.012497 | 5.3798e-05 | 3.4122e-05 | 0.076145 | 0.076145 | 0.076145 | 0.97548 | -0.47223 | 0.97433 | -0.49485 | 20.9189
42 | 0.01615 | 0.0040493 | -0.016149 | -0.0040487 | 1.1666e-06 | 6.8054e-07 | 0.02444 | 0.02444 | 0.02444 | 0.98333 | -0.32049 | 0.98325 | -0.32201 | 6.7143
43 | -0.01615 | -0.0040493 | 0.016155 | 0.0040522 | 4.9077e-06 | 2.8629e-06 | 0.02444 | 0.02444 | 0.02444 | 0.98333 | -0.32049 | 0.98365 | -0.31412 | 6.7143
44 | 0.016149 | 0.0040487 | -0.016145 | -0.0040464 | 3.8727e-06 | 2.2593e-06 | 0.02444 | 0.02444 | 0.02444 | 0.98325 | -0.32201 | 0.98299 | -0.32704 | 6.7143
45 | -0.031436 | -0.007882 | 0.031452 | 0.0078917 | 1.5387e-05 | 9.617e-06 | 0.047557 | 0.047557 | 0.047557 | 0.98365 | -0.31412 | 0.98418 | -0.30385 | 13.065
46 | 0.067426 | 0.016956 | -0.067326 | -0.016892 | 9.9425e-05 | 6.3308e-05 | 0.10196 | 0.10196 | 0.10196 | 0.98418 | -0.30385 | 0.98259 | -0.33477 | 28.0121
47 | 0.021102 | 0.0052916 | -0.021093 | -0.0052864 | 8.496e-06 | 5.1659e-06 | 0.032229 | 0.032229 | 0.032229 | 0.9743 | -0.49554 | 0.97387 | -0.50399 | 8.8541
48 | -0.021102 | -0.0052916 | 0.021114 | 0.0052989 | 1.1995e-05 | 7.293e-06 | 0.032229 | 0.032229 | 0.032229 | 0.9743 | -0.49554 | 0.9749 | -0.48362 | 8.8541
49 | -0.021114 | -0.0052989 | 0.021115 | 0.0053 | 1.8355e-06 | 1.116e-06 | 0.032229 | 0.032229 | 0.032229 | 0.9749 | -0.48362 | 0.975 | -0.4818 | 8.854
50 | 0.040173 | 0.010087 | -0.040136 | -0.010063 | 3.7407e-05 | 2.36e-05 | 0.060844 | 0.060844 | 0.060844 | 0.98259 | -0.33477 | 0.98159 | -0.35431 | 16.7154
51 | 0.0191 | 0.0047915 | -0.019093 | -0.0047871 | 7.3072e-06 | 4.3829e-06 | 0.028956 | 0.028956 | 0.028956 | 0.98159 | -0.35431 | 0.98118 | -0.36234 | 7.955
52 | 0.019093 | 0.0047871 | -0.019087 | -0.0047838 | 5.523e-06 | 3.3129e-06 | 0.028956 | 0.028956 | 0.028956 | 0.98118 | -0.36234 | 0.98087 | -0.36841 | 7.955
53 | -0.033806 | -0.0084725 | 0.03381 | 0.0084751 | 4.0985e-06 | 2.572e-06 | 0.051635 | 0.051635 | 0.051635 | 0.97421 | -0.49739 | 0.97433 | -0.49485 | 14.1855

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.53666 | 0.13647

## res_load
| p_mw | q_mvar
0 | 0.0034599 | 0.00086714
1 | 0.065082 | 0.016311
2 | 0.011283 | 0.0028279
3 | 0.011241 | 0.0028172
4 | 0.0055748 | 0.0013972
5 | 0.003193 | 0.00080023
6 | 0.009333 | 0.0023391
7 | 0.0046566 | 0.0011671
8 | 0.0067437 | 0.0016901
9 | 0.073247 | 0.018357
10 | 0.002622 | 0.00065714
11 | 0.0085338 | 0.0021388
12 | 0.013235 | 0.003317
13 | 0.0009414 | 0.00023594
14 | 0.0047834 | 0.0011988
15 | 0.0041871 | 0.0010494
16 | 0.027178 | 0.0068115
17 | 0.019554 | 0.0049007
18 | 0.015281 | 0.0038298
19 | 0.021093 | 0.0052864
20 | 0.016145 | 0.0040464
21 | 0.027153 | 0.0068052
22 | 0.021035 | 0.005272
23 | 0.019087 | 0.0047838
24 | 0.0022251 | 0.00055766
25 | 0.033806 | 0.0084725
26 | 0.016049 | 0.0040221
27 | 0.082097 | 0.020575

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1