## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2148-2_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2148-2_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2148-2_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_2148-2_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_2148-2_0_4_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_2148-2_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_2148-2_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_2148-2_0_4_node_36 | 0.4 | n |  | TRUE
8 | bus_LV_2148-2_0_4_node_38 | 0.4 | n |  | TRUE
9 | bus_LV_2148-2_0_4_node_35 | 0.4 | n |  | TRUE
10 | bus_LV_2148-2_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_2148-2_0_4_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_2148-2_0_4_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_2148-2_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_2148-2_0_4_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_2148-2_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_2148-2_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_2148-2_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_2148-2_0_4_node_77 | 0.4 | n |  | TRUE
19 | bus_LV_2148-2_0_4_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_2148-2_0_4_node_78 | 0.4 | n |  | TRUE
21 | bus_LV_2148-2_0_4_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_2148-2_0_4_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_2148-2_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_2148-2_0_4_node_25 | 0.4 | n |  | TRUE
25 | bus_LV_2148-2_0_4_node_24 | 0.4 | n |  | TRUE
26 | bus_LV_2148-2_0_4_node_32 | 0.4 | n |  | TRUE
27 | bus_LV_2148-2_0_4_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2148-2_0_4_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2148-2_0_4_node_70 | 0.4 | n |  | TRUE
30 | bus_LV_2148-2_0_4_node_69 | 0.4 | n |  | TRUE
31 | bus_LV_2148-2_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_2148-2_0_4_node_97 | 0.4 | n |  | TRUE
33 | bus_LV_2148-2_0_4_node_39 | 0.4 | n |  | TRUE
34 | bus_LV_2148-2_0_4_node_59 | 0.4 | n |  | TRUE
35 | bus_LV_2148-2_0_4_node_60 | 0.4 | n |  | TRUE
36 | bus_LV_2148-2_0_4_node_29 | 0.4 | n |  | TRUE
37 | bus_LV_2148-2_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_2148-2_0_4_node_112 | 0.4 | n |  | TRUE
39 | bus_LV_2148-2_0_4_node_113 | 0.4 | n |  | TRUE
40 | bus_LV_2148-2_0_4_node_110 | 0.4 | n |  | TRUE
41 | bus_LV_2148-2_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_2148-2_0_4_node_26 | 0.4 | n |  | TRUE
43 | bus_LV_2148-2_0_4_node_28 | 0.4 | n |  | TRUE
44 | bus_LV_2148-2_0_4_node_30 | 0.4 | n |  | TRUE
45 | bus_LV_2148-2_0_4_node_65 | 0.4 | n |  | TRUE
46 | bus_LV_2148-2_0_4_node_66 | 0.4 | n |  | TRUE
47 | bus_LV_2148-2_0_4_node_34 | 0.4 | n |  | TRUE
48 | bus_LV_2148-2_0_4_node_67 | 0.4 | n |  | TRUE
49 | bus_LV_2148-2_0_4_node_68 | 0.4 | n |  | TRUE
50 | bus_LV_2148-2_0_4_node_52 | 0.4 | n |  | TRUE
51 | bus_LV_2148-2_0_4_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_2148-2_0_4_node_106 | 0.4 | n |  | TRUE
53 | bus_LV_2148-2_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_2148-2_0_4_node_41 | 0.4 | n |  | TRUE
55 | bus_LV_2148-2_0_4_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_2148-2_0_4_node_98 | 0.4 | n |  | TRUE
57 | bus_LV_2148-2_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_2148-2_0_4_node_43 | 0.4 | n |  | TRUE
59 | bus_LV_2148-2_0_4_node_44 | 0.4 | n |  | TRUE
60 | bus_LV_2148-2_0_4_node_46 | 0.4 | n |  | TRUE
61 | bus_LV_2148-2_0_4_node_63 | 0.4 | n |  | TRUE
62 | bus_LV_2148-2_0_4_node_72 | 0.4 | n |  | TRUE
63 | bus_LV_2148-2_0_4_node_61 | 0.4 | n |  | TRUE
64 | bus_LV_2148-2_0_4_node_73 | 0.4 | n |  | TRUE
65 | bus_LV_2148-2_0_4_node_47 | 0.4 | n |  | TRUE
66 | bus_LV_2148-2_0_4_node_48 | 0.4 | n |  | TRUE
67 | bus_LV_2148-2_0_4_node_49 | 0.4 | n |  | TRUE
68 | bus_LV_2148-2_0_4_node_50 | 0.4 | n |  | TRUE
69 | bus_LV_2148-2_0_4_node_51 | 0.4 | n |  | TRUE
70 | bus_LV_2148-2_0_4_node_58 | 0.4 | n |  | TRUE
71 | bus_LV_2148-2_0_4_node_71 | 0.4 | n |  | TRUE
72 | bus_LV_2148-2_0_4_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_2148-2_0_4_node_105 | 0.4 | n |  | TRUE
74 | bus_LV_2148-2_0_4_node_54 | 0.4 | n |  | TRUE
75 | bus_LV_2148-2_0_4_node_55 | 0.4 | n |  | TRUE
76 | bus_LV_2148-2_0_4_node_57 | 0.4 | n |  | TRUE
77 | bus_LV_2148-2_0_4_node_107 | 0.4 | n |  | TRUE
78 | bus_LV_2148-2_0_4_node_108 | 0.4 | n |  | TRUE
79 | bus_LV_2148-2_0_4_node_62 | 0.4 | n |  | TRUE
80 | bus_LV_2148-2_0_4_node_64 | 0.4 | n |  | TRUE
81 | bus_LV_2148-2_0_4_node_75 | 0.4 | n |  | TRUE
82 | bus_LV_2148-2_0_4_node_91 | 0.4 | n |  | TRUE
83 | bus_LV_2148-2_0_4_node_90 | 0.4 | n |  | TRUE
84 | bus_LV_2148-2_0_4_node_74 | 0.4 | n |  | TRUE
85 | bus_LV_2148-2_0_4_node_102 | 0.4 | n |  | TRUE
86 | bus_LV_2148-2_0_4_node_103 | 0.4 | n |  | TRUE
87 | bus_LV_2148-2_0_4_node_101 | 0.4 | n |  | TRUE
88 | bus_LV_2148-2_0_4_node_79 | 0.4 | n |  | TRUE
89 | bus_LV_2148-2_0_4_node_80 | 0.4 | n |  | TRUE
90 | bus_LV_2148-2_0_4_node_81 | 0.4 | n |  | TRUE
91 | bus_LV_2148-2_0_4_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_2148-2_0_4_node_83 | 0.4 | n |  | TRUE
93 | bus_LV_2148-2_0_4_node_99 | 0.4 | n |  | TRUE
94 | bus_LV_2148-2_0_4_node_94 | 0.4 | n |  | TRUE
95 | bus_LV_2148-2_0_4_node_84 | 0.4 | n |  | TRUE
96 | bus_LV_2148-2_0_4_node_85 | 0.4 | n |  | TRUE
97 | bus_LV_2148-2_0_4_node_86 | 0.4 | n |  | TRUE
98 | bus_LV_2148-2_0_4_node_87 | 0.4 | n |  | TRUE
99 | bus_LV_2148-2_0_4_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_2148-2_0_4_node_89 | 0.4 | n |  | TRUE
101 | bus_LV_2148-2_0_4_node_95 | 0.4 | n |  | TRUE
102 | bus_LV_2148-2_0_4_node_96 | 0.4 | n |  | TRUE
103 | bus_LV_2148-2_0_4_node_104 | 0.4 | n |  | TRUE
104 | bus_LV_2148-2_0_4_node_130 | 0.4 | n |  | TRUE
105 | bus_LV_2148-2_0_4_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_2148-2_0_4_node_109 | 0.4 | n |  | TRUE
107 | bus_LV_2148-2_0_4_node_93 | 0.4 | n |  | TRUE
108 | bus_LV_2148-2_0_4_node_127 | 0.4 | n |  | TRUE
109 | bus_LV_2148-2_0_4_node_129 | 0.4 | n |  | TRUE
110 | bus_LV_2148-2_0_4_node_92 | 0.4 | n |  | TRUE
111 | bus_LV_2148-2_0_4_node_111 | 0.4 | n |  | TRUE
112 | bus_LV_2148-2_0_4_node_117 | 0.4 | n |  | TRUE
113 | bus_LV_2148-2_0_4_node_116 | 0.4 | n |  | TRUE
114 | bus_LV_2148-2_0_4_node_114 | 0.4 | n |  | TRUE
115 | bus_LV_2148-2_0_4_node_115 | 0.4 | n |  | TRUE
116 | bus_LV_2148-2_0_4_node_120 | 0.4 | n |  | TRUE
117 | bus_LV_2148-2_0_4_node_121 | 0.4 | n |  | TRUE
118 | bus_LV_2148-2_0_4_node_118 | 0.4 | n |  | TRUE
119 | bus_LV_2148-2_0_4_node_119 | 0.4 | n |  | TRUE
120 | bus_LV_2148-2_0_4_node_128 | 0.4 | n |  | TRUE
121 | bus_LV_2148-2_0_4_node_122 | 0.4 | n |  | TRUE
122 | bus_LV_2148-2_0_4_node_123 | 0.4 | n |  | TRUE
123 | bus_LV_2148-2_0_4_node_125 | 0.4 | n |  | TRUE
124 | bus_LV_2148-2_0_4_node_124 | 0.4 | n |  | TRUE
125 | bus_LV_2148-2_0_4_node_126 | 0.4 | n |  | TRUE
126 | bus_LV_2148-2_0_4_node_131 | 0.4 | n |  | TRUE
127 | bus_MV_31_0_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2148-2_0_4_load_0 | 0 | 0.007831 | 0.0019626 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2148-2_0_4_load_1 | 1 | 0.011221 | 0.0028124 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2148-2_0_4_load_9 | 5 | 0.0058971 | 0.001478 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2148-2_0_4_load_5 | 6 | 0.0056786 | 0.0014232 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2148-2_0_4_load_36 | 7 | 0.0087481 | 0.0021925 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2148-2_0_4_load_35 | 9 | 0.0043315 | 0.0010856 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2148-2_0_4_load_18 | 10 | 0.006074 | 0.0015223 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2148-2_0_4_load_19 | 11 | 0.0092445 | 0.0023169 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2148-2_0_4_load_4 | 12 | 0.010893 | 0.0027301 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2148-2_0_4_load_20 | 13 | 0.0074936 | 0.0018781 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2148-2_0_4_load_37 | 14 | 0.0047807 | 0.0011981 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2148-2_0_4_load_6 | 15 | 0.0014791 | 0.00037069 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2148-2_0_4_load_8 | 16 | 0.0053759 | 0.0013473 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2148-2_0_4_load_14 | 17 | 0.0038864 | 0.00097401 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2148-2_0_4_load_77 | 18 | 0.0044741 | 0.0011213 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2148-2_0_4_load_78 | 20 | 0.0065058 | 0.0016305 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2148-2_0_4_load_10 | 21 | 0.0074588 | 0.0018694 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2148-2_0_4_load_11 | 22 | 0.0056502 | 0.0014161 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2148-2_0_4_load_25 | 24 | 0.0041741 | 0.0010461 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2148-2_0_4_load_24 | 25 | 0.0036236 | 0.00090816 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2148-2_0_4_load_16 | 27 | 0.0053368 | 0.0013375 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2148-2_0_4_load_17 | 28 | 0.005307 | 0.0013301 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2148-2_0_4_load_70 | 29 | 0.0043809 | 0.001098 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2148-2_0_4_load_21 | 31 | 0.0085204 | 0.0021354 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2148-2_0_4_load_97 | 32 | 0.0081356 | 0.002039 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2148-2_0_4_load_39 | 33 | 0.0025854 | 0.00064797 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2148-2_0_4_load_59 | 34 | 0.010237 | 0.0025657 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2148-2_0_4_load_60 | 35 | 0.0073849 | 0.0018508 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2148-2_0_4_load_29 | 36 | 0.0068776 | 0.0017237 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2148-2_0_4_load_27 | 37 | 0.0043687 | 0.0010949 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2148-2_0_4_load_113 | 39 | 0.0040904 | 0.0010251 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2148-2_0_4_load_110 | 40 | 0.0067429 | 0.0016899 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2148-2_0_4_load_31 | 41 | 0.0061891 | 0.0015511 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2148-2_0_4_load_26 | 42 | 0.0088842 | 0.0022266 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2148-2_0_4_load_28 | 43 | 0.0034481 | 0.00086418 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2148-2_0_4_load_30 | 44 | 0.0021836 | 0.00054725 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2148-2_0_4_load_65 | 45 | 0.0030393 | 0.00076173 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2148-2_0_4_load_34 | 47 | 0.0048232 | 0.0012088 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2148-2_0_4_load_67 | 48 | 0.0046606 | 0.0011681 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2148-2_0_4_load_68 | 49 | 0.0038633 | 0.00096823 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2148-2_0_4_load_52 | 50 | 0.0045011 | 0.0011281 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2148-2_0_4_load_53 | 51 | 0.0054874 | 0.0013753 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2148-2_0_4_load_106 | 52 | 0.0042978 | 0.0010771 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2148-2_0_4_load_40 | 53 | 0.0049481 | 0.0012401 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2148-2_0_4_load_41 | 54 | 0.0055221 | 0.001384 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2148-2_0_4_load_42 | 55 | 0.0049219 | 0.0012335 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2148-2_0_4_load_98 | 56 | 0.0037881 | 0.00094938 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2148-2_0_4_load_43 | 58 | 0.0033014 | 0.00082741 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2148-2_0_4_load_63 | 61 | 0.0043129 | 0.0010809 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2148-2_0_4_load_72 | 62 | 0.0023042 | 0.00057749 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2148-2_0_4_load_61 | 63 | 0.0031205 | 0.00078206 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2148-2_0_4_load_47 | 65 | 0.0047018 | 0.0011784 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2148-2_0_4_load_48 | 66 | 0.0035205 | 0.00088231 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2148-2_0_4_load_49 | 67 | 0.0048875 | 0.0012249 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2148-2_0_4_load_50 | 68 | 0.0052746 | 0.0013219 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2148-2_0_4_load_58 | 70 | 0.0030409 | 0.00076213 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2148-2_0_4_load_71 | 71 | 0.0045968 | 0.0011521 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2148-2_0_4_load_56 | 72 | 0.002366 | 0.00059298 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2148-2_0_4_load_105 | 73 | 0.0036123 | 0.00090533 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2148-2_0_4_load_54 | 74 | 0.0023812 | 0.00059678 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2148-2_0_4_load_55 | 75 | 0.0043143 | 0.0010813 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2148-2_0_4_load_107 | 77 | 0.0031443 | 0.00078803 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2148-2_0_4_load_108 | 78 | 0.0035231 | 0.00088298 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2148-2_0_4_load_62 | 79 | 0.0055374 | 0.0013878 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2148-2_0_4_load_64 | 80 | 0.0031932 | 0.00080028 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2148-2_0_4_load_91 | 82 | 0.0036364 | 0.00091136 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2148-2_0_4_load_90 | 83 | 0.0017165 | 0.00043019 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2148-2_0_4_load_74 | 84 | 0.001607 | 0.00040276 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2148-2_0_4_load_103 | 86 | 0.0020209 | 0.00050648 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2148-2_0_4_load_101 | 87 | 0.0019714 | 0.00049408 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2148-2_0_4_load_79 | 88 | 0.0017065 | 0.00042769 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2148-2_0_4_load_80 | 89 | 0.0017237 | 0.000432 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2148-2_0_4_load_81 | 90 | 0.00149 | 0.00037343 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2148-2_0_4_load_82 | 91 | 0.0017962 | 0.00045017 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2148-2_0_4_load_83 | 92 | 0.0019267 | 0.00048287 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2148-2_0_4_load_99 | 93 | 0.0014615 | 0.00036629 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2148-2_0_4_load_94 | 94 | 0.0014626 | 0.00036656 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2148-2_0_4_load_84 | 95 | 0.002651 | 0.00066441 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2148-2_0_4_load_85 | 96 | 0.0018876 | 0.00047307 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2148-2_0_4_load_88 | 99 | 0.0022925 | 0.00057455 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2148-2_0_4_load_89 | 100 | 0.0014916 | 0.00037384 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2148-2_0_4_load_95 | 101 | 0.0041045 | 0.0010287 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2148-2_0_4_load_96 | 102 | 0.0067244 | 0.0016853 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2148-2_0_4_load_104 | 103 | 0.0013922 | 0.00034892 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2148-2_0_4_load_100 | 105 | 0.0033515 | 0.00083995 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2148-2_0_4_load_93 | 107 | 0.0014621 | 0.00036645 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2148-2_0_4_load_127 | 108 | 0.0030898 | 0.00077437 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2148-2_0_4_load_129 | 109 | 0.0015298 | 0.00038341 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2148-2_0_4_load_111 | 111 | 0.0048758 | 0.001222 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2148-2_0_4_load_116 | 113 | 0.00078544 | 0.00019685 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2148-2_0_4_load_114 | 114 | 0.0086024 | 0.002156 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2148-2_0_4_load_115 | 115 | 0.0040967 | 0.0010267 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2148-2_0_4_load_120 | 116 | 0.0019206 | 0.00048135 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2148-2_0_4_load_121 | 117 | 0.0025189 | 0.0006313 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2148-2_0_4_load_118 | 118 | 0.0019992 | 0.00050103 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2148-2_0_4_load_119 | 119 | 0.0019002 | 0.00047624 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2148-2_0_4_load_128 | 120 | 0.0017954 | 0.00044996 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2148-2_0_4_load_122 | 121 | 0.0025359 | 0.00063555 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2148-2_0_4_load_123 | 122 | 0.002582 | 0.00064712 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2148-2_0_4_load_125 | 123 | 0.0023983 | 0.00060108 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2148-2_0_4_load_124 | 124 | 0.0026685 | 0.00066878 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2148-2_0_4_load_126 | 125 | 0.00244 | 0.00061152 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2148-2_0_4_load_131 | 126 | 0.0011701 | 0.00029326 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2148-2_0_4_line_0 |  | 0 | 1 | 0.014089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2148-2_0_4_line_1 |  | 0 | 2 | 0.014304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2148-2_0_4_line_2 |  | 2 | 3 | 0.030498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2148-2_0_4_line_3 |  | 3 | 10 | 0.049104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2148-2_0_4_line_4 |  | 4 | 5 | 0.022339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2148-2_0_4_line_5 |  | 4 | 6 | 0.025445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2148-2_0_4_line_6 |  | 5 | 18 | 0.0052005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2148-2_0_4_line_7 |  | 6 | 15 | 0.0026142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2148-2_0_4_line_8 |  | 7 | 8 | 0.037737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2148-2_0_4_line_9 |  | 7 | 9 | 0.014407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2148-2_0_4_line_10 |  | 8 | 50 | 0.021944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2148-2_0_4_line_11 |  | 8 | 51 | 0.0033587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2148-2_0_4_line_12 |  | 9 | 14 | 0.0052655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_2148-2_0_4_line_13 |  | 10 | 11 | 0.047399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_2148-2_0_4_line_14 |  | 11 | 13 | 0.029436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_2148-2_0_4_line_15 |  | 11 | 12 | 0.024476 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_2148-2_0_4_line_16 |  | 13 | 31 | 0.030602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_2148-2_0_4_line_17 |  | 14 | 33 | 0.014941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2148-2_0_4_line_18 |  | 15 | 16 | 0.024139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_2148-2_0_4_line_19 |  | 16 | 17 | 0.0045868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_2148-2_0_4_line_20 |  | 17 | 19 | 0.013261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2148-2_0_4_line_21 |  | 18 | 20 | 0.021531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2148-2_0_4_line_22 |  | 19 | 27 | 0.021134 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2148-2_0_4_line_23 |  | 20 | 50 | 0.0084709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_2148-2_0_4_line_24 |  | 21 | 22 | 0.023318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_2148-2_0_4_line_25 |  | 22 | 23 | 0.019099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2148-2_0_4_line_26 |  | 23 | 24 | 0.012149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2148-2_0_4_line_27 |  | 23 | 25 | 0.018732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2148-2_0_4_line_28 |  | 24 | 26 | 0.014815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_2148-2_0_4_line_29 |  | 25 | 27 | 0.0021297 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2148-2_0_4_line_30 |  | 26 | 41 | 0.024201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2148-2_0_4_line_31 |  | 28 | 29 | 0.0021953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2148-2_0_4_line_32 |  | 29 | 30 | 0.023168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2148-2_0_4_line_33 |  | 30 | 71 | 0.015112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2148-2_0_4_line_34 |  | 30 | 68 | 0.013639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2148-2_0_4_line_35 |  | 31 | 34 | 0.020242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2148-2_0_4_line_36 |  | 32 | 33 | 0.021844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2148-2_0_4_line_37 |  | 34 | 35 | 0.00892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2148-2_0_4_line_38 |  | 34 | 36 | 0.034949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2148-2_0_4_line_39 |  | 35 | 37 | 0.031721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2148-2_0_4_line_40 |  | 37 | 42 | 0.00091277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2148-2_0_4_line_41 |  | 38 | 39 | 0.049223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2148-2_0_4_line_42 |  | 38 | 40 | 0.02049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2148-2_0_4_line_43 |  | 39 | 115 | 0.02459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2148-2_0_4_line_44 |  | 40 | 106 | 0.019872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2148-2_0_4_line_45 |  | 42 | 43 | 0.027397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2148-2_0_4_line_46 |  | 43 | 44 | 0.00043781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2148-2_0_4_line_47 |  | 44 | 45 | 0.034035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2148-2_0_4_line_48 |  | 45 | 46 | 0.014744 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2148-2_0_4_line_49 |  | 46 | 82 | 0.016237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2148-2_0_4_line_50 |  | 46 | 78 | 0.033177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
51 | LV_2148-2_0_4_line_51 |  | 47 | 48 | 0.002442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2148-2_0_4_line_52 |  | 48 | 49 | 0.033111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2148-2_0_4_line_53 |  | 49 | 81 | 0.0060776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2148-2_0_4_line_54 |  | 51 | 52 | 0.033177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2148-2_0_4_line_55 |  | 52 | 73 | 0.003782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2148-2_0_4_line_56 |  | 53 | 54 | 0.042429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2148-2_0_4_line_57 |  | 54 | 55 | 0.035515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2148-2_0_4_line_58 |  | 55 | 56 | 0.030499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2148-2_0_4_line_59 |  | 56 | 57 | 0.025497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2148-2_0_4_line_60 |  | 57 | 59 | 0.042517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2148-2_0_4_line_61 |  | 58 | 59 | 0.018213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2148-2_0_4_line_62 |  | 59 | 60 | 0.033608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2148-2_0_4_line_63 |  | 60 | 61 | 0.024214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2148-2_0_4_line_64 |  | 60 | 62 | 0.026086 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2148-2_0_4_line_65 |  | 61 | 63 | 0.0016687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2148-2_0_4_line_66 |  | 62 | 64 | 0.027246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2148-2_0_4_line_67 |  | 63 | 79 | 0.031837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2148-2_0_4_line_68 |  | 64 | 69 | 0.015385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2148-2_0_4_line_69 |  | 65 | 66 | 0.0024322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2148-2_0_4_line_70 |  | 65 | 67 | 0.031788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2148-2_0_4_line_71 |  | 66 | 68 | 0.029126 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2148-2_0_4_line_72 |  | 67 | 69 | 0.02336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2148-2_0_4_line_73 |  | 69 | 70 | 0.010053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2148-2_0_4_line_74 |  | 70 | 72 | 0.013285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2148-2_0_4_line_75 |  | 72 | 74 | 0.02151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2148-2_0_4_line_76 |  | 73 | 77 | 0.028244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_2148-2_0_4_line_77 |  | 74 | 75 | 0.002207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2148-2_0_4_line_78 |  | 75 | 76 | 0.023887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2148-2_0_4_line_79 |  | 76 | 77 | 0.022001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_2148-2_0_4_line_80 |  | 76 | 78 | 0.0053651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_2148-2_0_4_line_81 |  | 79 | 80 | 0.00050768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2148-2_0_4_line_82 |  | 80 | 81 | 0.028798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2148-2_0_4_line_83 |  | 82 | 83 | 0.026298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2148-2_0_4_line_84 |  | 83 | 110 | 0.019404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2148-2_0_4_line_85 |  | 84 | 85 | 0.011273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2148-2_0_4_line_86 |  | 85 | 86 | 0.025272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2148-2_0_4_line_87 |  | 85 | 87 | 0.02416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2148-2_0_4_line_88 |  | 86 | 112 | 0.025281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2148-2_0_4_line_89 |  | 87 | 91 | 0.012943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2148-2_0_4_line_90 |  | 88 | 89 | 0.0093554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2148-2_0_4_line_91 |  | 88 | 90 | 0.010153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2148-2_0_4_line_92 |  | 89 | 91 | 0.019215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_2148-2_0_4_line_93 |  | 90 | 92 | 0.018338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_2148-2_0_4_line_94 |  | 92 | 93 | 0.0015384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_2148-2_0_4_line_95 |  | 93 | 94 | 0.018222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_2148-2_0_4_line_96 |  | 94 | 110 | 0.0084122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_2148-2_0_4_line_97 |  | 95 | 96 | 0.001665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_2148-2_0_4_line_98 |  | 95 | 97 | 0.014262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_2148-2_0_4_line_99 |  | 96 | 98 | 0.02288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_2148-2_0_4_line_100 |  | 97 | 99 | 0.019586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2148-2_0_4_line_101 |  | 97 | 100 | 0.018556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2148-2_0_4_line_102 |  | 98 | 101 | 0.012454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2148-2_0_4_line_103 |  | 98 | 102 | 0.0027233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2148-2_0_4_line_104 |  | 99 | 103 | 0.010723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2148-2_0_4_line_105 |  | 100 | 104 | 0.026361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2148-2_0_4_line_106 |  | 101 | 105 | 0.029407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2148-2_0_4_line_107 |  | 102 | 106 | 0.023044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2148-2_0_4_line_108 |  | 103 | 107 | 0.02397 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2148-2_0_4_line_109 |  | 104 | 108 | 0.025878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2148-2_0_4_line_110 |  | 104 | 109 | 0.019858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2148-2_0_4_line_111 |  | 106 | 111 | 0.014814 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2148-2_0_4_line_112 |  | 107 | 110 | 0.011197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2148-2_0_4_line_113 |  | 108 | 125 | 0.018962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2148-2_0_4_line_114 |  | 109 | 126 | 0.0063824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2148-2_0_4_line_115 |  | 111 | 114 | 0.024178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2148-2_0_4_line_116 |  | 112 | 113 | 0.019257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_2148-2_0_4_line_117 |  | 116 | 117 | 0.020784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_2148-2_0_4_line_118 |  | 117 | 121 | 0.019698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_2148-2_0_4_line_119 |  | 117 | 118 | 0.046567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_2148-2_0_4_line_120 |  | 118 | 119 | 0.018542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_2148-2_0_4_line_121 |  | 119 | 120 | 0.0078274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_2148-2_0_4_line_122 |  | 121 | 122 | 0.019122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_2148-2_0_4_line_123 |  | 122 | 123 | 0.019506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_2148-2_0_4_line_124 |  | 123 | 124 | 0.02118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_2148-2_0_4_line_125 |  | 124 | 125 | 0.019906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2148-2_0_4_trafo_105 | 0.63 MVA 20/0.4 kV | 127 | 73 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2571036.7754 | 1165159.9812 | 2571036.3509 | 1165151.1951 | 2571037.9925 | 1165146.1636
1 | 2571037.4656 | 1165174.2681 | 2571036.7754 | 1165159.9812
2 | 2571067.132 | 1165166.8432 | 2571037.4656 | 1165174.2681
3 | 2571067.132 | 1165166.8432 | 2571061.6099 | 1165139.6561 | 2571060.0709 | 1165130.1587 | 2571059.0073 | 1165118.4667
4 | 2570989.0504 | 1165193.501 | 2570977.9938 | 1165174.0899
5 | 2570989.0504 | 1165193.501 | 2570966.7183 | 1165205.6958
6 | 2570977.9938 | 1165174.0899 | 2570975.4199 | 1165169.5711
7 | 2570966.7183 | 1165205.6958 | 2570964.4239 | 1165206.9487
8 | 2570949.7098 | 1165124.4343 | 2570983.8058 | 1165108.2609
9 | 2570984.4333 | 1165094.5224 | 2570986.1243 | 1165103.1915 | 2570983.8058 | 1165108.2609 | 2570983.8058 | 1165108.2609
10 | 2570949.7098 | 1165124.4343 | 2570960.5708 | 1165143.5021
11 | 2570949.7098 | 1165124.4343 | 2570948.117 | 1165121.4773
12 | 2570984.4333 | 1165094.5224 | 2570983.4252 | 1165089.3543
13 | 2571059.0073 | 1165118.4667 | 2571057.9198 | 1165106.5126 | 2571057.7186 | 1165087.0704 | 2571058.9303 | 1165071.1637
14 | 2571061.3035 | 1165041.8233 | 2571060.1991 | 1165055.2867 | 2571059.3603 | 1165065.5182 | 2571058.9303 | 1165071.1637
15 | 2571058.9303 | 1165071.1637 | 2571046.1216 | 1165092.021
16 | 2571061.3035 | 1165041.8233 | 2571061.6816 | 1165037.2148 | 2571064.4375 | 1165011.3833
17 | 2570983.6453 | 1165075.1448 | 2570981.46 | 1165079.2797 | 2570983.4252 | 1165089.3543
18 | 2570964.4239 | 1165206.9487 | 2570943.2375 | 1165218.5179
19 | 2570939.2118 | 1165220.7162 | 2570943.2375 | 1165218.5179
20 | 2570927.5732 | 1165227.0716 | 2570939.2118 | 1165220.7162
21 | 2570975.4199 | 1165169.5711 | 2570964.7635 | 1165150.8627
22 | 2570927.5732 | 1165227.0716 | 2570909.0571 | 1165237.2595
23 | 2570964.7635 | 1165150.8627 | 2570960.5708 | 1165143.5021
24 | 2570900.4045 | 1165263.8123 | 2570907.4732 | 1165275.9274 | 2570913.7624 | 1165282.7663
25 | 2570890.7795 | 1165247.3161 | 2570900.4045 | 1165263.8123
26 | 2570890.7795 | 1165247.3161 | 2570880.1685 | 1165253.233
27 | 2570890.7795 | 1165247.3161 | 2570907.1912 | 1165238.2861
28 | 2570867.2289 | 1165260.4484 | 2570880.1685 | 1165253.233
29 | 2570907.1912 | 1165238.2861 | 2570909.0571 | 1165237.2595
30 | 2570867.2289 | 1165260.4484 | 2570846.0533 | 1165272.1655
31 | 2570904.9009 | 1165188.1022 | 2570903.7969 | 1165186.2046
32 | 2570892.1463 | 1165166.1793 | 2570903.7969 | 1165186.2046
33 | 2570892.1463 | 1165166.1793 | 2570879.2883 | 1165174.1198
34 | 2570892.1463 | 1165166.1793 | 2570885.6229 | 1165154.2021
35 | 2571064.4375 | 1165011.3833 | 2571044.799 | 1165006.4793
36 | 2570993.0832 | 1165058.6018 | 2570993.2717 | 1165069.0507 | 2570983.6453 | 1165075.1448
37 | 2571035.9007 | 1165005.8568 | 2571044.799 | 1165006.4793
38 | 2571039.2229 | 1164971.9784 | 2571044.799 | 1165006.4793
39 | 2571008.7917 | 1164989.3841 | 2571035.9007 | 1165005.8568
40 | 2571007.9994 | 1164989.8373 | 2571008.7917 | 1164989.3841
41 | 2571062.8043 | 1164914.5915 | 2571061.9084 | 1164865.3767
42 | 2571062.8043 | 1164914.5915 | 2571042.3199 | 1164915.0856
43 | 2571061.9084 | 1164865.3767 | 2571061.4609 | 1164840.7905
44 | 2571022.4538 | 1164915.5648 | 2571042.3199 | 1164915.0856
45 | 2571007.9994 | 1164989.8373 | 2570984.2778 | 1165003.4053 | 2570984.2164 | 1165003.438
46 | 2570983.8301 | 1165003.6439 | 2570984.2164 | 1165003.438
47 | 2570983.8301 | 1165003.6439 | 2570953.7936 | 1165019.6495
48 | 2570940.7813 | 1165026.5834 | 2570953.7936 | 1165019.6495
49 | 2570940.7813 | 1165026.5834 | 2570932.1614 | 1165012.824
50 | 2570940.7813 | 1165026.5834 | 2570911.4987 | 1165042.18
51 | 2570846.1745 | 1165222.7205 | 2570844.9845 | 1165220.5881
52 | 2570828.849 | 1165191.6745 | 2570844.9845 | 1165220.5881
53 | 2570825.8873 | 1165186.3674 | 2570828.849 | 1165191.6745
54 | 2570932.3839 | 1165092.2681 | 2570948.117 | 1165121.4773
55 | 2570930.5905 | 1165088.9384 | 2570932.3839 | 1165092.2681
56 | 2570790.795 | 1165253.889 | 2570771.9113 | 1165239.602 | 2570763.4751 | 1165222.8573
57 | 2570763.4751 | 1165222.8573 | 2570747.4958 | 1165191.1403
58 | 2570733.7733 | 1165163.903 | 2570747.4958 | 1165191.1403
59 | 2570716.1398 | 1165146.2602 | 2570724.1497 | 1165151.0346 | 2570731.6346 | 1165159.658 | 2570733.7733 | 1165163.903
60 | 2570716.1398 | 1165146.2602 | 2570753.7462 | 1165126.2219
61 | 2570753.7462 | 1165126.2219 | 2570745.7245 | 1165109.8705
62 | 2570783.471 | 1165110.3799 | 2570753.7462 | 1165126.2219
63 | 2570783.471 | 1165110.3799 | 2570795.2729 | 1165131.5227
64 | 2570783.471 | 1165110.3799 | 2570806.4938 | 1165098.115
65 | 2570796.0862 | 1165132.9798 | 2570795.2729 | 1165131.5227
66 | 2570830.5406 | 1165085.3045 | 2570806.4938 | 1165098.115
67 | 2570796.0862 | 1165132.9798 | 2570811.6037 | 1165160.7788
68 | 2570844.1507 | 1165078.0568 | 2570830.5406 | 1165085.3045
69 | 2570870.5283 | 1165126.4874 | 2570871.6916 | 1165128.6234
70 | 2570870.5283 | 1165126.4874 | 2570855.3237 | 1165098.571
71 | 2570885.6229 | 1165154.2021 | 2570871.6916 | 1165128.6234
72 | 2570844.1507 | 1165078.0568 | 2570855.3237 | 1165098.571
73 | 2570844.1507 | 1165078.0568 | 2570853.0236 | 1165073.3301
74 | 2570853.0236 | 1165073.3301 | 2570864.7486 | 1165067.084
75 | 2570883.7331 | 1165056.9707 | 2570864.7486 | 1165067.084
76 | 2570930.5905 | 1165088.9384 | 2570917.1966 | 1165064.0719
77 | 2570883.7331 | 1165056.9707 | 2570885.681 | 1165055.9331
78 | 2570906.7634 | 1165044.7022 | 2570885.681 | 1165055.9331
79 | 2570906.7634 | 1165044.7022 | 2570917.1966 | 1165064.0719
80 | 2570906.7634 | 1165044.7022 | 2570911.4987 | 1165042.18
81 | 2570811.6037 | 1165160.7788 | 2570811.8511 | 1165161.2221
82 | 2570825.8873 | 1165186.3674 | 2570811.8511 | 1165161.2221
83 | 2570918.2 | 1164990.5382 | 2570932.1614 | 1165012.824
84 | 2570907.8982 | 1164974.0941 | 2570918.2 | 1164990.5382
85 | 2570802.9513 | 1165036.6141 | 2570806.7724 | 1165046.0448 | 2570807.3408 | 1165046.9837
86 | 2570802.9513 | 1165036.6141 | 2570790.2546 | 1165014.7636
87 | 2570802.9513 | 1165036.6141 | 2570811.4462 | 1165029.3357 | 2570822.7042 | 1165022.8879
88 | 2570777.5529 | 1164992.9046 | 2570790.2546 | 1165014.7636
89 | 2570822.7042 | 1165022.8879 | 2570833.9357 | 1165016.4551
90 | 2570858.7276 | 1165002.2559 | 2570850.6095 | 1165006.9055
91 | 2570858.7276 | 1165002.2559 | 2570867.538 | 1164997.2099
92 | 2570833.9357 | 1165016.4551 | 2570850.6095 | 1165006.9055
93 | 2570883.4511 | 1164988.0958 | 2570867.538 | 1164997.2099
94 | 2570884.7861 | 1164987.3313 | 2570883.4511 | 1164988.0958
95 | 2570900.5985 | 1164978.2749 | 2570884.7861 | 1164987.3313
96 | 2570907.8982 | 1164974.0941 | 2570900.5985 | 1164978.2749
97 | 2570977.088 | 1164934.4595 | 2570978.5328 | 1164933.6321
98 | 2570964.7119 | 1164941.5464 | 2570977.088 | 1164934.4595
99 | 2570998.388 | 1164922.2624 | 2570978.5328 | 1164933.6321
100 | 2570964.7119 | 1164941.5464 | 2570947.7169 | 1164951.2826
101 | 2570964.7119 | 1164941.5464 | 2570963.0946 | 1164938.0747 | 2570957.2546 | 1164924.5563
102 | 2570998.388 | 1164922.2624 | 2570993.0776 | 1164910.997
103 | 2570998.388 | 1164922.2624 | 2571000.751 | 1164920.9085
104 | 2570938.4124 | 1164956.613 | 2570947.7169 | 1164951.2826
105 | 2570946.8003 | 1164900.3568 | 2570957.2546 | 1164924.5563
106 | 2570980.8366 | 1164884.2614 | 2570985.9391 | 1164895.8537 | 2570993.0776 | 1164910.997
107 | 2571022.4538 | 1164915.5648 | 2571009.5218 | 1164915.8831 | 2571000.751 | 1164920.9085
108 | 2570938.4124 | 1164956.613 | 2570917.6137 | 1164968.5282
109 | 2570946.8003 | 1164900.3568 | 2570924.0952 | 1164912.7724
110 | 2570946.8003 | 1164900.3568 | 2570937.9808 | 1164882.5642
111 | 2571022.4538 | 1164915.5648 | 2571021.6287 | 1164900.7736
112 | 2570907.8982 | 1164974.0941 | 2570917.6137 | 1164968.5282
113 | 2570924.0952 | 1164912.7724 | 2570907.4581 | 1164921.8698
114 | 2570935.1462 | 1164876.8458 | 2570937.9808 | 1164882.5642
115 | 2571020.2821 | 1164876.6333 | 2571021.6287 | 1164900.7736
116 | 2570777.5529 | 1164992.9046 | 2570767.8214 | 1164976.2881
117 | 2570801.9991 | 1164979.537 | 2570820.2348 | 1164969.5653
118 | 2570820.2348 | 1164969.5653 | 2570837.5178 | 1164960.1146
119 | 2570820.2348 | 1164969.5653 | 2570796.5038 | 1164929.4985
120 | 2570812.7688 | 1164920.5966 | 2570796.5038 | 1164929.4985
121 | 2570819.6351 | 1164916.8387 | 2570812.7688 | 1164920.5966
122 | 2570854.2952 | 1164950.9404 | 2570837.5178 | 1164960.1146
123 | 2570871.4097 | 1164941.5819 | 2570854.2952 | 1164950.9404
124 | 2570889.9925 | 1164931.4204 | 2570871.4097 | 1164941.5819
125 | 2570889.9925 | 1164931.4204 | 2570907.4581 | 1164921.8698

## bus_geodata
| x | y | coords
0 | 2571036.7754 | 1165159.9812
1 | 2571037.9925 | 1165146.1636
2 | 2571037.4656 | 1165174.2681
3 | 2571067.132 | 1165166.8432
4 | 2570989.0504 | 1165193.501
5 | 2570977.9938 | 1165174.0899
6 | 2570966.7183 | 1165205.6958
7 | 2570983.8058 | 1165108.2609
8 | 2570949.7098 | 1165124.4343
9 | 2570984.4333 | 1165094.5224
10 | 2571059.0073 | 1165118.4667
11 | 2571058.9303 | 1165071.1637
12 | 2571046.1216 | 1165092.021
13 | 2571061.3035 | 1165041.8233
14 | 2570983.4252 | 1165089.3543
15 | 2570964.4239 | 1165206.9487
16 | 2570943.2375 | 1165218.5179
17 | 2570939.2118 | 1165220.7162
18 | 2570975.4199 | 1165169.5711
19 | 2570927.5732 | 1165227.0716
20 | 2570964.7635 | 1165150.8627
21 | 2570913.7624 | 1165282.7663
22 | 2570900.4045 | 1165263.8123
23 | 2570890.7795 | 1165247.3161
24 | 2570880.1685 | 1165253.233
25 | 2570907.1912 | 1165238.2861
26 | 2570867.2289 | 1165260.4484
27 | 2570909.0571 | 1165237.2595
28 | 2570904.9009 | 1165188.1022
29 | 2570903.7969 | 1165186.2046
30 | 2570892.1463 | 1165166.1793
31 | 2571064.4375 | 1165011.3833
32 | 2570993.0832 | 1165058.6018
33 | 2570983.6453 | 1165075.1448
34 | 2571044.799 | 1165006.4793
35 | 2571035.9007 | 1165005.8568
36 | 2571039.2229 | 1164971.9784
37 | 2571008.7917 | 1164989.3841
38 | 2571062.8043 | 1164914.5915
39 | 2571061.9084 | 1164865.3767
40 | 2571042.3199 | 1164915.0856
41 | 2570846.0533 | 1165272.1655
42 | 2571007.9994 | 1164989.8373
43 | 2570984.2164 | 1165003.438
44 | 2570983.8301 | 1165003.6439
45 | 2570953.7936 | 1165019.6495
46 | 2570940.7813 | 1165026.5834
47 | 2570846.1745 | 1165222.7205
48 | 2570844.9845 | 1165220.5881
49 | 2570828.849 | 1165191.6745
50 | 2570960.5708 | 1165143.5021
51 | 2570948.117 | 1165121.4773
52 | 2570932.3839 | 1165092.2681
53 | 2570790.795 | 1165253.889
54 | 2570763.4751 | 1165222.8573
55 | 2570747.4958 | 1165191.1403
56 | 2570733.7733 | 1165163.903
57 | 2570716.1398 | 1165146.2602
58 | 2570745.7245 | 1165109.8705
59 | 2570753.7462 | 1165126.2219
60 | 2570783.471 | 1165110.3799
61 | 2570795.2729 | 1165131.5227
62 | 2570806.4938 | 1165098.115
63 | 2570796.0862 | 1165132.9798
64 | 2570830.5406 | 1165085.3045
65 | 2570870.5283 | 1165126.4874
66 | 2570871.6916 | 1165128.6234
67 | 2570855.3237 | 1165098.571
68 | 2570885.6229 | 1165154.2021
69 | 2570844.1507 | 1165078.0568
70 | 2570853.0236 | 1165073.3301
71 | 2570879.2883 | 1165174.1198
72 | 2570864.7486 | 1165067.084
73 | 2570930.5905 | 1165088.9384
74 | 2570883.7331 | 1165056.9707
75 | 2570885.681 | 1165055.9331
76 | 2570906.7634 | 1165044.7022
77 | 2570917.1966 | 1165064.0719
78 | 2570911.4987 | 1165042.18
79 | 2570811.6037 | 1165160.7788
80 | 2570811.8511 | 1165161.2221
81 | 2570825.8873 | 1165186.3674
82 | 2570932.1614 | 1165012.824
83 | 2570918.2 | 1164990.5382
84 | 2570807.3408 | 1165046.9837
85 | 2570802.9513 | 1165036.6141
86 | 2570790.2546 | 1165014.7636
87 | 2570822.7042 | 1165022.8879
88 | 2570858.7276 | 1165002.2559
89 | 2570850.6095 | 1165006.9055
90 | 2570867.538 | 1164997.2099
91 | 2570833.9357 | 1165016.4551
92 | 2570883.4511 | 1164988.0958
93 | 2570884.7861 | 1164987.3313
94 | 2570900.5985 | 1164978.2749
95 | 2570977.088 | 1164934.4595
96 | 2570978.5328 | 1164933.6321
97 | 2570964.7119 | 1164941.5464
98 | 2570998.388 | 1164922.2624
99 | 2570947.7169 | 1164951.2826
100 | 2570957.2546 | 1164924.5563
101 | 2570993.0776 | 1164910.997
102 | 2571000.751 | 1164920.9085
103 | 2570938.4124 | 1164956.613
104 | 2570946.8003 | 1164900.3568
105 | 2570980.8366 | 1164884.2614
106 | 2571022.4538 | 1164915.5648
107 | 2570917.6137 | 1164968.5282
108 | 2570924.0952 | 1164912.7724
109 | 2570937.9808 | 1164882.5642
110 | 2570907.8982 | 1164974.0941
111 | 2571021.6287 | 1164900.7736
112 | 2570777.5529 | 1164992.9046
113 | 2570767.8214 | 1164976.2881
114 | 2571020.2821 | 1164876.6333
115 | 2571061.4609 | 1164840.7905
116 | 2570801.9991 | 1164979.537
117 | 2570820.2348 | 1164969.5653
118 | 2570796.5038 | 1164929.4985
119 | 2570812.7688 | 1164920.5966
120 | 2570819.6351 | 1164916.8387
121 | 2570837.5178 | 1164960.1146
122 | 2570854.2952 | 1164950.9404
123 | 2570871.4097 | 1164941.5819
124 | 2570889.9925 | 1164931.4204
125 | 2570907.4581 | 1164921.8698
126 | 2570935.1462 | 1164876.8458
127 | 2570949.7098 | 1165124.4343

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9742 | -0.49789 | 0.007831 | 0.0019626
1 | 0.97405 | -0.50079 | 0.011221 | 0.0028124
2 | 0.97445 | -0.49288 | 0 | 0
3 | 0.97499 | -0.48222 | 0 | 0
4 | 0.9918 | -0.15734 | 0 | 0
5 | 0.9928 | -0.13802 | 0.0058971 | 0.001478
6 | 0.99066 | -0.17939 | 0.0056786 | 0.0014232
7 | 0.99517 | -0.092511 | 0.0087481 | 0.0021925
8 | 0.99616 | -0.073546 | 0 | 0
9 | 0.99491 | -0.097542 | 0.0043315 | 0.0010856
10 | 0.97586 | -0.46508 | 0.006074 | 0.0015223
11 | 0.97697 | -0.4433 | 0.0092445 | 0.0023169
12 | 0.97672 | -0.44817 | 0.010893 | 0.0027301
13 | 0.97821 | -0.419 | 0.0074936 | 0.0018781
14 | 0.99484 | -0.098979 | 0.0047807 | 0.0011981
15 | 0.99056 | -0.1814 | 0.0014791 | 0.00037069
16 | 0.98964 | -0.19929 | 0.0053759 | 0.0013473
17 | 0.98948 | -0.20226 | 0.0038864 | 0.00097401
18 | 0.99306 | -0.13298 | 0.0044741 | 0.0011213
19 | 0.98909 | -0.20992 | 0 | 0
20 | 0.99423 | -0.11047 | 0.0065058 | 0.0016305
21 | 0.98761 | -0.2386 | 0.0074588 | 0.0018694
22 | 0.98777 | -0.23549 | 0.0056502 | 0.0014161
23 | 0.988 | -0.23102 | 0 | 0
24 | 0.98789 | -0.23327 | 0.0041741 | 0.0010461
25 | 0.98841 | -0.22317 | 0.0036236 | 0.00090816
26 | 0.9878 | -0.23491 | 0 | 0
27 | 0.98846 | -0.22214 | 0.0053368 | 0.0013375
28 | 0.98649 | -0.259 | 0.005307 | 0.0013301
29 | 0.9865 | -0.25879 | 0.0043809 | 0.001098
30 | 0.98671 | -0.25477 | 0 | 0
31 | 0.97971 | -0.38963 | 0.0085204 | 0.0021354
32 | 0.99453 | -0.10493 | 0.0081356 | 0.002039
33 | 0.99469 | -0.1018 | 0.0025854 | 0.00064797
34 | 0.98086 | -0.36713 | 0.010237 | 0.0025657
35 | 0.98151 | -0.35447 | 0.0073849 | 0.0018508
36 | 0.98064 | -0.37149 | 0.0068776 | 0.0017237
37 | 0.98403 | -0.30536 | 0.0043687 | 0.0010949
38 | 0.978 | -0.42332 | 0 | 0
39 | 0.97763 | -0.43067 | 0.0040904 | 0.0010251
40 | 0.97816 | -0.42026 | 0.0067429 | 0.0016899
41 | 0.98766 | -0.23758 | 0.0061891 | 0.0015511
42 | 0.98411 | -0.30388 | 0.0088842 | 0.0022266
43 | 0.98663 | -0.25517 | 0.0034481 | 0.00086418
44 | 0.98667 | -0.25437 | 0.0021836 | 0.00054725
45 | 0.98997 | -0.1908 | 0.0030393 | 0.00076173
46 | 0.99144 | -0.1626 | 0 | 0
47 | 0.98351 | -0.31699 | 0.0048232 | 0.0012088
48 | 0.98352 | -0.31678 | 0.0046606 | 0.0011681
49 | 0.98381 | -0.31112 | 0.0038633 | 0.00096823
50 | 0.99474 | -0.10066 | 0.0045011 | 0.0011281
51 | 0.99646 | -0.067718 | 0.0054874 | 0.0013753
52 | 0.99962 | -0.0071621 | 0.0042978 | 0.0010771
53 | 0.98272 | -0.33237 | 0.0049481 | 0.0012401
54 | 0.98291 | -0.32858 | 0.0055221 | 0.001384
55 | 0.98326 | -0.32187 | 0.0049219 | 0.0012335
56 | 0.98369 | -0.31341 | 0.0037881 | 0.00094938
57 | 0.98414 | -0.3046 | 0 | 0
58 | 0.98484 | -0.29102 | 0.0033014 | 0.00082741
59 | 0.98489 | -0.28994 | 0 | 0
60 | 0.98559 | -0.27637 | 0 | 0
61 | 0.98493 | -0.2892 | 0.0043129 | 0.0010809
62 | 0.98684 | -0.25206 | 0.0023042 | 0.00057749
63 | 0.98489 | -0.28995 | 0.0031205 | 0.00078206
64 | 0.9882 | -0.22561 | 0 | 0
65 | 0.98746 | -0.24009 | 0.0047018 | 0.0011784
66 | 0.98741 | -0.2411 | 0.0035205 | 0.00088231
67 | 0.98827 | -0.22432 | 0.0048875 | 0.0012249
68 | 0.98689 | -0.25129 | 0.0052746 | 0.0013219
69 | 0.98897 | -0.21071 | 0 | 0
70 | 0.98978 | -0.19514 | 0.0030409 | 0.00076213
71 | 0.98664 | -0.25602 | 0.0045968 | 0.0011521
72 | 0.99088 | -0.17388 | 0.002366 | 0.00059298
73 | 1 | 0 | -0.43546 | -0.11109
74 | 0.99271 | -0.13867 | 0.0023812 | 0.00059678
75 | 0.9929 | -0.13497 | 0.0043143 | 0.0010813
76 | 0.99508 | -0.093214 | 0 | 0
77 | 0.99722 | -0.052512 | 0.0031443 | 0.00078803
78 | 0.99472 | -0.10004 | 0.0035231 | 0.00088298
79 | 0.98425 | -0.30259 | 0.0055374 | 0.0013878
80 | 0.98424 | -0.30274 | 0.0031932 | 0.00080028
81 | 0.98388 | -0.30966 | 0 | 0
82 | 0.98985 | -0.19306 | 0.0036364 | 0.00091136
83 | 0.98737 | -0.2409 | 0.0017165 | 0.00043019
84 | 0.98438 | -0.29894 | 0.001607 | 0.00040276
85 | 0.9844 | -0.29862 | 0 | 0
86 | 0.98433 | -0.2999 | 0.0020209 | 0.00050648
87 | 0.98449 | -0.2967 | 0.0019714 | 0.00049408
88 | 0.9848 | -0.29072 | 0.0017065 | 0.00042769
89 | 0.98472 | -0.29239 | 0.0017237 | 0.000432
90 | 0.98491 | -0.2886 | 0.00149 | 0.00037343
91 | 0.98457 | -0.29521 | 0.0017962 | 0.00045017
92 | 0.98513 | -0.28428 | 0.0019267 | 0.00048287
93 | 0.98515 | -0.28387 | 0.0014615 | 0.00036629
94 | 0.98543 | -0.27847 | 0.0014626 | 0.00036656
95 | 0.9801 | -0.38216 | 0.002651 | 0.00066441
96 | 0.98003 | -0.3835 | 0.0018876 | 0.00047307
97 | 0.98073 | -0.36997 | 0 | 0
98 | 0.97913 | -0.4012 | 0 | 0
99 | 0.98213 | -0.34261 | 0.0022925 | 0.00057455
100 | 0.98021 | -0.38008 | 0.0014916 | 0.00037384
101 | 0.97904 | -0.40289 | 0.0041045 | 0.0010287
102 | 0.97904 | -0.40294 | 0.0067244 | 0.0016853
103 | 0.98292 | -0.32722 | 0.0013922 | 0.00034892
104 | 0.97951 | -0.39374 | 0 | 0
105 | 0.97895 | -0.40468 | 0.0033515 | 0.00083995
106 | 0.97844 | -0.41486 | 0 | 0
107 | 0.98471 | -0.29232 | 0.0014621 | 0.00036645
108 | 0.97889 | -0.40591 | 0.0030898 | 0.00077437
109 | 0.97946 | -0.39472 | 0.0015298 | 0.00038341
110 | 0.98557 | -0.27576 | 0 | 0
111 | 0.97825 | -0.41849 | 0.0048758 | 0.001222
112 | 0.98431 | -0.30025 | 0 | 0
113 | 0.9843 | -0.30053 | 0.00078544 | 0.00019685
114 | 0.97806 | -0.42228 | 0.0086024 | 0.002156
115 | 0.97754 | -0.4325 | 0.0040967 | 0.0010267
116 | 0.97704 | -0.44217 | 0.0019206 | 0.00048135
117 | 0.97708 | -0.44144 | 0.0025189 | 0.0006313
118 | 0.97684 | -0.44628 | 0.0019992 | 0.00050103
119 | 0.97677 | -0.44753 | 0.0019002 | 0.00047624
120 | 0.97676 | -0.44779 | 0.0017954 | 0.00044996
121 | 0.97727 | -0.43779 | 0.0025359 | 0.00063555
122 | 0.97749 | -0.43337 | 0.002582 | 0.00064712
123 | 0.97777 | -0.42794 | 0.0023983 | 0.00060108
124 | 0.97811 | -0.42113 | 0.0026685 | 0.00066878
125 | 0.97849 | -0.41376 | 0.00244 | 0.00061152
126 | 0.97945 | -0.39485 | 0.0011701 | 0.00029326
127 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.011223 | 0.0028132 | -0.011221 | -0.0028124 | 1.5526e-06 | 8.1827e-07 | 0.017143 | 0.017143 | 0.017143 | 0.9742 | -0.49789 | 0.97405 | -0.50079 | 4.7095
1 | -0.019054 | -0.0047758 | 0.019059 | 0.0047785 | 4.5433e-06 | 2.7296e-06 | 0.029104 | 0.029104 | 0.029104 | 0.9742 | -0.49789 | 0.97445 | -0.49288 | 7.9956
2 | -0.019059 | -0.0047785 | 0.019068 | 0.0047844 | 9.6872e-06 | 5.8197e-06 | 0.029104 | 0.029104 | 0.029104 | 0.97445 | -0.49288 | 0.97499 | -0.48222 | 7.9955
3 | -0.019068 | -0.0047844 | 0.019084 | 0.0047937 | 1.5597e-05 | 9.3691e-06 | 0.029104 | 0.029103 | 0.029104 | 0.97499 | -0.48222 | 0.97586 | -0.46508 | 7.9955
4 | -0.048996 | -0.012333 | 0.049042 | 0.012362 | 4.5291e-05 | 2.8698e-05 | 0.073529 | 0.073529 | 0.073529 | 0.9918 | -0.15734 | 0.9928 | -0.13802 | 20.2002
5 | 0.048996 | 0.012333 | -0.048945 | -0.0123 | 5.1588e-05 | 3.2688e-05 | 0.073529 | 0.073529 | 0.073529 | 0.9918 | -0.15734 | 0.99066 | -0.17939 | 20.2003
6 | -0.054939 | -0.01384 | 0.054952 | 0.013848 | 1.3231e-05 | 8.4004e-06 | 0.082367 | 0.082367 | 0.082367 | 0.9928 | -0.13802 | 0.99306 | -0.13298 | 22.6284
7 | 0.043266 | 0.010877 | -0.043262 | -0.010874 | 4.1417e-06 | 2.6171e-06 | 0.064999 | 0.064999 | 0.064999 | 0.99066 | -0.17939 | 0.99056 | -0.1814 | 17.857
8 | -0.02859 | -0.0071678 | 0.028616 | 0.0071839 | 2.5862e-05 | 1.6061e-05 | 0.042749 | 0.042749 | 0.042749 | 0.99517 | -0.092511 | 0.99616 | -0.073546 | 11.7443
9 | 0.019842 | 0.0049753 | -0.019837 | -0.0049725 | 4.7555e-06 | 2.8564e-06 | 0.029669 | 0.029669 | 0.029669 | 0.99517 | -0.092511 | 0.99491 | -0.097542 | 8.1508
10 | 0.07062 | 0.017847 | -0.070528 | -0.017788 | 9.1662e-05 | 5.8379e-05 | 0.10554 | 0.10554 | 0.10554 | 0.99616 | -0.073546 | 0.99474 | -0.10066 | 28.9948
11 | -0.099235 | -0.025031 | 0.099263 | 0.025048 | 2.7696e-05 | 1.7682e-05 | 0.14829 | 0.14829 | 0.14829 | 0.99616 | -0.073546 | 0.99646 | -0.067718 | 40.739
12 | 0.015505 | 0.0038869 | -0.015504 | -0.0038863 | 1.0619e-06 | 6.1127e-07 | 0.023191 | 0.023191 | 0.023191 | 0.99491 | -0.097542 | 0.99484 | -0.098979 | 6.371
13 | -0.025158 | -0.006316 | 0.025184 | 0.0063322 | 2.6162e-05 | 1.6151e-05 | 0.038365 | 0.038365 | 0.038365 | 0.97586 | -0.46508 | 0.97697 | -0.4433 | 10.5399
14 | -0.045324 | -0.01138 | 0.045377 | 0.011414 | 5.2617e-05 | 3.3306e-05 | 0.069041 | 0.069041 | 0.069041 | 0.97697 | -0.4433 | 0.97821 | -0.419 | 18.9672
15 | 0.010896 | 0.0027314 | -0.010893 | -0.0027301 | 2.5279e-06 | 1.3114e-06 | 0.016595 | 0.016596 | 0.016596 | 0.97697 | -0.4433 | 0.97672 | -0.44817 | 4.5592
16 | -0.05287 | -0.013292 | 0.052945 | 0.013339 | 7.4254e-05 | 4.7138e-05 | 0.080439 | 0.080439 | 0.080439 | 0.97821 | -0.419 | 0.97971 | -0.38963 | 22.0988
17 | 0.010724 | 0.0026882 | -0.010722 | -0.0026874 | 1.4415e-06 | 7.2862e-07 | 0.01604 | 0.01604 | 0.01604 | 0.99484 | -0.098979 | 0.99469 | -0.1018 | 4.4066
18 | 0.041783 | 0.010504 | -0.041747 | -0.010481 | 3.5675e-05 | 2.2522e-05 | 0.062778 | 0.062778 | 0.062778 | 0.99056 | -0.1814 | 0.98964 | -0.19929 | 17.2466
19 | 0.036371 | 0.0091339 | -0.036366 | -0.0091307 | 5.1455e-06 | 3.2342e-06 | 0.054695 | 0.054695 | 0.054695 | 0.98964 | -0.19929 | 0.98948 | -0.20226 | 15.026
20 | 0.03248 | 0.0081567 | -0.032468 | -0.0081493 | 1.1867e-05 | 7.4245e-06 | 0.04885 | 0.04885 | 0.04885 | 0.98948 | -0.20226 | 0.98909 | -0.20992 | 13.4204
21 | -0.059426 | -0.014969 | 0.05949 | 0.01501 | 6.4056e-05 | 4.0717e-05 | 0.089071 | 0.089071 | 0.089071 | 0.99306 | -0.13298 | 0.99423 | -0.11047 | 24.4701
22 | 0.032468 | 0.0081493 | -0.032449 | -0.0081374 | 1.8912e-05 | 1.1833e-05 | 0.04885 | 0.04885 | 0.04885 | 0.98909 | -0.20992 | 0.98846 | -0.22214 | 13.4204
23 | -0.065996 | -0.016641 | 0.066027 | 0.01666 | 3.1013e-05 | 1.9739e-05 | 0.098808 | 0.098808 | 0.098808 | 0.99423 | -0.11047 | 0.99474 | -0.10066 | 27.1451
24 | -0.0074588 | -0.0018694 | 0.0074599 | 0.0018698 | 1.1043e-06 | 4.0833e-07 | 0.011238 | 0.011238 | 0.011238 | 0.98761 | -0.2386 | 0.98777 | -0.23549 | 3.0874
25 | -0.01311 | -0.0032858 | 0.013113 | 0.0032874 | 2.7935e-06 | 1.5433e-06 | 0.01975 | 0.01975 | 0.01975 | 0.98777 | -0.23549 | 0.988 | -0.23102 | 5.4257
26 | 0.010366 | 0.0025981 | -0.010365 | -0.0025976 | 1.1104e-06 | 5.5508e-07 | 0.015612 | 0.015612 | 0.015612 | 0.988 | -0.23102 | 0.98789 | -0.23327 | 4.2889
27 | -0.023479 | -0.0058855 | 0.023487 | 0.0058909 | 8.7835e-06 | 5.3814e-06 | 0.035361 | 0.035361 | 0.035361 | 0.988 | -0.23102 | 0.98841 | -0.22317 | 9.7146
28 | 0.0061904 | 0.0015515 | -0.0061899 | -0.0015513 | 4.8304e-07 | 1.1948e-07 | 0.0093244 | 0.0093245 | 0.0093245 | 0.98789 | -0.23327 | 0.9878 | -0.23491 | 2.5617
29 | -0.027111 | -0.0067991 | 0.027112 | 0.0067999 | 1.3305e-06 | 8.2423e-07 | 0.040816 | 0.040816 | 0.040816 | 0.98841 | -0.22317 | 0.98846 | -0.22214 | 11.2133
30 | 0.0061899 | 0.0015513 | -0.0061891 | -0.0015511 | 7.8908e-07 | 1.9525e-07 | 0.0093245 | 0.0093246 | 0.0093246 | 0.9878 | -0.23491 | 0.98766 | -0.23758 | 2.5617
31 | -0.005307 | -0.0013301 | 0.005307 | 0.0013301 | 5.2754e-08 | 5.734e-09 | 0.008005 | 0.008005 | 0.008005 | 0.98649 | -0.259 | 0.9865 | -0.25879 | 2.1992
32 | -0.0096879 | -0.002428 | 0.0096898 | 0.0024289 | 1.8552e-06 | 8.9148e-07 | 0.014613 | 0.014613 | 0.014613 | 0.9865 | -0.25879 | 0.98671 | -0.25477 | 4.0146
33 | 0.0045971 | 0.0011521 | -0.0045968 | -0.0011521 | 2.7237e-07 | -1.8695e-08 | 0.0069327 | 0.0069327 | 0.0069327 | 0.98671 | -0.25477 | 0.98664 | -0.25602 | 1.9046
34 | -0.014287 | -0.003581 | 0.014289 | 0.0035823 | 2.3742e-06 | 1.3452e-06 | 0.021546 | 0.021546 | 0.021546 | 0.98671 | -0.25477 | 0.98689 | -0.25129 | 5.9191
35 | -0.061465 | -0.015474 | 0.061531 | 0.015517 | 6.6189e-05 | 4.2106e-05 | 0.09338 | 0.09338 | 0.09338 | 0.97971 | -0.38963 | 0.98086 | -0.36713 | 25.654
36 | -0.0081356 | -0.002039 | 0.0081368 | 0.0020395 | 1.2137e-06 | 4.9328e-07 | 0.012172 | 0.012172 | 0.012172 | 0.99453 | -0.10493 | 0.99469 | -0.1018 | 3.3441
37 | -0.078648 | -0.019806 | 0.078695 | 0.019837 | 4.7645e-05 | 3.038e-05 | 0.11935 | 0.11935 | 0.11935 | 0.98086 | -0.36713 | 0.98151 | -0.35447 | 32.7875
38 | 0.006879 | 0.0017242 | -0.0068776 | -0.0017237 | 1.4273e-06 | 4.7248e-07 | 0.010436 | 0.010436 | 0.010436 | 0.98086 | -0.36713 | 0.98064 | -0.37149 | 2.867
39 | -0.08608 | -0.021688 | 0.086283 | 0.021817 | 0.00020271 | 0.00012934 | 0.13054 | 0.13054 | 0.13054 | 0.98151 | -0.35447 | 0.98403 | -0.30536 | 35.8633
40 | -0.090651 | -0.022912 | 0.090658 | 0.022916 | 6.4384e-06 | 4.109e-06 | 0.13715 | 0.13715 | 0.13715 | 0.98403 | -0.30536 | 0.98411 | -0.30388 | 37.6781
41 | 0.0081903 | 0.002053 | -0.0081874 | -0.0020518 | 2.8665e-06 | 1.2171e-06 | 0.012462 | 0.012462 | 0.012462 | 0.978 | -0.42332 | 0.97763 | -0.43067 | 3.4236
42 | -0.0081903 | -0.002053 | 0.0081915 | 0.0020535 | 1.1932e-06 | 5.0649e-07 | 0.012462 | 0.012461 | 0.012462 | 0.978 | -0.42332 | 0.97816 | -0.42026 | 3.4235
43 | 0.0040971 | 0.0010267 | -0.0040967 | -0.0010267 | 3.586e-07 | -7.8804e-08 | 0.0062359 | 0.0062361 | 0.0062361 | 0.97763 | -0.43067 | 0.97754 | -0.4325 | 1.7132
44 | -0.014934 | -0.0037434 | 0.014938 | 0.0037457 | 3.8463e-06 | 2.2121e-06 | 0.022719 | 0.022719 | 0.022719 | 0.97816 | -0.42026 | 0.97844 | -0.41486 | 6.2415
45 | -0.099542 | -0.025142 | 0.099775 | 0.025291 | 0.00023296 | 0.00014875 | 0.15058 | 0.15058 | 0.15058 | 0.98411 | -0.30388 | 0.98663 | -0.25517 | 41.3686
46 | -0.10322 | -0.026155 | 0.10323 | 0.026158 | 3.9843e-06 | 2.5444e-06 | 0.15578 | 0.15578 | 0.15578 | 0.98663 | -0.25517 | 0.98667 | -0.25437 | 42.7972
47 | -0.10541 | -0.026705 | 0.10573 | 0.026911 | 0.00032297 | 0.00020626 | 0.15908 | 0.15907 | 0.15908 | 0.98667 | -0.25437 | 0.98997 | -0.1908 | 43.7019
48 | -0.10877 | -0.027673 | 0.10892 | 0.027768 | 0.00014807 | 9.4573e-05 | 0.16364 | 0.16364 | 0.16364 | 0.98997 | -0.1908 | 0.99144 | -0.1626 | 44.9569
49 | 0.10673 | 0.027173 | -0.10658 | -0.027073 | 0.00015654 | 9.9978e-05 | 0.16034 | 0.16034 | 0.16034 | 0.99144 | -0.1626 | 0.98985 | -0.19306 | 44.0507
50 | -0.21566 | -0.054941 | 0.21631 | 0.055358 | 0.00065298 | 0.00041705 | 0.32399 | 0.32399 | 0.32399 | 0.99144 | -0.1626 | 0.99472 | -0.10004 | 44.5038
51 | -0.0048232 | -0.0012088 | 0.0048233 | 0.0012088 | 4.8766e-08 | 2.2001e-10 | 0.0072974 | 0.0072974 | 0.0072974 | 0.98351 | -0.31699 | 0.98352 | -0.31678 | 2.0048
52 | -0.0094839 | -0.0023769 | 0.0094865 | 0.0023781 | 2.5564e-06 | 1.2158e-06 | 0.014349 | 0.014349 | 0.014349 | 0.98352 | -0.31678 | 0.98381 | -0.31112 | 3.9419
53 | -0.01335 | -0.0033463 | 0.013351 | 0.0033468 | 9.292e-07 | 5.1751e-07 | 0.020192 | 0.020192 | 0.020192 | 0.98381 | -0.31112 | 0.98388 | -0.30966 | 5.5472
54 | -0.10475 | -0.026424 | 0.10505 | 0.026618 | 0.00030466 | 0.00019455 | 0.15648 | 0.15648 | 0.15648 | 0.99646 | -0.067718 | 0.99962 | -0.0071621 | 42.9902
55 | -0.10935 | -0.027695 | 0.10939 | 0.027719 | 3.7627e-05 | 2.4031e-05 | 0.16288 | 0.16288 | 0.16288 | 0.99962 | -0.0071621 | 1 | 0 | 44.7477
56 | -0.0049481 | -0.0012401 | 0.004949 | 0.0012401 | 8.9313e-07 | 3.3927e-08 | 0.0074923 | 0.0074921 | 0.0074923 | 0.98272 | -0.33237 | 0.98291 | -0.32858 | 2.0583
57 | -0.010471 | -0.0026241 | 0.010474 | 0.0026258 | 3.3466e-06 | 1.6915e-06 | 0.015852 | 0.015852 | 0.015852 | 0.98291 | -0.32858 | 0.98326 | -0.32187 | 4.3549
58 | -0.015396 | -0.0038593 | 0.015403 | 0.0038629 | 6.2092e-06 | 3.5869e-06 | 0.0233 | 0.0233 | 0.0233 | 0.98326 | -0.32187 | 0.98369 | -0.31341 | 6.4012
59 | -0.019191 | -0.0048123 | 0.019199 | 0.0048171 | 8.0579e-06 | 4.8332e-06 | 0.02903 | 0.02903 | 0.02903 | 0.98369 | -0.31341 | 0.98414 | -0.3046 | 7.9754
60 | -0.019199 | -0.0048171 | 0.019212 | 0.0048252 | 1.3437e-05 | 8.0588e-06 | 0.02903 | 0.02903 | 0.02903 | 0.98414 | -0.3046 | 0.98489 | -0.28994 | 7.9753
61 | -0.0033014 | -0.00082741 | 0.0033016 | 0.00082728 | 1.6994e-07 | -1.2301e-07 | 0.0049881 | 0.0049881 | 0.0049881 | 0.98484 | -0.29102 | 0.98489 | -0.28994 | 1.3704
62 | -0.022514 | -0.0056525 | 0.022528 | 0.0056614 | 1.4585e-05 | 8.9061e-06 | 0.034018 | 0.034018 | 0.034018 | 0.98489 | -0.28994 | 0.98559 | -0.27637 | 9.3456
63 | 0.029551 | 0.0074204 | -0.029533 | -0.0074091 | 1.8079e-05 | 1.1262e-05 | 0.044621 | 0.044621 | 0.044621 | 0.98559 | -0.27637 | 0.98493 | -0.2892 | 12.2585
64 | -0.05208 | -0.013082 | 0.05214 | 0.01312 | 6.0494e-05 | 3.8383e-05 | 0.078639 | 0.078639 | 0.078639 | 0.98559 | -0.27637 | 0.98684 | -0.25206 | 21.6041
65 | 0.02522 | 0.0063282 | -0.025219 | -0.0063276 | 9.0862e-07 | 5.6028e-07 | 0.038105 | 0.038105 | 0.038105 | 0.98493 | -0.2892 | 0.98489 | -0.28995 | 10.4684
66 | -0.054444 | -0.013698 | 0.054513 | 0.013741 | 6.8891e-05 | 4.3742e-05 | 0.082113 | 0.082113 | 0.082113 | 0.98684 | -0.25206 | 0.9882 | -0.22561 | 22.5586
67 | 0.022099 | 0.0055456 | -0.022086 | -0.0055374 | 1.3311e-05 | 8.1141e-06 | 0.033391 | 0.033391 | 0.033391 | 0.98489 | -0.28995 | 0.98425 | -0.30259 | 9.1733
68 | -0.054513 | -0.013741 | 0.054552 | 0.013766 | 3.89e-05 | 2.4699e-05 | 0.082113 | 0.082113 | 0.082113 | 0.9882 | -0.22561 | 0.98897 | -0.21071 | 22.5585
69 | 0.023095 | 0.0057929 | -0.023094 | -0.0057923 | 1.1048e-06 | 6.7595e-07 | 0.034804 | 0.034804 | 0.034804 | 0.98746 | -0.24009 | 0.98741 | -0.2411 | 9.5614
70 | -0.027797 | -0.0069713 | 0.027818 | 0.0069843 | 2.0917e-05 | 1.298e-05 | 0.041889 | 0.041889 | 0.041889 | 0.98746 | -0.24009 | 0.98827 | -0.22432 | 11.5079
71 | 0.019573 | 0.0049099 | -0.019564 | -0.0049042 | 9.5042e-06 | 5.7103e-06 | 0.029498 | 0.029498 | 0.029498 | 0.98741 | -0.2411 | 0.98689 | -0.25129 | 8.104
72 | -0.032705 | -0.0082092 | 0.032726 | 0.0082225 | 2.1245e-05 | 1.3298e-05 | 0.049248 | 0.049248 | 0.049248 | 0.98827 | -0.22432 | 0.98897 | -0.21071 | 13.5296
73 | -0.087279 | -0.021989 | 0.087344 | 0.02203 | 6.5054e-05 | 4.1505e-05 | 0.13136 | 0.13136 | 0.13136 | 0.98897 | -0.21071 | 0.98978 | -0.19514 | 36.0881
74 | -0.090385 | -0.022792 | 0.090477 | 0.022851 | 9.2052e-05 | 5.8743e-05 | 0.13593 | 0.13593 | 0.13593 | 0.98978 | -0.19514 | 0.99088 | -0.17388 | 37.344
75 | -0.092843 | -0.023444 | 0.093 | 0.023544 | 0.00015694 | 0.00010016 | 0.13949 | 0.13949 | 0.13949 | 0.99088 | -0.17388 | 0.99271 | -0.13867 | 38.3201
76 | 0.32442 | 0.083366 | -0.32359 | -0.082839 | 0.00082523 | 0.00052704 | 0.48347 | 0.48347 | 0.48347 | 1 | 0 | 0.99722 | -0.052512 | 44.2737
77 | -0.095381 | -0.024141 | 0.095398 | 0.024152 | 1.6937e-05 | 1.0811e-05 | 0.14305 | 0.14305 | 0.14305 | 0.99271 | -0.13867 | 0.9929 | -0.13497 | 39.3006
78 | -0.099712 | -0.025233 | 0.099912 | 0.025361 | 0.00020026 | 0.00012786 | 0.14952 | 0.14952 | 0.14952 | 0.9929 | -0.13497 | 0.99508 | -0.093214 | 41.0769
79 | -0.31982 | -0.081648 | 0.32045 | 0.082051 | 0.0006304 | 0.0004026 | 0.47878 | 0.47878 | 0.47878 | 0.99508 | -0.093214 | 0.99722 | -0.052512 | 43.844
80 | 0.2199 | 0.056287 | -0.21983 | -0.056241 | 7.2705e-05 | 4.6322e-05 | 0.32926 | 0.32926 | 0.32926 | 0.99508 | -0.093214 | 0.99472 | -0.10004 | 30.1518
81 | 0.016548 | 0.0041496 | -0.016548 | -0.0041496 | 1.1917e-07 | 6.9818e-08 | 0.025019 | 0.025019 | 0.025019 | 0.98425 | -0.30259 | 0.98424 | -0.30274 | 6.8734
82 | 0.013355 | 0.0033493 | -0.013351 | -0.0033468 | 4.4028e-06 | 2.452e-06 | 0.020192 | 0.020192 | 0.020192 | 0.98424 | -0.30274 | 0.98388 | -0.30966 | 5.5472
83 | 0.10294 | 0.026162 | -0.1027 | -0.026011 | 0.00023656 | 0.00015106 | 0.15488 | 0.15488 | 0.15488 | 0.98985 | -0.19306 | 0.98737 | -0.2409 | 42.5489
84 | 0.10099 | 0.025581 | -0.10082 | -0.025473 | 0.00016877 | 0.00010776 | 0.15229 | 0.15229 | 0.15229 | 0.98737 | -0.2409 | 0.98557 | -0.27576 | 41.8383
85 | -0.001607 | -0.00040276 | 0.001607 | 0.00040263 | 2.4945e-08 | -1.2735e-07 | 0.0024292 | 0.0024292 | 0.0024292 | 0.98438 | -0.29894 | 0.9844 | -0.29862 | 0.66737
86 | 0.0028065 | 0.00070257 | -0.0028063 | -0.00070278 | 1.7054e-07 | -2.1211e-07 | 0.004242 | 0.0042422 | 0.0042422 | 0.9844 | -0.29862 | 0.98433 | -0.2999 | 1.1654
87 | -0.0044136 | -0.0011052 | 0.004414 | 0.0011051 | 4.0321e-07 | -4.9125e-08 | 0.0066712 | 0.0066711 | 0.0066712 | 0.9844 | -0.29862 | 0.98449 | -0.2967 | 1.8327
88 | 0.00078546 | 0.0001963 | -0.00078545 | -0.00019661 | 1.3363e-08 | -3.128e-07 | 0.0011872 | 0.0011873 | 0.0011873 | 0.98433 | -0.2999 | 0.98431 | -0.30025 | 0.32618
89 | -0.0063854 | -0.0015992 | 0.0063858 | 0.0015994 | 4.5206e-07 | 1.2473e-07 | 0.0096508 | 0.0096507 | 0.0096508 | 0.98449 | -0.2967 | 0.98457 | -0.29521 | 2.6513
90 | 0.0099076 | 0.0024824 | -0.0099068 | -0.002482 | 7.862e-07 | 3.8415e-07 | 0.01497 | 0.01497 | 0.01497 | 0.9848 | -0.29072 | 0.98472 | -0.29239 | 4.1126
91 | -0.011614 | -0.0029101 | 0.011615 | 0.0029107 | 1.1725e-06 | 6.2119e-07 | 0.017548 | 0.017548 | 0.017548 | 0.9848 | -0.29072 | 0.98491 | -0.2886 | 4.821
92 | 0.0081831 | 0.00205 | -0.008182 | -0.0020495 | 1.1017e-06 | 4.6071e-07 | 0.012365 | 0.012365 | 0.012365 | 0.98472 | -0.29239 | 0.98457 | -0.29521 | 3.3971
93 | -0.013105 | -0.0032841 | 0.013108 | 0.0032856 | 2.6959e-06 | 1.4919e-06 | 0.0198 | 0.019799 | 0.0198 | 0.98491 | -0.2886 | 0.98513 | -0.28428 | 5.4394
94 | -0.015035 | -0.0037685 | 0.015035 | 0.0037686 | 2.9753e-07 | 1.7083e-07 | 0.02271 | 0.02271 | 0.02271 | 0.98513 | -0.28428 | 0.98515 | -0.28387 | 6.2389
95 | -0.016496 | -0.0041349 | 0.016501 | 0.0041374 | 4.2426e-06 | 2.4832e-06 | 0.024917 | 0.024917 | 0.024917 | 0.98515 | -0.28387 | 0.98543 | -0.27847 | 6.8454
96 | -0.017963 | -0.004504 | 0.017966 | 0.0045053 | 2.3211e-06 | 1.3783e-06 | 0.027126 | 0.027126 | 0.027126 | 0.98543 | -0.27847 | 0.98557 | -0.27576 | 7.4521
97 | 0.044547 | 0.011189 | -0.044544 | -0.011187 | 2.8567e-06 | 1.8073e-06 | 0.067641 | 0.067641 | 0.067641 | 0.9801 | -0.38216 | 0.98003 | -0.3835 | 18.5828
98 | -0.047198 | -0.011853 | 0.047226 | 0.011871 | 2.7468e-05 | 1.74e-05 | 0.071666 | 0.071666 | 0.071666 | 0.9801 | -0.38216 | 0.98073 | -0.36997 | 19.6885
99 | 0.042657 | 0.010714 | -0.042621 | -0.010691 | 3.6e-05 | 2.2752e-05 | 0.064775 | 0.064775 | 0.064775 | 0.98003 | -0.3835 | 0.97913 | -0.4012 | 17.7954
100 | -0.077346 | -0.019447 | 0.077447 | 0.019511 | 0.00010119 | 6.4514e-05 | 0.11738 | 0.11738 | 0.11738 | 0.98073 | -0.36997 | 0.98213 | -0.34261 | 32.2461
101 | 0.03012 | 0.007576 | -0.030106 | -0.0075669 | 1.4539e-05 | 9.0709e-06 | 0.04571 | 0.04571 | 0.04571 | 0.98073 | -0.36997 | 0.98021 | -0.38008 | 12.5577
102 | 0.0074568 | 0.0018687 | -0.0074562 | -0.0018684 | 5.9977e-07 | 2.2723e-07 | 0.011332 | 0.011332 | 0.011332 | 0.97913 | -0.4012 | 0.97904 | -0.40289 | 3.1133
103 | 0.035164 | 0.0088228 | -0.035161 | -0.008821 | 2.9169e-06 | 1.8325e-06 | 0.053443 | 0.053443 | 0.053443 | 0.97913 | -0.4012 | 0.97904 | -0.40294 | 14.6822
104 | -0.079739 | -0.020086 | 0.079798 | 0.020123 | 5.8728e-05 | 3.745e-05 | 0.12085 | 0.12085 | 0.12085 | 0.98213 | -0.34261 | 0.98292 | -0.32722 | 33.2003
105 | 0.028614 | 0.0071931 | -0.028595 | -0.0071815 | 1.8659e-05 | 1.161e-05 | 0.043445 | 0.043446 | 0.043446 | 0.98021 | -0.38008 | 0.97951 | -0.39374 | 11.9356
106 | 0.0033517 | 0.00083977 | -0.0033515 | -0.00083995 | 2.8617e-07 | -1.8661e-07 | 0.0050941 | 0.0050942 | 0.0050942 | 0.97904 | -0.40289 | 0.97895 | -0.40468 | 1.3995
107 | 0.028436 | 0.0071357 | -0.02842 | -0.0071256 | 1.6145e-05 | 1.0043e-05 | 0.043223 | 0.043223 | 0.043223 | 0.97904 | -0.40294 | 0.97844 | -0.41486 | 11.8744
108 | -0.08119 | -0.020472 | 0.081326 | 0.020559 | 0.00013589 | 8.6668e-05 | 0.12296 | 0.12296 | 0.12296 | 0.98292 | -0.32722 | 0.98471 | -0.29232 | 33.7793
109 | 0.025895 | 0.006505 | -0.02588 | -0.0064958 | 1.5022e-05 | 9.2883e-06 | 0.039344 | 0.039344 | 0.039344 | 0.97951 | -0.39374 | 0.97889 | -0.40591 | 10.8088
110 | 0.0027001 | 0.00067642 | -0.0026999 | -0.00067659 | 1.2529e-07 | -1.6976e-07 | 0.0041017 | 0.0041018 | 0.0041018 | 0.97951 | -0.39374 | 0.97946 | -0.39472 | 1.1269
111 | 0.013482 | 0.00338 | -0.01348 | -0.0033787 | 2.3356e-06 | 1.3087e-06 | 0.020504 | 0.020504 | 0.020504 | 0.97844 | -0.41486 | 0.97825 | -0.41849 | 5.633
112 | -0.082788 | -0.020925 | 0.082854 | 0.020967 | 6.5781e-05 | 4.1957e-05 | 0.12517 | 0.12517 | 0.12517 | 0.98471 | -0.29232 | 0.98557 | -0.27576 | 34.3863
113 | 0.02279 | 0.0057214 | -0.022782 | -0.0057162 | 8.5359e-06 | 5.2247e-06 | 0.034647 | 0.034647 | 0.034647 | 0.97889 | -0.40591 | 0.97849 | -0.41376 | 9.5185
114 | 0.0011701 | 0.00029318 | -0.0011701 | -0.00029326 | 7.5634e-09 | -7.5487e-08 | 0.0017776 | 0.0017777 | 0.0017777 | 0.97946 | -0.39472 | 0.97945 | -0.39485 | 0.48837
115 | 0.008604 | 0.0021567 | -0.0086024 | -0.002156 | 1.553e-06 | 6.9044e-07 | 0.013088 | 0.013088 | 0.013088 | 0.97825 | -0.41849 | 0.97806 | -0.42228 | 3.5955
116 | 0.00078545 | 0.00019661 | -0.00078544 | -0.00019685 | 1.018e-08 | -2.3825e-07 | 0.0011873 | 0.0011874 | 0.0011874 | 0.98431 | -0.30025 | 0.9843 | -0.30053 | 0.32621
117 | -0.0019206 | -0.00048135 | 0.0019207 | 0.00048113 | 6.6682e-08 | -2.1763e-07 | 0.002925 | 0.0029249 | 0.002925 | 0.97704 | -0.44217 | 0.97708 | -0.44144 | 0.80358
118 | -0.010136 | -0.0025398 | 0.010138 | 0.0025406 | 1.76e-06 | 8.7966e-07 | 0.015436 | 0.015436 | 0.015436 | 0.97708 | -0.44144 | 0.97727 | -0.43779 | 4.2406
119 | 0.0056963 | 0.0014273 | -0.005695 | -0.0014271 | 1.3142e-06 | 2.5797e-07 | 0.0086749 | 0.0086751 | 0.0086751 | 0.97708 | -0.44144 | 0.97684 | -0.44628 | 2.3833
120 | 0.0036958 | 0.00092603 | -0.0036956 | -0.00092612 | 2.2038e-07 | -9.1056e-08 | 0.0056298 | 0.0056299 | 0.0056299 | 0.97684 | -0.44628 | 0.97677 | -0.44753 | 1.5467
121 | 0.0017954 | 0.00044988 | -0.0017954 | -0.00044996 | 2.1958e-08 | -8.392e-08 | 0.0027351 | 0.0027351 | 0.0027351 | 0.97677 | -0.44753 | 0.97676 | -0.44779 | 0.7514
122 | -0.012674 | -0.0031762 | 0.012676 | 0.0031776 | 2.6702e-06 | 1.4693e-06 | 0.019297 | 0.019297 | 0.019297 | 0.97727 | -0.43779 | 0.97749 | -0.43337 | 5.3014
123 | -0.015258 | -0.0038248 | 0.015262 | 0.0038271 | 3.9465e-06 | 2.2812e-06 | 0.023228 | 0.023227 | 0.023228 | 0.97749 | -0.43337 | 0.97777 | -0.42794 | 6.3812
124 | -0.01766 | -0.0044281 | 0.017666 | 0.0044315 | 5.7375e-06 | 3.4062e-06 | 0.026877 | 0.026877 | 0.026877 | 0.97777 | -0.42794 | 0.97811 | -0.42113 | 7.3839
125 | -0.020335 | -0.0051003 | 0.020342 | 0.0051046 | 7.1445e-06 | 4.3225e-06 | 0.030937 | 0.030937 | 0.030937 | 0.97811 | -0.42113 | 0.97849 | -0.41376 | 8.4991

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.43907 | 0.11199

## res_load
| p_mw | q_mvar
0 | 0.007831 | 0.0019626
1 | 0.011221 | 0.0028124
2 | 0.0058971 | 0.001478
3 | 0.0056786 | 0.0014232
4 | 0.0087481 | 0.0021925
5 | 0.0043315 | 0.0010856
6 | 0.006074 | 0.0015223
7 | 0.0092445 | 0.0023169
8 | 0.010893 | 0.0027301
9 | 0.0074936 | 0.0018781
10 | 0.0047807 | 0.0011981
11 | 0.0014791 | 0.00037069
12 | 0.0053759 | 0.0013473
13 | 0.0038864 | 0.00097401
14 | 0.0044741 | 0.0011213
15 | 0.0065058 | 0.0016305
16 | 0.0074588 | 0.0018694
17 | 0.0056502 | 0.0014161
18 | 0.0041741 | 0.0010461
19 | 0.0036236 | 0.00090816
20 | 0.0053368 | 0.0013375
21 | 0.005307 | 0.0013301
22 | 0.0043809 | 0.001098
23 | 0.0085204 | 0.0021354
24 | 0.0081356 | 0.002039
25 | 0.0025854 | 0.00064797
26 | 0.010237 | 0.0025657
27 | 0.0073849 | 0.0018508
28 | 0.0068776 | 0.0017237
29 | 0.0043687 | 0.0010949
30 | 0.0040904 | 0.0010251
31 | 0.0067429 | 0.0016899
32 | 0.0061891 | 0.0015511
33 | 0.0088842 | 0.0022266
34 | 0.0034481 | 0.00086418
35 | 0.0021836 | 0.00054725
36 | 0.0030393 | 0.00076173
37 | 0.0048232 | 0.0012088
38 | 0.0046606 | 0.0011681
39 | 0.0038633 | 0.00096823
40 | 0.0045011 | 0.0011281
41 | 0.0054874 | 0.0013753
42 | 0.0042978 | 0.0010771
43 | 0.0049481 | 0.0012401
44 | 0.0055221 | 0.001384
45 | 0.0049219 | 0.0012335
46 | 0.0037881 | 0.00094938
47 | 0.0033014 | 0.00082741
48 | 0.0043129 | 0.0010809
49 | 0.0023042 | 0.00057749
50 | 0.0031205 | 0.00078206
51 | 0.0047018 | 0.0011784
52 | 0.0035205 | 0.00088231
53 | 0.0048875 | 0.0012249
54 | 0.0052746 | 0.0013219
55 | 0.0030409 | 0.00076213
56 | 0.0045968 | 0.0011521
57 | 0.002366 | 0.00059298
58 | 0.0036123 | 0.00090533
59 | 0.0023812 | 0.00059678
60 | 0.0043143 | 0.0010813
61 | 0.0031443 | 0.00078803
62 | 0.0035231 | 0.00088298
63 | 0.0055374 | 0.0013878
64 | 0.0031932 | 0.00080028
65 | 0.0036364 | 0.00091136
66 | 0.0017165 | 0.00043019
67 | 0.001607 | 0.00040276
68 | 0.0020209 | 0.00050648
69 | 0.0019714 | 0.00049408
70 | 0.0017065 | 0.00042769
71 | 0.0017237 | 0.000432
72 | 0.00149 | 0.00037343
73 | 0.0017962 | 0.00045017
74 | 0.0019267 | 0.00048287
75 | 0.0014615 | 0.00036629
76 | 0.0014626 | 0.00036656
77 | 0.002651 | 0.00066441
78 | 0.0018876 | 0.00047307
79 | 0.0022925 | 0.00057455
80 | 0.0014916 | 0.00037384
81 | 0.0041045 | 0.0010287
82 | 0.0067244 | 0.0016853
83 | 0.0013922 | 0.00034892
84 | 0.0033515 | 0.00083995
85 | 0.0014621 | 0.00036645
86 | 0.0030898 | 0.00077437
87 | 0.0015298 | 0.00038341
88 | 0.0048758 | 0.001222
89 | 0.00078544 | 0.00019685
90 | 0.0086024 | 0.002156
91 | 0.0040967 | 0.0010267
92 | 0.0019206 | 0.00048135
93 | 0.0025189 | 0.0006313
94 | 0.0019992 | 0.00050103
95 | 0.0019002 | 0.00047624
96 | 0.0017954 | 0.00044996
97 | 0.0025359 | 0.00063555
98 | 0.002582 | 0.00064712
99 | 0.0023983 | 0.00060108
100 | 0.0026685 | 0.00066878
101 | 0.00244 | 0.00061152
102 | 0.0011701 | 0.00029326

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1