## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_2148-8_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_2148-8_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_2148-8_0_3_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_2148-8_0_3_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_2148-8_0_3_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_2148-8_0_3_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_2148-8_0_3_node_66 | 0.4 | n |  | TRUE
7 | bus_LV_2148-8_0_3_node_65 | 0.4 | n |  | TRUE
8 | bus_LV_2148-8_0_3_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_2148-8_0_3_node_101 | 0.4 | n |  | TRUE
10 | bus_LV_2148-8_0_3_node_102 | 0.4 | n |  | TRUE
11 | bus_LV_2148-8_0_3_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_2148-8_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_2148-8_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_2148-8_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_2148-8_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_2148-8_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_2148-8_0_3_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_2148-8_0_3_node_94 | 0.4 | n |  | TRUE
19 | bus_LV_2148-8_0_3_node_69 | 0.4 | n |  | TRUE
20 | bus_LV_2148-8_0_3_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_2148-8_0_3_node_96 | 0.4 | n |  | TRUE
22 | bus_LV_2148-8_0_3_node_93 | 0.4 | n |  | TRUE
23 | bus_LV_2148-8_0_3_node_58 | 0.4 | n |  | TRUE
24 | bus_LV_2148-8_0_3_node_67 | 0.4 | n |  | TRUE
25 | bus_LV_2148-8_0_3_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_2148-8_0_3_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_2148-8_0_3_node_16 | 0.4 | n |  | TRUE
28 | bus_LV_2148-8_0_3_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_2148-8_0_3_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_2148-8_0_3_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_2148-8_0_3_node_52 | 0.4 | n |  | TRUE
32 | bus_LV_2148-8_0_3_node_33 | 0.4 | n |  | TRUE
33 | bus_LV_2148-8_0_3_node_81 | 0.4 | n |  | TRUE
34 | bus_LV_2148-8_0_3_node_53 | 0.4 | n |  | TRUE
35 | bus_LV_2148-8_0_3_node_104 | 0.4 | n |  | TRUE
36 | bus_LV_2148-8_0_3_node_82 | 0.4 | n |  | TRUE
37 | bus_LV_2148-8_0_3_node_32 | 0.4 | n |  | TRUE
38 | bus_LV_2148-8_0_3_node_79 | 0.4 | n |  | TRUE
39 | bus_LV_2148-8_0_3_node_19 | 0.4 | n |  | TRUE
40 | bus_LV_2148-8_0_3_node_20 | 0.4 | n |  | TRUE
41 | bus_LV_2148-8_0_3_node_22 | 0.4 | n |  | TRUE
42 | bus_LV_2148-8_0_3_node_23 | 0.4 | n |  | TRUE
43 | bus_LV_2148-8_0_3_node_24 | 0.4 | n |  | TRUE
44 | bus_LV_2148-8_0_3_node_42 | 0.4 | n |  | TRUE
45 | bus_LV_2148-8_0_3_node_95 | 0.4 | n |  | TRUE
46 | bus_LV_2148-8_0_3_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_2148-8_0_3_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_2148-8_0_3_node_97 | 0.4 | n |  | TRUE
49 | bus_LV_2148-8_0_3_node_36 | 0.4 | n |  | TRUE
50 | bus_LV_2148-8_0_3_node_26 | 0.4 | n |  | TRUE
51 | bus_LV_2148-8_0_3_node_27 | 0.4 | n |  | TRUE
52 | bus_LV_2148-8_0_3_node_28 | 0.4 | n |  | TRUE
53 | bus_LV_2148-8_0_3_node_29 | 0.4 | n |  | TRUE
54 | bus_LV_2148-8_0_3_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_2148-8_0_3_node_41 | 0.4 | n |  | TRUE
56 | bus_LV_2148-8_0_3_node_38 | 0.4 | n |  | TRUE
57 | bus_LV_2148-8_0_3_node_80 | 0.4 | n |  | TRUE
58 | bus_LV_2148-8_0_3_node_46 | 0.4 | n |  | TRUE
59 | bus_LV_2148-8_0_3_node_39 | 0.4 | n |  | TRUE
60 | bus_LV_2148-8_0_3_node_62 | 0.4 | n |  | TRUE
61 | bus_LV_2148-8_0_3_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_2148-8_0_3_node_45 | 0.4 | n |  | TRUE
63 | bus_LV_2148-8_0_3_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_2148-8_0_3_node_77 | 0.4 | n |  | TRUE
65 | bus_LV_2148-8_0_3_node_85 | 0.4 | n |  | TRUE
66 | bus_LV_2148-8_0_3_node_83 | 0.4 | n |  | TRUE
67 | bus_LV_2148-8_0_3_node_48 | 0.4 | n |  | TRUE
68 | bus_LV_2148-8_0_3_node_44 | 0.4 | n |  | TRUE
69 | bus_LV_2148-8_0_3_node_47 | 0.4 | n |  | TRUE
70 | bus_LV_2148-8_0_3_node_72 | 0.4 | n |  | TRUE
71 | bus_LV_2148-8_0_3_node_73 | 0.4 | n |  | TRUE
72 | bus_LV_2148-8_0_3_node_49 | 0.4 | n |  | TRUE
73 | bus_LV_2148-8_0_3_node_50 | 0.4 | n |  | TRUE
74 | bus_LV_2148-8_0_3_node_51 | 0.4 | n |  | TRUE
75 | bus_LV_2148-8_0_3_node_91 | 0.4 | n |  | TRUE
76 | bus_LV_2148-8_0_3_node_92 | 0.4 | n |  | TRUE
77 | bus_LV_2148-8_0_3_node_103 | 0.4 | n |  | TRUE
78 | bus_LV_2148-8_0_3_node_54 | 0.4 | n |  | TRUE
79 | bus_LV_2148-8_0_3_node_55 | 0.4 | n |  | TRUE
80 | bus_LV_2148-8_0_3_node_56 | 0.4 | n |  | TRUE
81 | bus_LV_2148-8_0_3_node_57 | 0.4 | n |  | TRUE
82 | bus_LV_2148-8_0_3_node_63 | 0.4 | n |  | TRUE
83 | bus_LV_2148-8_0_3_node_64 | 0.4 | n |  | TRUE
84 | bus_LV_2148-8_0_3_node_59 | 0.4 | n |  | TRUE
85 | bus_LV_2148-8_0_3_node_60 | 0.4 | n |  | TRUE
86 | bus_LV_2148-8_0_3_node_61 | 0.4 | n |  | TRUE
87 | bus_LV_2148-8_0_3_node_119 | 0.4 | n |  | TRUE
88 | bus_LV_2148-8_0_3_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_2148-8_0_3_node_68 | 0.4 | n |  | TRUE
90 | bus_LV_2148-8_0_3_node_70 | 0.4 | n |  | TRUE
91 | bus_LV_2148-8_0_3_node_71 | 0.4 | n |  | TRUE
92 | bus_LV_2148-8_0_3_node_74 | 0.4 | n |  | TRUE
93 | bus_LV_2148-8_0_3_node_75 | 0.4 | n |  | TRUE
94 | bus_LV_2148-8_0_3_node_76 | 0.4 | n |  | TRUE
95 | bus_LV_2148-8_0_3_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_2148-8_0_3_node_98 | 0.4 | n |  | TRUE
97 | bus_LV_2148-8_0_3_node_84 | 0.4 | n |  | TRUE
98 | bus_LV_2148-8_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_2148-8_0_3_node_88 | 0.4 | n |  | TRUE
100 | bus_LV_2148-8_0_3_node_87 | 0.4 | n |  | TRUE
101 | bus_LV_2148-8_0_3_node_89 | 0.4 | n |  | TRUE
102 | bus_LV_2148-8_0_3_node_118 | 0.4 | n |  | TRUE
103 | bus_LV_2148-8_0_3_node_99 | 0.4 | n |  | TRUE
104 | bus_LV_2148-8_0_3_node_117 | 0.4 | n |  | TRUE
105 | bus_LV_2148-8_0_3_node_100 | 0.4 | n |  | TRUE
106 | bus_LV_2148-8_0_3_node_105 | 0.4 | n |  | TRUE
107 | bus_LV_2148-8_0_3_node_106 | 0.4 | n |  | TRUE
108 | bus_LV_2148-8_0_3_node_107 | 0.4 | n |  | TRUE
109 | bus_LV_2148-8_0_3_node_108 | 0.4 | n |  | TRUE
110 | bus_LV_2148-8_0_3_node_109 | 0.4 | n |  | TRUE
111 | bus_LV_2148-8_0_3_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_2148-8_0_3_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_2148-8_0_3_node_112 | 0.4 | n |  | TRUE
114 | bus_LV_2148-8_0_3_node_115 | 0.4 | n |  | TRUE
115 | bus_LV_2148-8_0_3_node_110 | 0.4 | n |  | TRUE
116 | bus_LV_2148-8_0_3_node_111 | 0.4 | n |  | TRUE
117 | bus_LV_2148-8_0_3_node_116 | 0.4 | n |  | TRUE
118 | bus_MV_31_0_node_161 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_2148-8_0_3_load_0 | 0 | 0.0034451 | 0.00086342 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_2148-8_0_3_load_1 | 1 | 0.0021602 | 0.00054141 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_2148-8_0_3_load_3 | 2 | 0.0016288 | 0.00040821 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_2148-8_0_3_load_6 | 3 | 0.0046851 | 0.0011742 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_2148-8_0_3_load_7 | 4 | 0.0051242 | 0.0012842 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_2148-8_0_3_load_4 | 5 | 0.002089 | 0.00052355 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_2148-8_0_3_load_66 | 6 | 0.0012128 | 0.00030396 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_2148-8_0_3_load_65 | 7 | 0.0017794 | 0.00044596 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_2148-8_0_3_load_8 | 8 | 0.003183 | 0.00079773 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_2148-8_0_3_load_101 | 9 | 0.0040957 | 0.0010265 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_2148-8_0_3_load_102 | 10 | 0.0066938 | 0.0016776 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_2148-8_0_3_load_30 | 11 | 0.0043756 | 0.0010966 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_2148-8_0_3_load_9 | 12 | 0.0047681 | 0.001195 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_2148-8_0_3_load_11 | 14 | 0.0043568 | 0.0010919 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_2148-8_0_3_load_13 | 16 | 0.0037792 | 0.00094715 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_2148-8_0_3_load_25 | 17 | 0.0050402 | 0.0012632 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_2148-8_0_3_load_96 | 21 | 0.0036647 | 0.00091846 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_2148-8_0_3_load_93 | 22 | 0.0050043 | 0.0012542 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_2148-8_0_3_load_58 | 23 | 0.0013696 | 0.00034325 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_2148-8_0_3_load_67 | 24 | 0.0032285 | 0.00080913 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_2148-8_0_3_load_14 | 25 | 0.0028622 | 0.00071734 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_2148-8_0_3_load_15 | 26 | 0.004264 | 0.0010687 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_2148-8_0_3_load_16 | 27 | 0.0020577 | 0.00051571 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_2148-8_0_3_load_17 | 28 | 0.0034579 | 0.00086662 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_2148-8_0_3_load_18 | 29 | 0.00098858 | 0.00024776 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_2148-8_0_3_load_34 | 30 | 0.0027551 | 0.00069048 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_2148-8_0_3_load_52 | 31 | 0.005433 | 0.0013616 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_2148-8_0_3_load_33 | 32 | 0.002416 | 0.00060551 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_2148-8_0_3_load_81 | 33 | 0.004276 | 0.0010717 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_2148-8_0_3_load_53 | 34 | 0.0047209 | 0.0011832 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_2148-8_0_3_load_104 | 35 | 0.0020137 | 0.00050469 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_2148-8_0_3_load_82 | 36 | 0.005525 | 0.0013847 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_2148-8_0_3_load_32 | 37 | 0.0023008 | 0.00057664 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_2148-8_0_3_load_79 | 38 | 0.0056754 | 0.0014224 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_2148-8_0_3_load_19 | 39 | 0.0036286 | 0.0009094 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_2148-8_0_3_load_22 | 41 | 0.0023683 | 0.00059356 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_2148-8_0_3_load_23 | 42 | 0.0019953 | 0.00050006 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_2148-8_0_3_load_24 | 43 | 0.0037114 | 0.00093016 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_2148-8_0_3_load_42 | 44 | 0.0023066 | 0.00057809 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_2148-8_0_3_load_35 | 46 | 0.0032191 | 0.00080679 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_2148-8_0_3_load_43 | 47 | 0.0044997 | 0.0011277 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_2148-8_0_3_load_97 | 48 | 0.0031649 | 0.00079321 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_2148-8_0_3_load_36 | 49 | 0.0030826 | 0.00077258 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_2148-8_0_3_load_26 | 50 | 0.0038756 | 0.00097132 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_2148-8_0_3_load_27 | 51 | 0.0039901 | 0.001 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_2148-8_0_3_load_31 | 54 | 0.0013105 | 0.00032845 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_2148-8_0_3_load_41 | 55 | 0.0029232 | 0.00073261 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_2148-8_0_3_load_38 | 56 | 0.0034449 | 0.00086337 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_2148-8_0_3_load_80 | 57 | 0.0020818 | 0.00052175 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_2148-8_0_3_load_39 | 59 | 0.0025697 | 0.00064402 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_2148-8_0_3_load_62 | 60 | 0.0025654 | 0.00064296 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_2148-8_0_3_load_37 | 61 | 0.0061311 | 0.0015366 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_2148-8_0_3_load_40 | 63 | 0.0028096 | 0.00070416 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_2148-8_0_3_load_85 | 65 | 0.0033909 | 0.00084985 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_2148-8_0_3_load_83 | 66 | 0.002982 | 0.00074735 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_2148-8_0_3_load_48 | 67 | 0.0028155 | 0.00070563 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_2148-8_0_3_load_44 | 68 | 0.0035372 | 0.00088652 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_2148-8_0_3_load_47 | 69 | 0.0032073 | 0.00080383 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_2148-8_0_3_load_72 | 70 | 0.0032134 | 0.00080535 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_2148-8_0_3_load_73 | 71 | 0.0077648 | 0.001946 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_2148-8_0_3_load_49 | 72 | 0.0034272 | 0.00085893 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_2148-8_0_3_load_50 | 73 | 0.0021279 | 0.00053331 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_2148-8_0_3_load_91 | 75 | 0.0026834 | 0.00067251 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_2148-8_0_3_load_92 | 76 | 0.0049345 | 0.0012367 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_2148-8_0_3_load_103 | 77 | 0.0037679 | 0.00094432 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_2148-8_0_3_load_54 | 78 | 0.0029554 | 0.0007407 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_2148-8_0_3_load_55 | 79 | 0.0022341 | 0.00055992 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_2148-8_0_3_load_56 | 80 | 0.0044477 | 0.0011147 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_2148-8_0_3_load_57 | 81 | 0.0019238 | 0.00048215 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_2148-8_0_3_load_63 | 82 | 0.0022657 | 0.00056784 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_2148-8_0_3_load_64 | 83 | 0.0015053 | 0.00037727 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_2148-8_0_3_load_59 | 84 | 0.00094386 | 0.00023655 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_2148-8_0_3_load_60 | 85 | 0.0028542 | 0.00071533 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_2148-8_0_3_load_61 | 86 | 0.0040415 | 0.0010129 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_2148-8_0_3_load_119 | 87 | 0.010513 | 0.0026347 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_2148-8_0_3_load_78 | 88 | 0.00099192 | 0.0002486 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_2148-8_0_3_load_68 | 89 | 0.0024786 | 0.0006212 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_2148-8_0_3_load_70 | 90 | 0.0025039 | 0.00062754 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_2148-8_0_3_load_71 | 91 | 0.0032585 | 0.00081665 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_2148-8_0_3_load_74 | 92 | 0.0024558 | 0.00061548 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_2148-8_0_3_load_75 | 93 | 0.0024935 | 0.00062493 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_2148-8_0_3_load_76 | 94 | 0.0027376 | 0.00068612 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_2148-8_0_3_load_86 | 95 | 0.003135 | 0.0007857 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_2148-8_0_3_load_98 | 96 | 0.0016023 | 0.00040157 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_2148-8_0_3_load_84 | 97 | 0.003668 | 0.00091928 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_2148-8_0_3_load_88 | 99 | 0.0020733 | 0.00051961 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_2148-8_0_3_load_87 | 100 | 0.0064924 | 0.0016271 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_2148-8_0_3_load_89 | 101 | 0.0066755 | 0.001673 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_2148-8_0_3_load_118 | 102 | 0.0015277 | 0.00038288 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_2148-8_0_3_load_99 | 103 | 0.0024354 | 0.00061036 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_2148-8_0_3_load_117 | 104 | 0.0014667 | 0.0003676 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_2148-8_0_3_load_100 | 105 | 0.0060392 | 0.0015136 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_2148-8_0_3_load_105 | 106 | 0.0022439 | 0.00056238 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_2148-8_0_3_load_106 | 107 | 0.0015933 | 0.00039931 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_2148-8_0_3_load_107 | 108 | 0.0013255 | 0.00033219 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_2148-8_0_3_load_108 | 109 | 0.0022741 | 0.00056994 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_2148-8_0_3_load_109 | 110 | 0.00085072 | 0.00021321 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_2148-8_0_3_load_113 | 111 | 0.0021193 | 0.00053115 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_2148-8_0_3_load_114 | 112 | 0.0013925 | 0.000349 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_2148-8_0_3_load_112 | 113 | 0.001495 | 0.00037467 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_2148-8_0_3_load_115 | 114 | 0.0012698 | 0.00031825 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_2148-8_0_3_load_110 | 115 | 0.0014114 | 0.00035373 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_2148-8_0_3_load_111 | 116 | 0.0031895 | 0.00079935 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_2148-8_0_3_load_116 | 117 | 0.0024613 | 0.00061687 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 14 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_2148-8_0_3_line_0 |  | 0 | 1 | 0.017454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_2148-8_0_3_line_1 |  | 1 | 2 | 0.005384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_2148-8_0_3_line_2 |  | 2 | 6 | 0.013986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_2148-8_0_3_line_3 |  | 3 | 4 | 0.029254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_2148-8_0_3_line_4 |  | 3 | 5 | 0.051057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_2148-8_0_3_line_5 |  | 4 | 8 | 0.01608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_2148-8_0_3_line_6 |  | 6 | 7 | 0.015961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_2148-8_0_3_line_7 |  | 7 | 11 | 0.021324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_2148-8_0_3_line_8 |  | 7 | 8 | 0.051003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_2148-8_0_3_line_9 |  | 8 | 9 | 0.0065851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_2148-8_0_3_line_10 |  | 9 | 10 | 0.025482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_2148-8_0_3_line_11 |  | 11 | 52 | 0.018936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_2148-8_0_3_line_12 |  | 12 | 13 | 0.033157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_2148-8_0_3_line_13 |  | 12 | 14 | 0.031847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_2148-8_0_3_line_14 |  | 13 | 15 | 0.001721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_2148-8_0_3_line_15 |  | 13 | 16 | 0.0002251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_2148-8_0_3_line_16 |  | 15 | 17 | 0.035341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_2148-8_0_3_line_17 |  | 15 | 18 | 0.021923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_2148-8_0_3_line_18 |  | 16 | 19 | 0.010962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_2148-8_0_3_line_19 |  | 17 | 20 | 0.028211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_2148-8_0_3_line_20 |  | 18 | 21 | 0.041258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_2148-8_0_3_line_21 |  | 18 | 22 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_2148-8_0_3_line_22 |  | 19 | 23 | 0.029197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_2148-8_0_3_line_23 |  | 19 | 24 | 0.033045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_2148-8_0_3_line_24 |  | 20 | 43 | 0.020276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
25 | LV_2148-8_0_3_line_25 |  | 21 | 102 | 0.030145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_2148-8_0_3_line_26 |  | 22 | 45 | 0.033938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_2148-8_0_3_line_27 |  | 23 | 80 | 0.0068653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_2148-8_0_3_line_28 |  | 24 | 89 | 0.013798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_2148-8_0_3_line_29 |  | 25 | 26 | 0.021135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_2148-8_0_3_line_30 |  | 25 | 27 | 0.039227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_2148-8_0_3_line_31 |  | 26 | 28 | 0.014373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_2148-8_0_3_line_32 |  | 27 | 29 | 0.014758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_2148-8_0_3_line_33 |  | 28 | 33 | 0.012817 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_2148-8_0_3_line_34 |  | 29 | 35 | 0.050674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_2148-8_0_3_line_35 |  | 30 | 31 | 0.025069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_2148-8_0_3_line_36 |  | 30 | 32 | 0.022798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_2148-8_0_3_line_37 |  | 31 | 34 | 0.029482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_2148-8_0_3_line_38 |  | 32 | 37 | 0.021227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_2148-8_0_3_line_39 |  | 33 | 36 | 0.044391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_2148-8_0_3_line_40 |  | 35 | 37 | 0.046642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_2148-8_0_3_line_41 |  | 35 | 38 | 0.18017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_2148-8_0_3_line_42 |  | 36 | 98 | 0.028201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_2148-8_0_3_line_43 |  | 38 | 88 | 0.00030509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_2148-8_0_3_line_44 |  | 39 | 40 | 0.027613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_2148-8_0_3_line_45 |  | 40 | 41 | 0.0097338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_2148-8_0_3_line_46 |  | 40 | 42 | 0.011994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_2148-8_0_3_line_47 |  | 41 | 44 | 0.011211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_2148-8_0_3_line_48 |  | 42 | 45 | 0.04385 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_2148-8_0_3_line_49 |  | 43 | 46 | 0.012382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_2148-8_0_3_line_50 |  | 44 | 47 | 0.0090701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_2148-8_0_3_line_51 |  | 45 | 48 | 0.01867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_2148-8_0_3_line_52 |  | 46 | 49 | 0.029346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_2148-8_0_3_line_53 |  | 47 | 67 | 0.010439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_2148-8_0_3_line_54 |  | 48 | 103 | 0.017843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_2148-8_0_3_line_55 |  | 49 | 61 | 0.014978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_2148-8_0_3_line_56 |  | 50 | 51 | 0.028925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_2148-8_0_3_line_57 |  | 50 | 52 | 0.026128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_2148-8_0_3_line_58 |  | 51 | 53 | 0.0010541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_2148-8_0_3_line_59 |  | 52 | 54 | 0.027336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_2148-8_0_3_line_60 |  | 53 | 55 | 0.027375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_2148-8_0_3_line_61 |  | 53 | 56 | 0.021898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_2148-8_0_3_line_62 |  | 54 | 57 | 0.026807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_2148-8_0_3_line_63 |  | 55 | 58 | 0.032753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_2148-8_0_3_line_64 |  | 56 | 59 | 0.0026724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_2148-8_0_3_line_65 |  | 57 | 60 | 0.038732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_2148-8_0_3_line_66 |  | 58 | 62 | 0.042563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_2148-8_0_3_line_67 |  | 58 | 61 | 0.0082352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_2148-8_0_3_line_68 |  | 59 | 63 | 0.024811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_2148-8_0_3_line_69 |  | 60 | 85 | 0.013929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_2148-8_0_3_line_70 |  | 62 | 69 | 0.016588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_2148-8_0_3_line_71 |  | 62 | 68 | 0.022197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_2148-8_0_3_line_72 |  | 63 | 64 | 0.0070001 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_2148-8_0_3_line_73 |  | 64 | 65 | 0.014394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_2148-8_0_3_line_74 |  | 64 | 66 | 0.018628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_2148-8_0_3_line_75 |  | 65 | 77 | 0.014823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_2148-8_0_3_line_76 |  | 66 | 97 | 0.010769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_2148-8_0_3_line_77 |  | 69 | 70 | 0.016669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_2148-8_0_3_line_78 |  | 70 | 71 | 0.029498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_2148-8_0_3_line_79 |  | 72 | 73 | 0.016623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_2148-8_0_3_line_80 |  | 73 | 74 | 0.004832 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_2148-8_0_3_line_81 |  | 74 | 75 | 0.0089946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_2148-8_0_3_line_82 |  | 74 | 76 | 0.02965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_2148-8_0_3_line_83 |  | 75 | 77 | 0.0076794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_2148-8_0_3_line_84 |  | 78 | 79 | 0.031367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_2148-8_0_3_line_85 |  | 78 | 80 | 0.053415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_2148-8_0_3_line_86 |  | 79 | 81 | 0.059018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_2148-8_0_3_line_87 |  | 81 | 82 | 0.046904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_2148-8_0_3_line_88 |  | 82 | 83 | 0.01221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_2148-8_0_3_line_89 |  | 84 | 85 | 0.0042032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_2148-8_0_3_line_90 |  | 84 | 86 | 0.01906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_2148-8_0_3_line_91 |  | 87 | 88 | 0.16168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_2148-8_0_3_line_92 |  | 89 | 90 | 0.014388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
93 | LV_2148-8_0_3_line_93 |  | 90 | 91 | 0.0074968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
94 | LV_2148-8_0_3_line_94 |  | 91 | 92 | 0.045381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
95 | LV_2148-8_0_3_line_95 |  | 92 | 93 | 0.053141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
96 | LV_2148-8_0_3_line_96 |  | 93 | 94 | 0.024739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
97 | LV_2148-8_0_3_line_97 |  | 94 | 95 | 0.0040311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
98 | LV_2148-8_0_3_line_98 |  | 95 | 96 | 0.019989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
99 | LV_2148-8_0_3_line_99 |  | 96 | 98 | 0.051477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
100 | LV_2148-8_0_3_line_100 |  | 98 | 99 | 0.013617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_2148-8_0_3_line_101 |  | 99 | 100 | 0.016378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_2148-8_0_3_line_102 |  | 100 | 101 | 0.02543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_2148-8_0_3_line_103 |  | 102 | 104 | 0.044695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_2148-8_0_3_line_104 |  | 103 | 105 | 0.025252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_2148-8_0_3_line_105 |  | 104 | 117 | 0.016504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_2148-8_0_3_line_106 |  | 106 | 107 | 0.0018509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_2148-8_0_3_line_107 |  | 106 | 108 | 0.010324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_2148-8_0_3_line_108 |  | 107 | 109 | 0.017982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_2148-8_0_3_line_109 |  | 108 | 110 | 0.015396 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_2148-8_0_3_line_110 |  | 109 | 111 | 0.0016813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_2148-8_0_3_line_111 |  | 110 | 112 | 0.023435 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_2148-8_0_3_line_112 |  | 111 | 113 | 0.017179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_2148-8_0_3_line_113 |  | 112 | 114 | 0.017239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_2148-8_0_3_line_114 |  | 113 | 116 | 0.018855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_2148-8_0_3_line_115 |  | 114 | 117 | 0.017422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_2148-8_0_3_line_116 |  | 115 | 116 | 0.00067951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_2148-8_0_3_trafo_11 | 0.63 MVA 20/0.4 kV | 118 | 14 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2570348.5419 | 1165772.3283 | 2570359.8969 | 1165785.584
1 | 2570363.3994 | 1165789.6729 | 2570359.8969 | 1165785.584
2 | 2570363.3994 | 1165789.6729 | 2570372.4979 | 1165800.2944
3 | 2570392.4975 | 1165743.5859 | 2570410.9933 | 1165766.2513
4 | 2570392.4975 | 1165743.5859 | 2570386.9681 | 1165692.8296
5 | 2570421.1599 | 1165778.7097 | 2570410.9933 | 1165766.2513
6 | 2570382.8813 | 1165812.4158 | 2570372.4979 | 1165800.2944
7 | 2570382.8813 | 1165812.4158 | 2570383.3073 | 1165812.9132 | 2570394.3423 | 1165830.3898
8 | 2570382.8813 | 1165812.4158 | 2570421.1599 | 1165778.7097
9 | 2570425.3233 | 1165783.8117 | 2570421.1599 | 1165778.7097
10 | 2570441.4344 | 1165803.5547 | 2570425.3233 | 1165783.8117
11 | 2570399.6691 | 1165848.5616 | 2570394.3423 | 1165830.3898 | 2570394.3423 | 1165830.3898
12 | 2570555.136 | 1166059.7252 | 2570525.8245 | 1166044.2255
13 | 2570498.0447 | 1166028.6569 | 2570520.8931 | 1166041.6177 | 2570525.8245 | 1166044.2255
14 | 2570555.8633 | 1166058.1653 | 2570555.136 | 1166059.7252
15 | 2570555.0073 | 1166059.9099 | 2570555.136 | 1166059.7252
16 | 2570555.8633 | 1166058.1653 | 2570532.6774 | 1166031.4927
17 | 2570555.8633 | 1166058.1653 | 2570570.6824 | 1166041.9731
18 | 2570548.7424 | 1166068.9058 | 2570555.0073 | 1166059.9099
19 | 2570514.1695 | 1166010.2015 | 2570532.6774 | 1166031.4927
20 | 2570570.6824 | 1166041.9731 | 2570601.0898 | 1166069.8594
21 | 2570570.6824 | 1166041.9731 | 2570586.4425 | 1166024.7597
22 | 2570548.7424 | 1166068.9058 | 2570559.4052 | 1166088.7301 | 2570564.0361 | 1166093.5535
23 | 2570548.7424 | 1166068.9058 | 2570543.4955 | 1166082.4051 | 2570540.1183 | 1166099.3526 | 2570540.1387 | 1166100.6333
24 | 2570514.1695 | 1166010.2015 | 2570501.3115 | 1165994.5243
25 | 2570604.8344 | 1166094.6211 | 2570604.8344 | 1166094.6211 | 2570608.1017 | 1166091.1256 | 2570610.0399 | 1166088.2479 | 2570610.7871 | 1166084.509 | 2570610.1037 | 1166080.9772 | 2570608.7565 | 1166077.9156 | 2570604.0448 | 1166072.5694 | 2570601.0898 | 1166069.8594
26 | 2570609.3604 | 1165999.7284 | 2570586.4425 | 1166024.7597
27 | 2570564.0361 | 1166093.5535 | 2570568.7909 | 1166098.5058
28 | 2570540.1387 | 1166100.6333 | 2570540.3584 | 1166114.4293
29 | 2570525.5676 | 1166252.8434 | 2570542.9542 | 1166264.8592
30 | 2570525.5676 | 1166252.8434 | 2570505.7193 | 1166239.1264 | 2570492.8109 | 1166231.291
31 | 2570554.9913 | 1166272.7125 | 2570544.8666 | 1166266.1809 | 2570542.9542 | 1166264.8592
32 | 2570480.1949 | 1166223.6331 | 2570492.8109 | 1166231.291
33 | 2570554.9913 | 1166272.7125 | 2570565.7614 | 1166279.6605
34 | 2570480.1949 | 1166223.6331 | 2570480.1949 | 1166223.6331 | 2570469.0718 | 1166220.7086 | 2570457.6367 | 1166219.7089 | 2570444.0971 | 1166223.5666 | 2570435.4465 | 1166228.3117 | 2570432.6049 | 1166230.7571
35 | 2570473.7979 | 1166306.3033 | 2570492.0369 | 1166323.5024
36 | 2570473.7979 | 1166306.3033 | 2570457.2115 | 1166290.6626
37 | 2570492.0369 | 1166323.5024 | 2570513.4865 | 1166343.729
38 | 2570457.2115 | 1166290.6626 | 2570445.5146 | 1166279.6326 | 2570441.3771 | 1166276.5672
39 | 2570565.7614 | 1166279.6605 | 2570572.999 | 1166284.3296 | 2570588.6999 | 1166298.1373 | 2570598.6407 | 1166309.1959
40 | 2570432.6049 | 1166230.7571 | 2570441.3771 | 1166276.5672
41 | 2570432.6049 | 1166230.7571 | 2570256.9313 | 1166270.7725
42 | 2570622.3168 | 1166315.3812 | 2570616.0794 | 1166318.9135 | 2570610.4447 | 1166318.8967 | 2570602.8177 | 1166313.8427 | 2570598.6407 | 1166309.1959
43 | 2570256.9313 | 1166270.7725 | 2570256.649 | 1166270.8881
44 | 2570570.5378 | 1165959.5874 | 2570549.9922 | 1165978.0357
45 | 2570570.5378 | 1165959.5874 | 2570564.1684 | 1165952.227
46 | 2570570.5378 | 1165959.5874 | 2570578.8758 | 1165968.2085
47 | 2570564.1684 | 1165952.227 | 2570556.832 | 1165943.7492
48 | 2570609.3604 | 1165999.7284 | 2570578.8758 | 1165968.2085
49 | 2570493.4597 | 1165984.9508 | 2570501.3115 | 1165994.5243
50 | 2570556.832 | 1165943.7492 | 2570551.5805 | 1165937.6806 | 2570550.5366 | 1165937.7217
51 | 2570609.3604 | 1165999.7284 | 2570622.9849 | 1165986.9632
52 | 2570493.4597 | 1165984.9508 | 2570474.8497 | 1165962.2604
53 | 2570540.7913 | 1165940.4795 | 2570545.1429 | 1165937.9346 | 2570550.5366 | 1165937.7217
54 | 2570636.006 | 1165974.7635 | 2570622.9849 | 1165986.9632
55 | 2570474.8497 | 1165962.2604 | 2570465.3514 | 1165950.6795
56 | 2570418.3145 | 1165899.9685 | 2570411.6618 | 1165889.4232 | 2570407.0272 | 1165873.6322
57 | 2570399.6691 | 1165848.5616 | 2570407.0272 | 1165873.6322
58 | 2570418.8769 | 1165900.86 | 2570418.3145 | 1165899.9685
59 | 2570399.6691 | 1165848.5616 | 2570373.9775 | 1165857.9009
60 | 2570418.8769 | 1165900.86 | 2570423.8465 | 1165908.7395 | 2570436.7416 | 1165921.3822
61 | 2570418.8769 | 1165900.86 | 2570431.5536 | 1165886.479 | 2570433.7581 | 1165884.8725
62 | 2570351.016 | 1165871.2244 | 2570354.1427 | 1165868.2968 | 2570365.7207 | 1165860.9024 | 2570373.9775 | 1165857.9009
63 | 2570460.1289 | 1165944.3119 | 2570436.7416 | 1165921.3822
64 | 2570433.7581 | 1165884.8725 | 2570435.9179 | 1165883.2987
65 | 2570351.016 | 1165871.2244 | 2570346.1102 | 1165875.8181 | 2570344.1862 | 1165883.098 | 2570351.1185 | 1165899.2275 | 2570354.3975 | 1165905.3267
66 | 2570428.9432 | 1165973.3695 | 2570460.1289 | 1165944.3119
67 | 2570460.1289 | 1165944.3119 | 2570465.3514 | 1165950.6795
68 | 2570435.9179 | 1165883.2987 | 2570455.9693 | 1165868.6866
69 | 2570354.3975 | 1165905.3267 | 2570357.1149 | 1165910.3813 | 2570358.4608 | 1165913.1427 | 2570356.6547 | 1165917.9318
70 | 2570428.9432 | 1165973.3695 | 2570428.352 | 1165983.8889 | 2570431.1357 | 1165989.2626
71 | 2570428.9432 | 1165973.3695 | 2570412.9063 | 1165988.7162
72 | 2570461.6266 | 1165864.5639 | 2570455.9693 | 1165868.6866
73 | 2570461.6266 | 1165864.5639 | 2570471.1776 | 1165875.3332
74 | 2570461.6266 | 1165864.5639 | 2570476.6806 | 1165853.5919
75 | 2570471.1776 | 1165875.3332 | 2570481.0131 | 1165886.4233
76 | 2570485.3831 | 1165847.2492 | 2570476.6806 | 1165853.5919
77 | 2570440.9506 | 1166002.5455 | 2570434.389 | 1165995.5428 | 2570431.1357 | 1165989.2626
78 | 2570440.9506 | 1166002.5455 | 2570461.1196 | 1166024.0708
79 | 2570506.3151 | 1165914.9467 | 2570495.2834 | 1165902.5125
80 | 2570492.0766 | 1165898.898 | 2570495.2834 | 1165902.5125
81 | 2570492.0766 | 1165898.898 | 2570486.1085 | 1165892.1687
82 | 2570516.131 | 1165881.4707 | 2570492.0766 | 1165898.898
83 | 2570481.0131 | 1165886.4233 | 2570486.1085 | 1165892.1687
84 | 2570606.3863 | 1166136.4038 | 2570630.062 | 1166156.9799
85 | 2570606.3863 | 1166136.4038 | 2570599.0827 | 1166130.0563 | 2570568.7909 | 1166098.5058
86 | 2570653.8558 | 1166209.3491 | 2570645.9204 | 1166176.5948 | 2570633.7436 | 1166160.1794 | 2570630.062 | 1166156.9799
87 | 2570653.8558 | 1166209.3491 | 2570656.9147 | 1166221.9751 | 2570662.2763 | 1166233.4214 | 2570676.1834 | 1166249.5184
88 | 2570684.1657 | 1166258.7576 | 2570676.1834 | 1166249.5184
89 | 2570352.4516 | 1165917.9626 | 2570356.6547 | 1165917.9318 | 2570356.6547 | 1165917.9318
90 | 2570335.5885 | 1165909.4429 | 2570343.8997 | 1165914.9156 | 2570351.9692 | 1165917.9661 | 2570352.4516 | 1165917.9626
91 | 2570256.649 | 1166270.8881 | 2570175.9248 | 1166130.8039
92 | 2570540.3584 | 1166114.4293 | 2570540.3732 | 1166115.3595 | 2570541.7945 | 1166125.7133 | 2570542.5833 | 1166128.6147
93 | 2570542.5833 | 1166128.6147 | 2570544.5499 | 1166135.8489
94 | 2570565.9941 | 1166175.6487 | 2570552.0124 | 1166153.1548 | 2570545.5761 | 1166139.624 | 2570544.5499 | 1166135.8489
95 | 2570565.9941 | 1166175.6487 | 2570584.1767 | 1166204.9009 | 2570593.871 | 1166220.8904
96 | 2570593.871 | 1166220.8904 | 2570596.5415 | 1166225.2951 | 2570605.3005 | 1166242.815
97 | 2570607.1032 | 1166246.4207 | 2570607.1032 | 1166246.4207 | 2570605.3005 | 1166242.815
98 | 2570607.1032 | 1166246.4207 | 2570613.5466 | 1166265.3431
99 | 2570622.3168 | 1166315.3812 | 2570623.4408 | 1166311.9739 | 2570623.464 | 1166304.2254 | 2570614.8088 | 1166269.0499 | 2570613.5466 | 1166265.3431
100 | 2570622.3168 | 1166315.3812 | 2570629.8232 | 1166326.7421
101 | 2570638.343 | 1166340.6954 | 2570636.447 | 1166336.7672 | 2570629.8232 | 1166326.7421
102 | 2570638.343 | 1166340.6954 | 2570649.3971 | 1166363.5973
103 | 2570604.8344 | 1166094.6211 | 2570599.6202 | 1166099.2046 | 2570596.6056 | 1166102.699 | 2570595.285 | 1166105.0511 | 2570594.9395 | 1166107.9765 | 2570595.1613 | 1166111.0436 | 2570596.9689 | 1166114.3142 | 2570602.0226 | 1166119.1474 | 2570612.0866 | 1166128.428
104 | 2570636.006 | 1165974.7635 | 2570641.2548 | 1165969.8457 | 2570655.8354 | 1165959.1901
105 | 2570624.2193 | 1166139.6161 | 2570612.0866 | 1166128.428
106 | 2570689.8499 | 1166189.5245 | 2570690.9142 | 1166191.0387
107 | 2570689.8499 | 1166189.5245 | 2570689.644 | 1166189.2316 | 2570687.2611 | 1166185.7192 | 2570684.947 | 1166183.7295 | 2570682.6284 | 1166182.4069
108 | 2570701.2545 | 1166205.7498 | 2570690.9142 | 1166191.0387
109 | 2570682.6284 | 1166182.4069 | 2570682.6284 | 1166182.4069 | 2570668.3002 | 1166176.773
110 | 2570702.2214 | 1166207.1253 | 2570701.2545 | 1166205.7498
111 | 2570668.3002 | 1166176.773 | 2570666.3205 | 1166175.9945 | 2570659.276 | 1166172.6495 | 2570649.5092 | 1166163.3164
112 | 2570712.1001 | 1166221.1798 | 2570702.2214 | 1166207.1253
113 | 2570649.5092 | 1166163.3164 | 2570638.1769 | 1166152.4871 | 2570637.0268 | 1166151.4265
114 | 2570722.8283 | 1166236.6839 | 2570718.285 | 1166229.9789 | 2570712.1001 | 1166221.1798
115 | 2570637.0268 | 1166151.4265 | 2570624.2193 | 1166139.6161
116 | 2570723.2094 | 1166237.2465 | 2570722.8283 | 1166236.6839

## bus_geodata
| x | y | coords
0 | 2570348.5419 | 1165772.3283
1 | 2570359.8969 | 1165785.584
2 | 2570363.3994 | 1165789.6729
3 | 2570392.4975 | 1165743.5859
4 | 2570410.9933 | 1165766.2513
5 | 2570386.9681 | 1165692.8296
6 | 2570372.4979 | 1165800.2944
7 | 2570382.8813 | 1165812.4158
8 | 2570421.1599 | 1165778.7097
9 | 2570425.3233 | 1165783.8117
10 | 2570441.4344 | 1165803.5547
11 | 2570394.3423 | 1165830.3898
12 | 2570525.8245 | 1166044.2255
13 | 2570555.136 | 1166059.7252
14 | 2570498.0447 | 1166028.6569
15 | 2570555.8633 | 1166058.1653
16 | 2570555.0073 | 1166059.9099
17 | 2570532.6774 | 1166031.4927
18 | 2570570.6824 | 1166041.9731
19 | 2570548.7424 | 1166068.9058
20 | 2570514.1695 | 1166010.2015
21 | 2570601.0898 | 1166069.8594
22 | 2570586.4425 | 1166024.7597
23 | 2570564.0361 | 1166093.5535
24 | 2570540.1387 | 1166100.6333
25 | 2570525.5676 | 1166252.8434
26 | 2570542.9542 | 1166264.8592
27 | 2570492.8109 | 1166231.291
28 | 2570554.9913 | 1166272.7125
29 | 2570480.1949 | 1166223.6331
30 | 2570473.7979 | 1166306.3033
31 | 2570492.0369 | 1166323.5024
32 | 2570457.2115 | 1166290.6626
33 | 2570565.7614 | 1166279.6605
34 | 2570513.4865 | 1166343.729
35 | 2570432.6049 | 1166230.7571
36 | 2570598.6407 | 1166309.1959
37 | 2570441.3771 | 1166276.5672
38 | 2570256.9313 | 1166270.7725
39 | 2570549.9922 | 1165978.0357
40 | 2570570.5378 | 1165959.5874
41 | 2570564.1684 | 1165952.227
42 | 2570578.8758 | 1165968.2085
43 | 2570501.3115 | 1165994.5243
44 | 2570556.832 | 1165943.7492
45 | 2570609.3604 | 1165999.7284
46 | 2570493.4596 | 1165984.9508
47 | 2570550.5366 | 1165937.7217
48 | 2570622.9849 | 1165986.9632
49 | 2570474.8497 | 1165962.2604
50 | 2570407.0272 | 1165873.6322
51 | 2570418.3145 | 1165899.9685
52 | 2570399.6691 | 1165848.5616
53 | 2570418.8769 | 1165900.86
54 | 2570373.9775 | 1165857.9009
55 | 2570436.7416 | 1165921.3822
56 | 2570433.7581 | 1165884.8725
57 | 2570351.016 | 1165871.2244
58 | 2570460.1289 | 1165944.3119
59 | 2570435.9179 | 1165883.2987
60 | 2570354.3975 | 1165905.3267
61 | 2570465.3514 | 1165950.6795
62 | 2570428.9432 | 1165973.3695
63 | 2570455.9693 | 1165868.6866
64 | 2570461.6266 | 1165864.5639
65 | 2570471.1776 | 1165875.3332
66 | 2570476.6806 | 1165853.5919
67 | 2570540.7913 | 1165940.4795
68 | 2570412.9063 | 1165988.7162
69 | 2570431.1357 | 1165989.2626
70 | 2570440.9506 | 1166002.5455
71 | 2570461.1196 | 1166024.0708
72 | 2570506.3151 | 1165914.9467
73 | 2570495.2834 | 1165902.5125
74 | 2570492.0766 | 1165898.898
75 | 2570486.1085 | 1165892.1687
76 | 2570516.131 | 1165881.4707
77 | 2570481.0131 | 1165886.4233
78 | 2570606.3863 | 1166136.4038
79 | 2570630.062 | 1166156.9799
80 | 2570568.7909 | 1166098.5058
81 | 2570653.8558 | 1166209.3491
82 | 2570676.1834 | 1166249.5184
83 | 2570684.1657 | 1166258.7576
84 | 2570352.4516 | 1165917.9626
85 | 2570356.6547 | 1165917.9318
86 | 2570335.5885 | 1165909.4429
87 | 2570175.9248 | 1166130.8039
88 | 2570256.649 | 1166270.8881
89 | 2570540.3584 | 1166114.4293
90 | 2570542.5833 | 1166128.6147
91 | 2570544.5499 | 1166135.8489
92 | 2570565.9941 | 1166175.6487
93 | 2570593.871 | 1166220.8904
94 | 2570605.3005 | 1166242.815
95 | 2570607.1032 | 1166246.4207
96 | 2570613.5466 | 1166265.3431
97 | 2570485.3831 | 1165847.2492
98 | 2570622.3168 | 1166315.3812
99 | 2570629.8232 | 1166326.7421
100 | 2570638.343 | 1166340.6954
101 | 2570649.3971 | 1166363.5973
102 | 2570604.8344 | 1166094.6211
103 | 2570636.006 | 1165974.7635
104 | 2570612.0866 | 1166128.428
105 | 2570655.8354 | 1165959.1901
106 | 2570689.8499 | 1166189.5245
107 | 2570690.9142 | 1166191.0387
108 | 2570682.6284 | 1166182.4069
109 | 2570701.2545 | 1166205.7498
110 | 2570668.3003 | 1166176.773
111 | 2570702.2214 | 1166207.1253
112 | 2570649.5092 | 1166163.3164
113 | 2570712.1001 | 1166221.1798
114 | 2570637.0268 | 1166151.4265
115 | 2570723.2094 | 1166237.2465
116 | 2570722.8283 | 1166236.6839
117 | 2570624.2193 | 1166139.6161
118 | 2570555.136 | 1166059.7252

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97147 | -0.55014 | 0.0034451 | 0.00086342
1 | 0.97153 | -0.54902 | 0.0021602 | 0.00054141
2 | 0.97156 | -0.54847 | 0.0016288 | 0.00040821
3 | 0.97018 | -0.57571 | 0.0046851 | 0.0011742
4 | 0.97037 | -0.57204 | 0.0051242 | 0.0012842
5 | 0.97008 | -0.57769 | 0.002089 | 0.00052355
6 | 0.97165 | -0.5466 | 0.0012128 | 0.00030396
7 | 0.97178 | -0.54411 | 0.0017794 | 0.00044596
8 | 0.97054 | -0.5685 | 0.003183 | 0.00079773
9 | 0.97048 | -0.56981 | 0.0040957 | 0.0010265
10 | 0.97032 | -0.57297 | 0.0066938 | 0.0016776
11 | 0.9725 | -0.52991 | 0.0043756 | 0.0010966
12 | 0.99679 | -0.06071 | 0.0047681 | 0.001195
13 | 0.99349 | -0.1234 | 0 | 0
14 | 1 | 0 | -0.3343 | -0.085546
15 | 0.99338 | -0.12545 | 0 | 0
16 | 0.99348 | -0.12356 | 0.0037792 | 0.00094715
17 | 0.99185 | -0.15459 | 0.0050402 | 0.0012632
18 | 0.99213 | -0.14971 | 0 | 0
19 | 0.99309 | -0.13106 | 0 | 0
20 | 0.99067 | -0.17707 | 0 | 0
21 | 0.99106 | -0.1704 | 0.0036647 | 0.00091846
22 | 0.9914 | -0.16388 | 0.0050043 | 0.0012542
23 | 0.99265 | -0.13969 | 0.0013696 | 0.00034325
24 | 0.99208 | -0.15044 | 0.0032285 | 0.00080913
25 | 0.97948 | -0.39385 | 0.0028622 | 0.00071734
26 | 0.98033 | -0.37745 | 0.004264 | 0.0010687
27 | 0.97803 | -0.42231 | 0.0020577 | 0.00051571
28 | 0.98095 | -0.3652 | 0.0034579 | 0.00086662
29 | 0.97751 | -0.43249 | 0.00098858 | 0.00024776
30 | 0.97443 | -0.49303 | 0.0027551 | 0.00069048
31 | 0.97419 | -0.49771 | 0.005433 | 0.0013616
32 | 0.9747 | -0.48763 | 0.002416 | 0.00060551
33 | 0.98156 | -0.35349 | 0.004276 | 0.0010717
34 | 0.97406 | -0.50026 | 0.0047209 | 0.0011832
35 | 0.97577 | -0.4666 | 0.0020137 | 0.00050469
36 | 0.98381 | -0.30963 | 0.005525 | 0.0013847
37 | 0.975 | -0.48166 | 0.0023008 | 0.00057664
38 | 0.97288 | -0.52346 | 0.0056754 | 0.0014224
39 | 0.98951 | -0.20036 | 0.0036286 | 0.0009094
40 | 0.98961 | -0.19857 | 0 | 0
41 | 0.9895 | -0.20065 | 0.0023683 | 0.00059356
42 | 0.98978 | -0.19524 | 0.0019953 | 0.00050006
43 | 0.9894 | -0.20136 | 0.0037114 | 0.00093016
44 | 0.9894 | -0.20257 | 0.0023066 | 0.00057809
45 | 0.99049 | -0.18151 | 0 | 0
46 | 0.98789 | -0.2303 | 0.0032191 | 0.00080679
47 | 0.98934 | -0.20375 | 0.0044997 | 0.0011277
48 | 0.99029 | -0.18537 | 0.0031649 | 0.00079321
49 | 0.9844 | -0.29753 | 0.0030826 | 0.00077258
50 | 0.97454 | -0.48973 | 0.0038756 | 0.00097132
51 | 0.97611 | -0.45891 | 0.0039901 | 0.001
52 | 0.97321 | -0.51579 | 0 | 0
53 | 0.97617 | -0.45771 | 0 | 0
54 | 0.97286 | -0.52274 | 0.0013105 | 0.00032845
55 | 0.97867 | -0.40878 | 0.0029232 | 0.00073261
56 | 0.97544 | -0.47206 | 0.0034449 | 0.00086337
57 | 0.97255 | -0.52891 | 0.0020818 | 0.00052175
58 | 0.98175 | -0.34884 | 0 | 0
59 | 0.97536 | -0.47365 | 0.0025697 | 0.00064402
60 | 0.97217 | -0.53634 | 0.0025654 | 0.00064296
61 | 0.98266 | -0.33119 | 0.0061311 | 0.0015366
62 | 0.98105 | -0.36249 | 0 | 0
63 | 0.97467 | -0.4872 | 0.0028096 | 0.00070416
64 | 0.97449 | -0.49067 | 0 | 0
65 | 0.97422 | -0.49604 | 0.0033909 | 0.00084985
66 | 0.97438 | -0.49294 | 0.002982 | 0.00074735
67 | 0.98931 | -0.20428 | 0.0028155 | 0.00070563
68 | 0.98098 | -0.36392 | 0.0035372 | 0.00088652
69 | 0.98083 | -0.36676 | 0.0032073 | 0.00080383
70 | 0.98066 | -0.37007 | 0.0032134 | 0.00080535
71 | 0.98045 | -0.37423 | 0.0077648 | 0.001946
72 | 0.97373 | -0.50579 | 0.0034272 | 0.00085893
73 | 0.97378 | -0.50474 | 0.0021279 | 0.00053331
74 | 0.97381 | -0.50425 | 0 | 0
75 | 0.97389 | -0.50251 | 0.0026834 | 0.00067251
76 | 0.97367 | -0.50694 | 0.0049345 | 0.0012367
77 | 0.97399 | -0.50065 | 0.0037679 | 0.00094432
78 | 0.99202 | -0.15185 | 0.0029554 | 0.0007407
79 | 0.99179 | -0.15625 | 0.0022341 | 0.00055992
80 | 0.99255 | -0.14155 | 0.0044477 | 0.0011147
81 | 0.99148 | -0.16222 | 0.0019238 | 0.00048215
82 | 0.99132 | -0.16535 | 0.0022657 | 0.00056784
83 | 0.99131 | -0.16568 | 0.0015053 | 0.00037727
84 | 0.97205 | -0.53874 | 0.00094386 | 0.00023655
85 | 0.97207 | -0.53835 | 0.0028542 | 0.00071533
86 | 0.97198 | -0.54016 | 0.0040415 | 0.0010129
87 | 0.97129 | -0.55488 | 0.010513 | 0.0026347
88 | 0.97288 | -0.52352 | 0.00099192 | 0.0002486
89 | 0.99167 | -0.15828 | 0.0024786 | 0.0006212
90 | 0.99125 | -0.16625 | 0.0025039 | 0.00062754
91 | 0.99104 | -0.17029 | 0.0032585 | 0.00081665
92 | 0.98981 | -0.19393 | 0.0024558 | 0.00061548
93 | 0.98841 | -0.22091 | 0.0024935 | 0.00062493
94 | 0.98777 | -0.23313 | 0.0027376 | 0.00068612
95 | 0.98767 | -0.23506 | 0.003135 | 0.0007857
96 | 0.9872 | -0.24424 | 0.0016023 | 0.00040157
97 | 0.97434 | -0.49367 | 0.003668 | 0.00091928
98 | 0.98539 | -0.27907 | 0 | 0
99 | 0.9852 | -0.28279 | 0.0020733 | 0.00051961
100 | 0.985 | -0.28667 | 0.0064924 | 0.0016271
101 | 0.98485 | -0.28972 | 0.0066755 | 0.001673
102 | 0.99038 | -0.18359 | 0.0015277 | 0.00038288
103 | 0.99015 | -0.18806 | 0.0024354 | 0.00061036
104 | 0.98943 | -0.20195 | 0.0014667 | 0.0003676
105 | 0.99001 | -0.19077 | 0.0060392 | 0.0015136
106 | 0.9878 | -0.23361 | 0.0022439 | 0.00056238
107 | 0.98778 | -0.23401 | 0.0015933 | 0.00039931
108 | 0.98794 | -0.23097 | 0.0013255 | 0.00033219
109 | 0.98761 | -0.23738 | 0.0022741 | 0.00056994
110 | 0.98816 | -0.22666 | 0.00085072 | 0.00021321
111 | 0.98759 | -0.23762 | 0.0021193 | 0.00053115
112 | 0.98851 | -0.21976 | 0.0013925 | 0.000349
113 | 0.9875 | -0.2395 | 0.001495 | 0.00037467
114 | 0.9888 | -0.21426 | 0.0012698 | 0.00031825
115 | 0.98742 | -0.24106 | 0.0014114 | 0.00035373
116 | 0.98742 | -0.24105 | 0.0031895 | 0.00079935
117 | 0.9891 | -0.20831 | 0.0024613 | 0.00061687
118 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0034451 | -0.00086342 | 0.0034453 | 0.00086332 | 1.8225e-07 | -9.9478e-08 | 0.0052769 | 0.0052768 | 0.0052769 | 0.97147 | -0.55014 | 0.97153 | -0.54902 | 1.4497
1 | -0.0056055 | -0.0014047 | 0.0056057 | 0.0014048 | 1.4882e-07 | 2.8574e-08 | 0.0085855 | 0.0085854 | 0.0085855 | 0.97153 | -0.54902 | 0.97156 | -0.54847 | 2.3586
2 | -0.0072344 | -0.001813 | 0.0072351 | 0.0018132 | 6.4387e-07 | 2.3887e-07 | 0.01108 | 0.01108 | 0.01108 | 0.97156 | -0.54847 | 0.97165 | -0.5466 | 3.044
3 | -0.0067743 | -0.0016972 | 0.0067754 | 0.0016976 | 1.1842e-06 | 3.9658e-07 | 0.01039 | 0.01039 | 0.01039 | 0.97018 | -0.57571 | 0.97037 | -0.57204 | 2.8543
4 | 0.0020892 | 0.00052305 | -0.002089 | -0.00052355 | 1.9657e-07 | -5.046e-07 | 0.0032041 | 0.0032043 | 0.0032043 | 0.97018 | -0.57571 | 0.97008 | -0.57769 | 0.88031
5 | -0.0119 | -0.0029819 | 0.011902 | 0.002983 | 2.0078e-06 | 1.0863e-06 | 0.018247 | 0.018247 | 0.018247 | 0.97037 | -0.57204 | 0.97054 | -0.5685 | 5.013
6 | -0.0084479 | -0.0021172 | 0.0084489 | 0.0021176 | 1.0018e-06 | 4.4342e-07 | 0.012937 | 0.012937 | 0.012937 | 0.97165 | -0.5466 | 0.97178 | -0.54411 | 3.5542
7 | -0.036134 | -0.0090677 | 0.036159 | 0.0090831 | 2.4484e-05 | 1.5405e-05 | 0.055334 | 0.055334 | 0.055334 | 0.97178 | -0.54411 | 0.9725 | -0.52991 | 15.2016
8 | 0.025906 | 0.0065041 | -0.025876 | -0.0064855 | 3.0102e-05 | 1.8634e-05 | 0.039672 | 0.039672 | 0.039672 | 0.97178 | -0.54411 | 0.97054 | -0.5685 | 10.899
9 | 0.010791 | 0.0027048 | -0.01079 | -0.0027044 | 6.7596e-07 | 3.5124e-07 | 0.016545 | 0.016545 | 0.016545 | 0.97054 | -0.5685 | 0.97048 | -0.56981 | 4.5453
10 | 0.0066948 | 0.0016779 | -0.0066938 | -0.0016776 | 1.0069e-06 | 3.2961e-07 | 0.010265 | 0.010265 | 0.010265 | 0.97048 | -0.56981 | 0.97032 | -0.57297 | 2.8201
11 | -0.040534 | -0.01018 | 0.040562 | 0.010197 | 2.7322e-05 | 1.7251e-05 | 0.062029 | 0.062029 | 0.062029 | 0.9725 | -0.52991 | 0.97321 | -0.51579 | 17.0409
12 | 0.32691 | 0.083726 | -0.32592 | -0.083094 | 0.00098966 | 0.00063209 | 0.48865 | 0.48865 | 0.48865 | 0.99679 | -0.06071 | 0.99349 | -0.1234 | 44.7482
13 | -0.33168 | -0.084921 | 0.33265 | 0.085546 | 0.00097844 | 0.00062495 | 0.49577 | 0.49577 | 0.49577 | 0.99679 | -0.06071 | 1 | 0 | 45.4
14 | 0.20485 | 0.052309 | -0.20483 | -0.052296 | 2.0297e-05 | 1.2924e-05 | 0.30717 | 0.30717 | 0.30717 | 0.99349 | -0.1234 | 0.99338 | -0.12545 | 28.1289
15 | 0.12106 | 0.030785 | -0.12106 | -0.030784 | 9.2676e-07 | 5.8438e-07 | 0.18148 | 0.18148 | 0.18148 | 0.99349 | -0.1234 | 0.99348 | -0.12356 | 16.6194
16 | 0.14206 | 0.036477 | -0.14185 | -0.03635 | 0.00020062 | 0.00012702 | 0.2131 | 0.2131 | 0.2131 | 0.99338 | -0.12545 | 0.99185 | -0.15459 | 19.5148
17 | 0.062779 | 0.015818 | -0.062706 | -0.015772 | 7.2746e-05 | 4.6274e-05 | 0.094068 | 0.094068 | 0.094068 | 0.99338 | -0.12545 | 0.99213 | -0.14971 | 25.8428
18 | 0.11728 | 0.029837 | -0.11724 | -0.029811 | 4.2361e-05 | 2.6685e-05 | 0.17582 | 0.17582 | 0.17582 | 0.99348 | -0.12356 | 0.99309 | -0.13106 | 16.101
19 | 0.13681 | 0.035087 | -0.13667 | -0.034993 | 0.00014898 | 9.4255e-05 | 0.20554 | 0.20554 | 0.20554 | 0.99185 | -0.15459 | 0.99067 | -0.17707 | 18.8224
20 | 0.028379 | 0.0071456 | -0.028351 | -0.0071282 | 2.8046e-05 | 1.7417e-05 | 0.042576 | 0.042576 | 0.042576 | 0.99213 | -0.14971 | 0.99106 | -0.1704 | 11.6967
21 | 0.034326 | 0.0086266 | -0.034303 | -0.0086121 | 2.3205e-05 | 1.455e-05 | 0.051492 | 0.051492 | 0.051492 | 0.99213 | -0.14971 | 0.9914 | -0.16388 | 14.1462
22 | 0.016719 | 0.0041939 | -0.016712 | -0.0041899 | 6.8719e-06 | 4.0204e-06 | 0.025053 | 0.025053 | 0.025053 | 0.99309 | -0.13106 | 0.99265 | -0.13969 | 6.8826
23 | 0.10052 | 0.025617 | -0.10043 | -0.025558 | 9.3896e-05 | 5.8812e-05 | 0.15077 | 0.15077 | 0.15077 | 0.99309 | -0.13106 | 0.99208 | -0.15044 | 13.8069
24 | 0.13667 | 0.034993 | -0.1365 | -0.034891 | 0.00016061 | 0.00010227 | 0.20554 | 0.20554 | 0.20554 | 0.99067 | -0.17707 | 0.9894 | -0.20136 | 28.2336
25 | 0.024687 | 0.0062097 | -0.024671 | -0.0062001 | 1.5537e-05 | 9.5557e-06 | 0.037074 | 0.037074 | 0.037074 | 0.99106 | -0.1704 | 0.99038 | -0.18359 | 10.1851
26 | 0.029299 | 0.0073579 | -0.029274 | -0.0073426 | 2.4618e-05 | 1.5318e-05 | 0.043981 | 0.043981 | 0.043981 | 0.9914 | -0.16388 | 0.99049 | -0.18151 | 12.0827
27 | 0.015343 | 0.0038466 | -0.015341 | -0.0038459 | 1.3619e-06 | 7.8286e-07 | 0.023 | 0.023 | 0.023 | 0.99265 | -0.13969 | 0.99255 | -0.14155 | 6.3186
28 | 0.0972 | 0.024749 | -0.097164 | -0.024726 | 3.6728e-05 | 2.2972e-05 | 0.14593 | 0.14593 | 0.14593 | 0.99208 | -0.15044 | 0.99167 | -0.15828 | 13.3635
29 | -0.042947 | -0.010841 | 0.042981 | 0.010863 | 3.3766e-05 | 2.1344e-05 | 0.065273 | 0.065272 | 0.065273 | 0.97948 | -0.39385 | 0.98033 | -0.37745 | 17.932
30 | 0.040085 | 0.010124 | -0.04003 | -0.01009 | 5.4601e-05 | 3.4452e-05 | 0.060924 | 0.060924 | 0.060924 | 0.97948 | -0.39385 | 0.97803 | -0.42231 | 16.7375
31 | -0.047245 | -0.011931 | 0.047273 | 0.011949 | 2.7744e-05 | 1.7575e-05 | 0.071745 | 0.071745 | 0.071745 | 0.98033 | -0.37745 | 0.98095 | -0.3652 | 19.7101
32 | 0.037973 | 0.0095739 | -0.037954 | -0.0095623 | 1.8485e-05 | 1.1646e-05 | 0.057794 | 0.057794 | 0.057794 | 0.97803 | -0.42231 | 0.97751 | -0.43249 | 15.8774
33 | -0.050731 | -0.012816 | 0.050759 | 0.012834 | 2.8489e-05 | 1.8071e-05 | 0.07699 | 0.07699 | 0.07699 | 0.98095 | -0.3652 | 0.98156 | -0.35349 | 21.1511
34 | 0.036965 | 0.0093145 | -0.036905 | -0.0092766 | 6.0209e-05 | 3.79e-05 | 0.056289 | 0.056289 | 0.056289 | 0.97751 | -0.43249 | 0.97577 | -0.4666 | 15.464
35 | 0.010157 | 0.0025459 | -0.010154 | -0.0025448 | 2.2616e-06 | 1.1352e-06 | 0.01551 | 0.01551 | 0.01551 | 0.97443 | -0.49303 | 0.97419 | -0.49771 | 4.2611
36 | -0.012912 | -0.0032364 | 0.012915 | 0.0032383 | 3.3237e-06 | 1.8431e-06 | 0.019717 | 0.019717 | 0.019717 | 0.97443 | -0.49303 | 0.9747 | -0.48763 | 5.4169
37 | 0.0047215 | 0.0011832 | -0.0047209 | -0.0011832 | 5.7501e-07 | 9.7639e-10 | 0.0072117 | 0.0072118 | 0.0072118 | 0.97419 | -0.49771 | 0.97406 | -0.50026 | 1.9813
38 | -0.015331 | -0.0038438 | 0.015335 | 0.0038463 | 4.3606e-06 | 2.5262e-06 | 0.023406 | 0.023405 | 0.023406 | 0.9747 | -0.48763 | 0.975 | -0.48166 | 6.4301
39 | -0.055035 | -0.013905 | 0.055151 | 0.013979 | 0.00011599 | 7.367e-05 | 0.083472 | 0.083472 | 0.083472 | 0.98156 | -0.35349 | 0.98381 | -0.30963 | 22.9319
40 | 0.017649 | 0.0044305 | -0.017636 | -0.0044229 | 1.2672e-05 | 7.5282e-06 | 0.026917 | 0.026917 | 0.026917 | 0.97577 | -0.4666 | 0.975 | -0.48166 | 7.3948
41 | 0.017243 | 0.0043415 | -0.017196 | -0.0043138 | 4.6741e-05 | 2.767e-05 | 0.026302 | 0.026302 | 0.026302 | 0.97577 | -0.4666 | 0.97288 | -0.52346 | 7.2259
42 | -0.060676 | -0.015364 | 0.060765 | 0.01542 | 8.9175e-05 | 5.6714e-05 | 0.091828 | 0.091828 | 0.091828 | 0.98381 | -0.30963 | 0.98539 | -0.27907 | 25.2276
43 | 0.01152 | 0.0028914 | -0.01152 | -0.0028914 | 3.5528e-08 | 1.8949e-08 | 0.017622 | 0.017622 | 0.017622 | 0.97288 | -0.52346 | 0.97288 | -0.52352 | 4.8412
44 | -0.0036286 | -0.0009094 | 0.0036289 | 0.00090924 | 3.083e-07 | -1.5743e-07 | 0.0054566 | 0.0054564 | 0.0054566 | 0.98951 | -0.20036 | 0.98961 | -0.19857 | 1.4991
45 | 0.011993 | 0.0030061 | -0.011991 | -0.0030055 | 1.187e-06 | 6.3462e-07 | 0.018033 | 0.018033 | 0.018033 | 0.98961 | -0.19857 | 0.9895 | -0.20065 | 4.9541
46 | -0.015622 | -0.0039154 | 0.015624 | 0.0039168 | 2.4815e-06 | 1.434e-06 | 0.023489 | 0.023489 | 0.023489 | 0.98961 | -0.19857 | 0.98978 | -0.19524 | 6.4531
47 | 0.0096231 | 0.0024119 | -0.0096222 | -0.0024115 | 8.8046e-07 | 4.195e-07 | 0.014471 | 0.014471 | 0.014471 | 0.9895 | -0.20065 | 0.9894 | -0.20257 | 3.9757
48 | -0.017619 | -0.0044169 | 0.017631 | 0.0044237 | 1.1538e-05 | 6.8202e-06 | 0.026489 | 0.026489 | 0.026489 | 0.98978 | -0.19524 | 0.99049 | -0.18151 | 7.2772
49 | 0.13279 | 0.03396 | -0.13261 | -0.033842 | 0.00018565 | 0.00011866 | 0.19996 | 0.19996 | 0.19996 | 0.9894 | -0.20136 | 0.98789 | -0.2303 | 54.9337
50 | 0.0073156 | 0.0018334 | -0.0073152 | -0.0018333 | 4.1173e-07 | 1.4703e-07 | 0.011002 | 0.011002 | 0.011002 | 0.9894 | -0.20257 | 0.98934 | -0.20375 | 3.0226
51 | 0.011644 | 0.0029189 | -0.011641 | -0.0029178 | 2.1423e-06 | 1.1308e-06 | 0.017492 | 0.017493 | 0.017493 | 0.99049 | -0.18151 | 0.99029 | -0.18537 | 4.8057
52 | 0.12939 | 0.033035 | -0.12897 | -0.032767 | 0.00041893 | 0.00026774 | 0.19511 | 0.19511 | 0.19511 | 0.98789 | -0.2303 | 0.9844 | -0.29753 | 53.6017
53 | 0.0028156 | 0.00070554 | -0.0028155 | -0.00070563 | 7.02e-08 | -8.9116e-08 | 0.0042347 | 0.0042347 | 0.0042347 | 0.98934 | -0.20375 | 0.98931 | -0.20428 | 1.1634
54 | 0.0084765 | 0.0021246 | -0.0084754 | -0.0021241 | 1.0855e-06 | 4.6519e-07 | 0.012737 | 0.012737 | 0.012737 | 0.99029 | -0.18537 | 0.99015 | -0.18806 | 3.4992
55 | 0.12589 | 0.031995 | -0.12568 | -0.031865 | 0.00020372 | 0.00013019 | 0.19045 | 0.19045 | 0.19045 | 0.9844 | -0.29753 | 0.98266 | -0.33119 | 52.3216
56 | -0.058315 | -0.014676 | 0.058401 | 0.014731 | 8.6041e-05 | 5.4705e-05 | 0.089063 | 0.089063 | 0.089063 | 0.97454 | -0.48973 | 0.97611 | -0.45891 | 24.4679
57 | 0.05444 | 0.013705 | -0.054372 | -0.013662 | 6.7736e-05 | 4.3026e-05 | 0.083146 | 0.083146 | 0.083146 | 0.97454 | -0.48973 | 0.97321 | -0.51579 | 22.8422
58 | -0.062391 | -0.015731 | 0.062395 | 0.015733 | 3.5784e-06 | 2.277e-06 | 0.095146 | 0.095146 | 0.095146 | 0.97611 | -0.45891 | 0.97617 | -0.45771 | 26.1389
59 | 0.01381 | 0.0034647 | -0.013806 | -0.0034621 | 4.5712e-06 | 2.586e-06 | 0.021117 | 0.021117 | 0.021117 | 0.97321 | -0.51579 | 0.97286 | -0.52274 | 5.8014
60 | -0.098264 | -0.024745 | 0.098495 | 0.024892 | 0.00023045 | 0.00014715 | 0.14983 | 0.14983 | 0.14983 | 0.97617 | -0.45771 | 0.97867 | -0.40878 | 41.1624
61 | 0.035869 | 0.0090122 | -0.035845 | -0.0089967 | 2.4558e-05 | 1.5443e-05 | 0.054685 | 0.054686 | 0.054686 | 0.97617 | -0.45771 | 0.97544 | -0.47206 | 15.0235
62 | 0.012495 | 0.0031336 | -0.012492 | -0.0031316 | 3.6721e-06 | 2.0174e-06 | 0.019113 | 0.019113 | 0.019113 | 0.97286 | -0.52274 | 0.97255 | -0.52891 | 5.2507
63 | -0.10142 | -0.025625 | 0.10171 | 0.025812 | 0.00029233 | 0.00018668 | 0.15428 | 0.15428 | 0.15428 | 0.97867 | -0.40878 | 0.98175 | -0.34884 | 42.3834
64 | 0.0324 | 0.0081333 | -0.032398 | -0.0081318 | 2.4486e-06 | 1.5337e-06 | 0.04943 | 0.04943 | 0.04943 | 0.97544 | -0.47206 | 0.97536 | -0.47365 | 13.5798
65 | 0.01041 | 0.0026099 | -0.010406 | -0.002608 | 3.6846e-06 | 1.8777e-06 | 0.015927 | 0.015928 | 0.015928 | 0.97255 | -0.52891 | 0.97217 | -0.53634 | 4.3757
66 | 0.017741 | 0.0044516 | -0.017729 | -0.0044448 | 1.1542e-05 | 6.8492e-06 | 0.026891 | 0.026891 | 0.026891 | 0.98175 | -0.34884 | 0.98105 | -0.36249 | 7.3877
67 | -0.11945 | -0.030263 | 0.11955 | 0.030328 | 0.00010136 | 6.4766e-05 | 0.18117 | 0.18117 | 0.18117 | 0.98175 | -0.34884 | 0.98266 | -0.33119 | 49.771
68 | 0.029828 | 0.0074878 | -0.029809 | -0.0074758 | 1.927e-05 | 1.2024e-05 | 0.04551 | 0.04551 | 0.04551 | 0.97536 | -0.47365 | 0.97467 | -0.4872 | 12.5028
69 | 0.0078406 | 0.001965 | -0.0078399 | -0.0019647 | 7.5229e-07 | 3.0877e-07 | 0.012001 | 0.012001 | 0.012001 | 0.97217 | -0.53634 | 0.97207 | -0.53835 | 3.297
70 | 0.014192 | 0.0035584 | -0.014189 | -0.0035567 | 2.8824e-06 | 1.6353e-06 | 0.021526 | 0.021526 | 0.021526 | 0.98105 | -0.36249 | 0.98083 | -0.36676 | 5.9137
71 | 0.0035375 | 0.00088639 | -0.0035372 | -0.00088652 | 2.3963e-07 | -1.2689e-07 | 0.0053654 | 0.0053655 | 0.0053655 | 0.98105 | -0.36249 | 0.98098 | -0.36392 | 1.4741
72 | 0.026999 | 0.0067716 | -0.026994 | -0.0067688 | 4.4603e-06 | 2.7674e-06 | 0.041221 | 0.041221 | 0.041221 | 0.97467 | -0.4872 | 0.97449 | -0.49067 | 11.3244
73 | 0.020344 | 0.005102 | -0.020338 | -0.0050989 | 5.2093e-06 | 3.1546e-06 | 0.031065 | 0.031065 | 0.031065 | 0.97449 | -0.49067 | 0.97422 | -0.49604 | 8.5344
74 | 0.0066508 | 0.0016668 | -0.0066501 | -0.0016666 | 7.2045e-07 | 2.2904e-07 | 0.010155 | 0.010156 | 0.010156 | 0.97449 | -0.49067 | 0.97438 | -0.49294 | 2.79
75 | 0.016948 | 0.004249 | -0.016944 | -0.0042468 | 3.7248e-06 | 2.1993e-06 | 0.025886 | 0.025886 | 0.025886 | 0.97422 | -0.49604 | 0.97399 | -0.50065 | 7.1116
76 | 0.0036681 | 0.00091922 | -0.003668 | -0.00091928 | 1.2672e-07 | -5.3027e-08 | 0.0056017 | 0.0056017 | 0.0056017 | 0.97438 | -0.49294 | 0.97434 | -0.49367 | 1.5389
77 | 0.010981 | 0.0027529 | -0.01098 | -0.002752 | 1.735e-06 | 9.0008e-07 | 0.01666 | 0.01666 | 0.01666 | 0.98083 | -0.36676 | 0.98066 | -0.37007 | 4.577
78 | 0.0077664 | 0.0019467 | -0.0077648 | -0.001946 | 1.5362e-06 | 6.1107e-07 | 0.011784 | 0.011785 | 0.011785 | 0.98066 | -0.37007 | 0.98045 | -0.37423 | 3.2375
79 | -0.0034272 | -0.00085893 | 0.0034274 | 0.00085884 | 1.7098e-07 | -9.7353e-08 | 0.0052373 | 0.0052372 | 0.0052373 | 0.97373 | -0.50579 | 0.97378 | -0.50474 | 1.4388
80 | -0.0055553 | -0.0013921 | 0.0055554 | 0.0013922 | 1.3057e-07 | 2.3454e-08 | 0.0084889 | 0.0084889 | 0.0084889 | 0.97378 | -0.50474 | 0.97381 | -0.50425 | 2.3321
81 | -0.010491 | -0.0026289 | 0.010491 | 0.0026293 | 8.667e-07 | 4.4278e-07 | 0.01603 | 0.01603 | 0.01603 | 0.97381 | -0.50425 | 0.97389 | -0.50251 | 4.4038
82 | 0.0049351 | 0.0012367 | -0.0049345 | -0.0012367 | 6.323e-07 | 3.5846e-08 | 0.007541 | 0.0075411 | 0.0075411 | 0.97381 | -0.50425 | 0.97367 | -0.50694 | 2.0717
83 | -0.013175 | -0.0033019 | 0.013176 | 0.0033025 | 1.1669e-06 | 6.5125e-07 | 0.02013 | 0.02013 | 0.02013 | 0.97389 | -0.50251 | 0.97399 | -0.50065 | 5.5301
84 | 0.0079328 | 0.0019877 | -0.0079312 | -0.0019871 | 1.6655e-06 | 6.6102e-07 | 0.011899 | 0.011899 | 0.011899 | 0.99202 | -0.15185 | 0.99179 | -0.15625 | 3.269
85 | -0.010888 | -0.0027284 | 0.010894 | 0.0027312 | 5.3428e-06 | 2.7294e-06 | 0.016332 | 0.016332 | 0.016332 | 0.99202 | -0.15185 | 0.99255 | -0.14155 | 4.4868
86 | 0.0056971 | 0.0014272 | -0.0056954 | -0.0014269 | 1.6169e-06 | 2.7344e-07 | 0.0085473 | 0.0085475 | 0.0085475 | 0.99179 | -0.15625 | 0.99148 | -0.16222 | 2.3482
87 | 0.0037717 | 0.00094473 | -0.0037711 | -0.00094498 | 5.6355e-07 | -2.4414e-07 | 0.0056603 | 0.0056605 | 0.0056605 | 0.99148 | -0.16222 | 0.99132 | -0.16535 | 1.5551
88 | 0.0015054 | 0.00037713 | -0.0015053 | -0.00037727 | 2.3378e-08 | -1.4245e-07 | 0.0022596 | 0.0022596 | 0.0022596 | 0.99132 | -0.16535 | 0.99131 | -0.16568 | 0.62077
89 | -0.0049856 | -0.0012494 | 0.0049857 | 0.0012494 | 9.1807e-08 | 6.6517e-09 | 0.0076319 | 0.0076319 | 0.0076319 | 0.97205 | -0.53874 | 0.97207 | -0.53835 | 2.0967
90 | 0.0040417 | 0.0010128 | -0.0040415 | -0.0010129 | 2.7361e-07 | -6.1147e-08 | 0.006187 | 0.0061871 | 0.0061871 | 0.97205 | -0.53874 | 0.97198 | -0.54016 | 1.6998
91 | -0.010513 | -0.0026347 | 0.010528 | 0.0026428 | 1.5726e-05 | 8.06e-06 | 0.016105 | 0.016105 | 0.016105 | 0.97129 | -0.55488 | 0.97288 | -0.52352 | 4.4246
92 | 0.094685 | 0.024105 | -0.094649 | -0.024082 | 3.6372e-05 | 2.2721e-05 | 0.14221 | 0.14221 | 0.14221 | 0.99167 | -0.15828 | 0.99125 | -0.16625 | 13.0229
93 | 0.092145 | 0.023454 | -0.092127 | -0.023443 | 1.7963e-05 | 1.1207e-05 | 0.13845 | 0.13845 | 0.13845 | 0.99125 | -0.16625 | 0.99104 | -0.17029 | 12.6787
94 | 0.088868 | 0.022627 | -0.088767 | -0.022563 | 0.00010119 | 6.3008e-05 | 0.13356 | 0.13356 | 0.13356 | 0.99104 | -0.17029 | 0.98981 | -0.19393 | 12.2307
95 | 0.086311 | 0.021948 | -0.086199 | -0.021878 | 0.00011203 | 6.9655e-05 | 0.12987 | 0.12987 | 0.12987 | 0.98981 | -0.19393 | 0.98841 | -0.22091 | 11.8927
96 | 0.083706 | 0.021253 | -0.083657 | -0.021223 | 4.9183e-05 | 3.0527e-05 | 0.12611 | 0.12611 | 0.12611 | 0.98841 | -0.22091 | 0.98777 | -0.23313 | 11.549
97 | 0.080919 | 0.020537 | -0.080911 | -0.020532 | 7.4988e-06 | 4.6444e-06 | 0.12199 | 0.12199 | 0.12199 | 0.98777 | -0.23313 | 0.98767 | -0.23506 | 11.1713
98 | 0.077776 | 0.019746 | -0.077742 | -0.019725 | 3.4361e-05 | 2.1224e-05 | 0.11727 | 0.11727 | 0.11727 | 0.98767 | -0.23506 | 0.9872 | -0.24424 | 10.7388
99 | 0.07614 | 0.019324 | -0.076012 | -0.019243 | 0.00012732 | 8.0171e-05 | 0.11485 | 0.11485 | 0.11485 | 0.9872 | -0.24424 | 0.98539 | -0.27907 | 15.7766
100 | 0.015247 | 0.003823 | -0.015245 | -0.0038214 | 2.7071e-06 | 1.5591e-06 | 0.023025 | 0.023025 | 0.023025 | 0.98539 | -0.27907 | 0.9852 | -0.28279 | 6.3256
101 | 0.013171 | 0.0033018 | -0.013169 | -0.0033005 | 2.4306e-06 | 1.3471e-06 | 0.019894 | 0.019894 | 0.019894 | 0.9852 | -0.28279 | 0.985 | -0.28667 | 5.4653
102 | 0.0066765 | 0.0016733 | -0.0066755 | -0.001673 | 9.7011e-07 | 2.9723e-07 | 0.010086 | 0.010086 | 0.010086 | 0.985 | -0.28667 | 0.98485 | -0.28972 | 2.7709
103 | 0.023143 | 0.0058173 | -0.023123 | -0.0058049 | 2.0273e-05 | 1.24e-05 | 0.034778 | 0.034779 | 0.034779 | 0.99038 | -0.18359 | 0.98943 | -0.20195 | 9.5545
104 | 0.00604 | 0.0015137 | -0.0060392 | -0.0015136 | 7.8022e-07 | 1.746e-07 | 0.009077 | 0.0090772 | 0.0090772 | 0.99015 | -0.18806 | 0.99001 | -0.19077 | 2.4937
105 | 0.021656 | 0.0054373 | -0.02165 | -0.0054333 | 6.5663e-06 | 3.9906e-06 | 0.032573 | 0.032573 | 0.032573 | 0.98943 | -0.20195 | 0.9891 | -0.20831 | 8.9486
106 | 0.012085 | 0.0030293 | -0.012085 | -0.0030291 | 2.3004e-07 | 1.2353e-07 | 0.018205 | 0.018205 | 0.018205 | 0.9878 | -0.23361 | 0.98778 | -0.23401 | 5.0015
107 | -0.014329 | -0.0035916 | 0.014331 | 0.0035927 | 1.8038e-06 | 1.0223e-06 | 0.021586 | 0.021586 | 0.021586 | 0.9878 | -0.23361 | 0.98794 | -0.23097 | 5.9301
108 | 0.010492 | 0.0026298 | -0.01049 | -0.002629 | 1.6845e-06 | 8.4794e-07 | 0.015805 | 0.015805 | 0.015805 | 0.98778 | -0.23401 | 0.98761 | -0.23738 | 4.3422
109 | -0.015657 | -0.0039249 | 0.01566 | 0.0039267 | 3.2107e-06 | 1.8577e-06 | 0.023582 | 0.023582 | 0.023582 | 0.98794 | -0.23097 | 0.98816 | -0.22666 | 6.4786
110 | 0.0082161 | 0.002059 | -0.008216 | -0.002059 | 9.6617e-08 | 4.0321e-08 | 0.012379 | 0.012379 | 0.012379 | 0.98761 | -0.23738 | 0.98759 | -0.23762 | 3.4008
111 | -0.01651 | -0.0041399 | 0.016516 | 0.0041431 | 5.4325e-06 | 3.1765e-06 | 0.024863 | 0.024863 | 0.024863 | 0.98816 | -0.22666 | 0.98851 | -0.21976 | 6.8305
112 | 0.0060967 | 0.0015279 | -0.0060962 | -0.0015277 | 5.436e-07 | 1.2811e-07 | 0.0091859 | 0.009186 | 0.009186 | 0.98759 | -0.23762 | 0.9875 | -0.2395 | 2.5236
113 | -0.017908 | -0.0044921 | 0.017913 | 0.0044949 | 4.6985e-06 | 2.786e-06 | 0.026959 | 0.026959 | 0.026959 | 0.98851 | -0.21976 | 0.9888 | -0.21426 | 7.4063
114 | 0.0046012 | 0.0011531 | -0.0046009 | -0.0011531 | 3.3989e-07 | -2.3665e-08 | 0.0069333 | 0.0069334 | 0.0069334 | 0.9875 | -0.2395 | 0.98742 | -0.24105 | 1.9048
115 | -0.019183 | -0.0048131 | 0.019188 | 0.0048164 | 5.4452e-06 | 3.2614e-06 | 0.02887 | 0.02887 | 0.02887 | 0.9888 | -0.21426 | 0.9891 | -0.20831 | 7.9313
116 | -0.0014114 | -0.00035373 | 0.0014114 | 0.00035372 | 1.1526e-09 | -7.9539e-09 | 0.002127 | 0.002127 | 0.002127 | 0.98742 | -0.24106 | 0.98742 | -0.24105 | 0.58433

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.33866 | 0.086638

## res_load
| p_mw | q_mvar
0 | 0.0034451 | 0.00086342
1 | 0.0021602 | 0.00054141
2 | 0.0016288 | 0.00040821
3 | 0.0046851 | 0.0011742
4 | 0.0051242 | 0.0012842
5 | 0.002089 | 0.00052355
6 | 0.0012128 | 0.00030396
7 | 0.0017794 | 0.00044596
8 | 0.003183 | 0.00079773
9 | 0.0040957 | 0.0010265
10 | 0.0066938 | 0.0016776
11 | 0.0043756 | 0.0010966
12 | 0.0047681 | 0.001195
13 | 0.0043568 | 0.0010919
14 | 0.0037792 | 0.00094715
15 | 0.0050402 | 0.0012632
16 | 0.0036647 | 0.00091846
17 | 0.0050043 | 0.0012542
18 | 0.0013696 | 0.00034325
19 | 0.0032285 | 0.00080913
20 | 0.0028622 | 0.00071734
21 | 0.004264 | 0.0010687
22 | 0.0020577 | 0.00051571
23 | 0.0034579 | 0.00086662
24 | 0.00098858 | 0.00024776
25 | 0.0027551 | 0.00069048
26 | 0.005433 | 0.0013616
27 | 0.002416 | 0.00060551
28 | 0.004276 | 0.0010717
29 | 0.0047209 | 0.0011832
30 | 0.0020137 | 0.00050469
31 | 0.005525 | 0.0013847
32 | 0.0023008 | 0.00057664
33 | 0.0056754 | 0.0014224
34 | 0.0036286 | 0.0009094
35 | 0.0023683 | 0.00059356
36 | 0.0019953 | 0.00050006
37 | 0.0037114 | 0.00093016
38 | 0.0023066 | 0.00057809
39 | 0.0032191 | 0.00080679
40 | 0.0044997 | 0.0011277
41 | 0.0031649 | 0.00079321
42 | 0.0030826 | 0.00077258
43 | 0.0038756 | 0.00097132
44 | 0.0039901 | 0.001
45 | 0.0013105 | 0.00032845
46 | 0.0029232 | 0.00073261
47 | 0.0034449 | 0.00086337
48 | 0.0020818 | 0.00052175
49 | 0.0025697 | 0.00064402
50 | 0.0025654 | 0.00064296
51 | 0.0061311 | 0.0015366
52 | 0.0028096 | 0.00070416
53 | 0.0033909 | 0.00084985
54 | 0.002982 | 0.00074735
55 | 0.0028155 | 0.00070563
56 | 0.0035372 | 0.00088652
57 | 0.0032073 | 0.00080383
58 | 0.0032134 | 0.00080535
59 | 0.0077648 | 0.001946
60 | 0.0034272 | 0.00085893
61 | 0.0021279 | 0.00053331
62 | 0.0026834 | 0.00067251
63 | 0.0049345 | 0.0012367
64 | 0.0037679 | 0.00094432
65 | 0.0029554 | 0.0007407
66 | 0.0022341 | 0.00055992
67 | 0.0044477 | 0.0011147
68 | 0.0019238 | 0.00048215
69 | 0.0022657 | 0.00056784
70 | 0.0015053 | 0.00037727
71 | 0.00094386 | 0.00023655
72 | 0.0028542 | 0.00071533
73 | 0.0040415 | 0.0010129
74 | 0.010513 | 0.0026347
75 | 0.00099192 | 0.0002486
76 | 0.0024786 | 0.0006212
77 | 0.0025039 | 0.00062754
78 | 0.0032585 | 0.00081665
79 | 0.0024558 | 0.00061548
80 | 0.0024935 | 0.00062493
81 | 0.0027376 | 0.00068612
82 | 0.003135 | 0.0007857
83 | 0.0016023 | 0.00040157
84 | 0.003668 | 0.00091928
85 | 0.0020733 | 0.00051961
86 | 0.0064924 | 0.0016271
87 | 0.0066755 | 0.001673
88 | 0.0015277 | 0.00038288
89 | 0.0024354 | 0.00061036
90 | 0.0014667 | 0.0003676
91 | 0.0060392 | 0.0015136
92 | 0.0022439 | 0.00056238
93 | 0.0015933 | 0.00039931
94 | 0.0013255 | 0.00033219
95 | 0.0022741 | 0.00056994
96 | 0.00085072 | 0.00021321
97 | 0.0021193 | 0.00053115
98 | 0.0013925 | 0.000349
99 | 0.001495 | 0.00037467
100 | 0.0012698 | 0.00031825
101 | 0.0014114 | 0.00035373
102 | 0.0031895 | 0.00079935
103 | 0.0024613 | 0.00061687

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1