## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3215-16_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3215-16_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3215-16_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3215-16_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3215-16_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3215-16_0_6_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_3215-16_0_6_node_19 | 0.4 | n |  | TRUE
7 | bus_LV_3215-16_0_6_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_3215-16_0_6_node_5 | 0.4 | n |  | TRUE
9 | bus_LV_3215-16_0_6_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_3215-16_0_6_node_41 | 0.4 | n |  | TRUE
11 | bus_LV_3215-16_0_6_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_3215-16_0_6_node_51 | 0.4 | n |  | TRUE
13 | bus_LV_3215-16_0_6_node_8 | 0.4 | n |  | TRUE
14 | bus_LV_3215-16_0_6_node_49 | 0.4 | n |  | TRUE
15 | bus_LV_3215-16_0_6_node_48 | 0.4 | n |  | TRUE
16 | bus_LV_3215-16_0_6_node_15 | 0.4 | n |  | TRUE
17 | bus_LV_3215-16_0_6_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_3215-16_0_6_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_3215-16_0_6_node_40 | 0.4 | n |  | TRUE
20 | bus_LV_3215-16_0_6_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_3215-16_0_6_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_3215-16_0_6_node_12 | 0.4 | n |  | TRUE
23 | bus_LV_3215-16_0_6_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_3215-16_0_6_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_3215-16_0_6_node_25 | 0.4 | n |  | TRUE
26 | bus_LV_3215-16_0_6_node_103 | 0.4 | n |  | TRUE
27 | bus_LV_3215-16_0_6_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_3215-16_0_6_node_17 | 0.4 | n |  | TRUE
29 | bus_LV_3215-16_0_6_node_61 | 0.4 | n |  | TRUE
30 | bus_LV_3215-16_0_6_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_3215-16_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_3215-16_0_6_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_3215-16_0_6_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_3215-16_0_6_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_3215-16_0_6_node_36 | 0.4 | n |  | TRUE
36 | bus_LV_3215-16_0_6_node_26 | 0.4 | n |  | TRUE
37 | bus_LV_3215-16_0_6_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_3215-16_0_6_node_91 | 0.4 | n |  | TRUE
39 | bus_LV_3215-16_0_6_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_3215-16_0_6_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_3215-16_0_6_node_95 | 0.4 | n |  | TRUE
42 | bus_LV_3215-16_0_6_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_3215-16_0_6_node_94 | 0.4 | n |  | TRUE
44 | bus_LV_3215-16_0_6_node_99 | 0.4 | n |  | TRUE
45 | bus_LV_3215-16_0_6_node_92 | 0.4 | n |  | TRUE
46 | bus_LV_3215-16_0_6_node_33 | 0.4 | n |  | TRUE
47 | bus_LV_3215-16_0_6_node_73 | 0.4 | n |  | TRUE
48 | bus_LV_3215-16_0_6_node_72 | 0.4 | n |  | TRUE
49 | bus_LV_3215-16_0_6_node_34 | 0.4 | n |  | TRUE
50 | bus_LV_3215-16_0_6_node_96 | 0.4 | n |  | TRUE
51 | bus_LV_3215-16_0_6_node_75 | 0.4 | n |  | TRUE
52 | bus_LV_3215-16_0_6_node_66 | 0.4 | n |  | TRUE
53 | bus_LV_3215-16_0_6_node_97 | 0.4 | n |  | TRUE
54 | bus_LV_3215-16_0_6_node_93 | 0.4 | n |  | TRUE
55 | bus_LV_3215-16_0_6_node_100 | 0.4 | n |  | TRUE
56 | bus_LV_3215-16_0_6_node_102 | 0.4 | n |  | TRUE
57 | bus_LV_3215-16_0_6_node_101 | 0.4 | n |  | TRUE
58 | bus_LV_3215-16_0_6_node_71 | 0.4 | n |  | TRUE
59 | bus_LV_3215-16_0_6_node_85 | 0.4 | n |  | TRUE
60 | bus_LV_3215-16_0_6_node_89 | 0.4 | n |  | TRUE
61 | bus_LV_3215-16_0_6_node_90 | 0.4 | n |  | TRUE
62 | bus_LV_3215-16_0_6_node_76 | 0.4 | n |  | TRUE
63 | bus_LV_3215-16_0_6_node_65 | 0.4 | n |  | TRUE
64 | bus_LV_3215-16_0_6_node_37 | 0.4 | n |  | TRUE
65 | bus_LV_3215-16_0_6_node_38 | 0.4 | n |  | TRUE
66 | bus_LV_3215-16_0_6_node_44 | 0.4 | n |  | TRUE
67 | bus_LV_3215-16_0_6_node_43 | 0.4 | n |  | TRUE
68 | bus_LV_3215-16_0_6_node_45 | 0.4 | n |  | TRUE
69 | bus_LV_3215-16_0_6_node_46 | 0.4 | n |  | TRUE
70 | bus_LV_3215-16_0_6_node_67 | 0.4 | n |  | TRUE
71 | bus_LV_3215-16_0_6_node_83 | 0.4 | n |  | TRUE
72 | bus_LV_3215-16_0_6_node_68 | 0.4 | n |  | TRUE
73 | bus_LV_3215-16_0_6_node_56 | 0.4 | n |  | TRUE
74 | bus_LV_3215-16_0_6_node_81 | 0.4 | n |  | TRUE
75 | bus_LV_3215-16_0_6_node_52 | 0.4 | n |  | TRUE
76 | bus_LV_3215-16_0_6_node_53 | 0.4 | n |  | TRUE
77 | bus_LV_3215-16_0_6_node_54 | 0.4 | n |  | TRUE
78 | bus_LV_3215-16_0_6_node_55 | 0.4 | n |  | TRUE
79 | bus_LV_3215-16_0_6_node_57 | 0.4 | n |  | TRUE
80 | bus_LV_3215-16_0_6_node_58 | 0.4 | n |  | TRUE
81 | bus_LV_3215-16_0_6_node_60 | 0.4 | n |  | TRUE
82 | bus_LV_3215-16_0_6_node_62 | 0.4 | n |  | TRUE
83 | bus_LV_3215-16_0_6_node_63 | 0.4 | n |  | TRUE
84 | bus_LV_3215-16_0_6_node_64 | 0.4 | n |  | TRUE
85 | bus_LV_3215-16_0_6_node_69 | 0.4 | n |  | TRUE
86 | bus_LV_3215-16_0_6_node_70 | 0.4 | n |  | TRUE
87 | bus_LV_3215-16_0_6_node_77 | 0.4 | n |  | TRUE
88 | bus_LV_3215-16_0_6_node_78 | 0.4 | n |  | TRUE
89 | bus_LV_3215-16_0_6_node_79 | 0.4 | n |  | TRUE
90 | bus_LV_3215-16_0_6_node_80 | 0.4 | n |  | TRUE
91 | bus_LV_3215-16_0_6_node_82 | 0.4 | n |  | TRUE
92 | bus_LV_3215-16_0_6_node_84 | 0.4 | n |  | TRUE
93 | bus_LV_3215-16_0_6_node_88 | 0.4 | n |  | TRUE
94 | bus_LV_3215-16_0_6_node_98 | 0.4 | n |  | TRUE
95 | bus_LV_3215-16_0_6_node_87 | 0.4 | n |  | TRUE
96 | bus_MV_235_0_node_31 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3215-16_0_6_load_0 | 0 | 0.018228 | 0.0045684 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3215-16_0_6_load_1 | 1 | 0.017256 | 0.0043248 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3215-16_0_6_load_3 | 3 | 0.0077579 | 0.0019443 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3215-16_0_6_load_4 | 4 | 0.011519 | 0.0028869 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3215-16_0_6_load_50 | 7 | 0.030005 | 0.0075199 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3215-16_0_6_load_41 | 10 | 0.01542 | 0.0038646 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3215-16_0_6_load_51 | 12 | 0.012844 | 0.0032189 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3215-16_0_6_load_49 | 14 | 0.023848 | 0.0059768 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3215-16_0_6_load_48 | 15 | 0.0079831 | 0.0020008 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3215-16_0_6_load_15 | 16 | 0.0080666 | 0.0020217 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3215-16_0_6_load_21 | 17 | 0.006337 | 0.0015882 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3215-16_0_6_load_10 | 20 | 0.0063352 | 0.0015878 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3215-16_0_6_load_11 | 21 | 0.0063104 | 0.0015815 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3215-16_0_6_load_12 | 22 | 0.0043106 | 0.0010803 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3215-16_0_6_load_13 | 23 | 0.006337 | 0.0015882 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3215-16_0_6_load_20 | 24 | 0.010266 | 0.0025729 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3215-16_0_6_load_103 | 26 | 0.0095746 | 0.0023996 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3215-16_0_6_load_17 | 28 | 0.008102 | 0.0020305 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3215-16_0_6_load_61 | 29 | 0.0022079 | 0.00055336 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3215-16_0_6_load_59 | 30 | 0.0090639 | 0.0022716 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3215-16_0_6_load_22 | 31 | 0.011919 | 0.0029873 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3215-16_0_6_load_36 | 35 | 0.0014103 | 0.00035345 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3215-16_0_6_load_91 | 38 | 0.0053976 | 0.0013528 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3215-16_0_6_load_74 | 39 | 0.0011504 | 0.00028831 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3215-16_0_6_load_95 | 41 | 0.0073816 | 0.00185 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3215-16_0_6_load_94 | 43 | 0.0055825 | 0.0013991 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3215-16_0_6_load_99 | 44 | 0.0050746 | 0.0012718 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3215-16_0_6_load_92 | 45 | 0.018683 | 0.0046824 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3215-16_0_6_load_73 | 47 | 0.0014419 | 0.00036136 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3215-16_0_6_load_72 | 48 | 0.0026113 | 0.00065446 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3215-16_0_6_load_96 | 50 | 0.0040316 | 0.0010104 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3215-16_0_6_load_75 | 51 | 0.0046493 | 0.0011652 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3215-16_0_6_load_66 | 52 | 0.0014616 | 0.00036631 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3215-16_0_6_load_97 | 53 | 0.0050521 | 0.0012662 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3215-16_0_6_load_93 | 54 | 0.0014868 | 0.00037262 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3215-16_0_6_load_100 | 55 | 0.020339 | 0.0050974 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3215-16_0_6_load_102 | 56 | 0.014665 | 0.0036754 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3215-16_0_6_load_71 | 58 | 0.0010548 | 0.00026435 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3215-16_0_6_load_89 | 60 | 0.0028615 | 0.00071715 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3215-16_0_6_load_90 | 61 | 0.0045478 | 0.0011398 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3215-16_0_6_load_76 | 62 | 0.013773 | 0.0034518 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3215-16_0_6_load_65 | 63 | 0.0044675 | 0.0011197 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3215-16_0_6_load_37 | 64 | 0.0063242 | 0.001585 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3215-16_0_6_load_44 | 66 | 0.0040496 | 0.0010149 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3215-16_0_6_load_43 | 67 | 0.018652 | 0.0046745 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3215-16_0_6_load_83 | 71 | 0.0025137 | 0.00063 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3215-16_0_6_load_68 | 72 | 0.0022705 | 0.00056905 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3215-16_0_6_load_56 | 73 | 0.0033519 | 0.00084007 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3215-16_0_6_load_81 | 74 | 0.0034524 | 0.00086526 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3215-16_0_6_load_53 | 76 | 0.012196 | 0.0030567 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3215-16_0_6_load_54 | 77 | 0.0022307 | 0.00055907 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3215-16_0_6_load_55 | 78 | 0.0022221 | 0.00055692 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3215-16_0_6_load_57 | 79 | 0.0095318 | 0.0023889 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3215-16_0_6_load_60 | 81 | 0.0011494 | 0.00028807 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3215-16_0_6_load_62 | 82 | 0.006816 | 0.0017082 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3215-16_0_6_load_63 | 83 | 0.0010445 | 0.00026178 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3215-16_0_6_load_64 | 84 | 0.0010238 | 0.00025658 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3215-16_0_6_load_69 | 85 | 0.0017835 | 0.00044699 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3215-16_0_6_load_70 | 86 | 0.0010195 | 0.00025551 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3215-16_0_6_load_77 | 87 | 0.0040979 | 0.001027 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3215-16_0_6_load_78 | 88 | 0.0039597 | 0.00099239 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3215-16_0_6_load_79 | 89 | 0.0035 | 0.00087718 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3215-16_0_6_load_80 | 90 | 0.0028682 | 0.00071883 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3215-16_0_6_load_82 | 91 | 0.002632 | 0.00065964 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3215-16_0_6_load_84 | 92 | 0.008374 | 0.0020987 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3215-16_0_6_load_88 | 93 | 0.056186 | 0.014081 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3215-16_0_6_load_98 | 94 | 0.0060267 | 0.0015104 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3215-16_0_6_load_87 | 95 | 0.0062005 | 0.001554 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 73 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3215-16_0_6_line_0 |  | 0 | 1 | 0.0072219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3215-16_0_6_line_1 |  | 0 | 2 | 0.026998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3215-16_0_6_line_2 |  | 1 | 3 | 0.021092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_3215-16_0_6_line_3 |  | 2 | 4 | 0.023619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3215-16_0_6_line_4 |  | 2 | 5 | 0.065205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3215-16_0_6_line_5 |  | 3 | 6 | 0.031938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_3215-16_0_6_line_6 |  | 4 | 7 | 0.03365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3215-16_0_6_line_7 |  | 5 | 16 | 0.023825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3215-16_0_6_line_8 |  | 6 | 17 | 0.024352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3215-16_0_6_line_9 |  | 6 | 18 | 0.025736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_3215-16_0_6_line_10 |  | 7 | 14 | 0.031274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3215-16_0_6_line_11 |  | 8 | 9 | 0.009576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3215-16_0_6_line_12 |  | 8 | 10 | 0.043604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3215-16_0_6_line_13 |  | 9 | 13 | 0.003168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3215-16_0_6_line_14 |  | 11 | 12 | 0.036784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3215-16_0_6_line_15 |  | 11 | 13 | 0.044695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3215-16_0_6_line_16 |  | 11 | 14 | 0.024098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3215-16_0_6_line_17 |  | 13 | 15 | 0.01975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3215-16_0_6_line_18 |  | 15 | 19 | 0.039794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3215-16_0_6_line_19 |  | 17 | 28 | 0.0094166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3215-16_0_6_line_20 |  | 18 | 24 | 0.015209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_3215-16_0_6_line_21 |  | 18 | 23 | 0.020285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3215-16_0_6_line_22 |  | 19 | 65 | 0.01695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3215-16_0_6_line_23 |  | 20 | 21 | 0.0093886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3215-16_0_6_line_24 |  | 20 | 22 | 0.0123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3215-16_0_6_line_25 |  | 21 | 23 | 0.02161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3215-16_0_6_line_26 |  | 24 | 29 | 0.019304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_3215-16_0_6_line_27 |  | 25 | 26 | 0.012401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3215-16_0_6_line_28 |  | 25 | 27 | 0.010218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3215-16_0_6_line_29 |  | 27 | 33 | 0.058561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3215-16_0_6_line_30 |  | 27 | 31 | 0.032356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3215-16_0_6_line_31 |  | 29 | 30 | 0.0052255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_3215-16_0_6_line_32 |  | 30 | 80 | 0.017214 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_3215-16_0_6_line_33 |  | 31 | 32 | 0.033414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3215-16_0_6_line_34 |  | 32 | 34 | 0.01122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3215-16_0_6_line_35 |  | 32 | 35 | 0.019921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3215-16_0_6_line_36 |  | 33 | 45 | 0.051404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3215-16_0_6_line_37 |  | 34 | 39 | 0.011588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3215-16_0_6_line_38 |  | 34 | 36 | 0.0097128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3215-16_0_6_line_39 |  | 35 | 52 | 0.021585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3215-16_0_6_line_40 |  | 36 | 37 | 0.037954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3215-16_0_6_line_41 |  | 36 | 38 | 0.0063989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3215-16_0_6_line_42 |  | 37 | 44 | 0.019084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3215-16_0_6_line_43 |  | 39 | 47 | 0.0079082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3215-16_0_6_line_44 |  | 40 | 41 | 0.029882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3215-16_0_6_line_45 |  | 40 | 42 | 0.010075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3215-16_0_6_line_46 |  | 40 | 43 | 0.014545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3215-16_0_6_line_47 |  | 41 | 53 | 0.023544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3215-16_0_6_line_48 |  | 42 | 51 | 0.0024136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3215-16_0_6_line_49 |  | 42 | 46 | 0.012679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3215-16_0_6_line_50 |  | 42 | 49 | 0.022319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3215-16_0_6_line_51 |  | 43 | 54 | 0.0087711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3215-16_0_6_line_52 |  | 44 | 55 | 0.023891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3215-16_0_6_line_53 |  | 46 | 47 | 0.032095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3215-16_0_6_line_54 |  | 46 | 48 | 0.014002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_3215-16_0_6_line_55 |  | 48 | 58 | 0.021358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_3215-16_0_6_line_56 |  | 49 | 50 | 0.016265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3215-16_0_6_line_57 |  | 51 | 62 | 0.033693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3215-16_0_6_line_58 |  | 52 | 63 | 0.0032224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3215-16_0_6_line_59 |  | 53 | 94 | 0.0028489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3215-16_0_6_line_60 |  | 55 | 57 | 0.038272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3215-16_0_6_line_61 |  | 56 | 57 | 0.033364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3215-16_0_6_line_62 |  | 58 | 86 | 0.0063544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
63 | LV_3215-16_0_6_line_63 |  | 59 | 60 | 0.020893 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3215-16_0_6_line_64 |  | 59 | 61 | 0.0088114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3215-16_0_6_line_65 |  | 60 | 93 | 0.022191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3215-16_0_6_line_66 |  | 61 | 88 | 0.012068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3215-16_0_6_line_67 |  | 62 | 87 | 0.023182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3215-16_0_6_line_68 |  | 63 | 84 | 0.003903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3215-16_0_6_line_69 |  | 64 | 65 | 0.02306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3215-16_0_6_line_70 |  | 66 | 67 | 0.0034503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3215-16_0_6_line_71 |  | 67 | 68 | 0.026786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3215-16_0_6_line_72 |  | 68 | 69 | 0.008457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3215-16_0_6_line_73 |  | 69 | 70 | 0.017672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3215-16_0_6_line_74 |  | 69 | 71 | 0.010808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3215-16_0_6_line_75 |  | 70 | 72 | 0.022805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_3215-16_0_6_line_76 |  | 70 | 73 | 0.0078582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_3215-16_0_6_line_77 |  | 71 | 74 | 0.0031346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3215-16_0_6_line_78 |  | 72 | 85 | 0.0075342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_3215-16_0_6_line_79 |  | 73 | 75 | 0.0066503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_3215-16_0_6_line_80 |  | 74 | 89 | 0.0096475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3215-16_0_6_line_81 |  | 75 | 76 | 0.020421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
82 | LV_3215-16_0_6_line_82 |  | 76 | 77 | 0.016389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
83 | LV_3215-16_0_6_line_83 |  | 77 | 78 | 0.0088686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_3215-16_0_6_line_84 |  | 78 | 79 | 0.0069184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_3215-16_0_6_line_85 |  | 79 | 80 | 0.0072864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_3215-16_0_6_line_86 |  | 81 | 82 | 0.0004647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3215-16_0_6_line_87 |  | 82 | 83 | 0.0076905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3215-16_0_6_line_88 |  | 83 | 84 | 0.0061414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3215-16_0_6_line_89 |  | 85 | 86 | 0.0064348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_3215-16_0_6_line_90 |  | 87 | 88 | 0.00047139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3215-16_0_6_line_91 |  | 89 | 90 | 0.011776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3215-16_0_6_line_92 |  | 90 | 91 | 0.0070598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3215-16_0_6_line_93 |  | 91 | 92 | 0.00050695 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3215-16_0_6_line_94 |  | 93 | 95 | 0.00030638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3215-16_0_6_trafo_56 | 0.63 MVA 20/0.4 kV | 96 | 73 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2754054.2753 | 1260823.3067 | 2754051.709 | 1260816.5562
1 | 2754063.8691 | 1260848.5432 | 2754054.2753 | 1260823.3067
2 | 2754051.709 | 1260816.5562 | 2754044.2139 | 1260796.8403
3 | 2754063.8691 | 1260848.5432 | 2754085.8149 | 1260839.8109
4 | 2754026.2549 | 1260884.289 | 2754070.2667 | 1260864.0254 | 2754063.8691 | 1260848.5432
5 | 2754021.6157 | 1260776.7259 | 2754040.5689 | 1260787.2522 | 2754044.2139 | 1260796.8403
6 | 2754085.8149 | 1260839.8109 | 2754115.55 | 1260827.9793 | 2754117.0974 | 1260827.4146
7 | 2754026.2549 | 1260884.289 | 2754015.9046 | 1260862.8295
8 | 2754021.6157 | 1260776.7259 | 2754004.3512 | 1260786.7533 | 2753999.967 | 1260786.5946 | 2753999.967 | 1260786.5946
9 | 2754008.4274 | 1260756.4843 | 2754008.3029 | 1260761.2637 | 2754010.936 | 1260767.8611 | 2754021.6157 | 1260776.7259
10 | 2754146.4763 | 1260816.6935 | 2754117.0974 | 1260827.4146
11 | 2754211.174 | 1260804.8696 | 2754220.3627 | 1260802.0841
12 | 2754220.3627 | 1260802.0841 | 2754219.1804 | 1260798.85 | 2754206.7399 | 1260760.6648
13 | 2754211.174 | 1260804.8696 | 2754208.1269 | 1260805.7689
14 | 2754169.7711 | 1260810.641 | 2754155.7365 | 1260776.6391
15 | 2754169.7711 | 1260810.641 | 2754172.5514 | 1260817.3647 | 2754186.0552 | 1260812.7675 | 2754208.1269 | 1260805.7689
16 | 2754169.7711 | 1260810.641 | 2754151.3064 | 1260814.9309 | 2754146.4763 | 1260816.6935
17 | 2754208.1269 | 1260805.7689 | 2754207.3523 | 1260803.0905 | 2754202.9192 | 1260790.0617 | 2754199.9194 | 1260791.1735
18 | 2754212.3699 | 1260828.9697 | 2754203.7951 | 1260803.0199 | 2754199.9194 | 1260791.1735
19 | 2753999.967 | 1260786.5946 | 2753993.4057 | 1260793.349
20 | 2754008.4274 | 1260756.4843 | 2754011.5886 | 1260753.23 | 2754017.6938 | 1260751.5872 | 2754022.0439 | 1260751.6116
21 | 2754008.4274 | 1260756.4843 | 2754004.6826 | 1260750.8812 | 2754000.4354 | 1260738.0187
22 | 2754212.3699 | 1260828.9697 | 2754204.6215 | 1260831.4592 | 2754205.8419 | 1260835.2615 | 2754207.2897 | 1260839.8817
23 | 2753990.7156 | 1260708.5829 | 2753993.6594 | 1260717.4981
24 | 2753990.7156 | 1260708.5829 | 2753989.9571 | 1260706.2861 | 2753987.9811 | 1260696.6041
25 | 2753993.6594 | 1260717.4981 | 2754000.4354 | 1260738.0187
26 | 2754040.7622 | 1260749.8784 | 2754026.6203 | 1260753.0767 | 2754022.0439 | 1260751.6116
27 | 2753969.6482 | 1260658.3424 | 2753979.9485 | 1260651.3923
28 | 2753979.9485 | 1260651.3923 | 2753981.0275 | 1260641.2323
29 | 2753932.5441 | 1260631.6277 | 2753932.5698 | 1260635.8549 | 2753941.009 | 1260638.11 | 2753948.3313 | 1260637.8002 | 2753951.4416 | 1260637.6588 | 2753981.5569 | 1260636.2521 | 2753981.0275 | 1260641.2323
30 | 2753981.0275 | 1260641.2323 | 2754013.3801 | 1260640.7511
31 | 2754040.7622 | 1260749.8784 | 2754045.8589 | 1260748.7257
32 | 2754062.6489 | 1260744.9286 | 2754045.8589 | 1260748.7257
33 | 2754046.7901 | 1260640.2541 | 2754013.3801 | 1260640.7511
34 | 2754046.7901 | 1260640.2541 | 2754058.0431 | 1260640.147
35 | 2754046.7901 | 1260640.2541 | 2754047.735 | 1260660.1528
36 | 2753932.5441 | 1260631.6277 | 2753983.9454 | 1260631.1399
37 | 2754058.0431 | 1260640.147 | 2754069.6308 | 1260640.0369
38 | 2754057.7155 | 1260630.4398 | 2754057.877 | 1260635.2377 | 2754058.0431 | 1260640.147
39 | 2754049.7605 | 1260681.6273 | 2754048.1338 | 1260668.5511 | 2754047.735 | 1260660.1528
40 | 2754057.7155 | 1260630.4398 | 2754067.1085 | 1260629.6613 | 2754072.0134 | 1260628.0763 | 2754076.469 | 1260624.9225 | 2754079.2139 | 1260621.446 | 2754086.2474 | 1260609.9397
41 | 2754057.7155 | 1260630.4398 | 2754051.3169 | 1260630.5005
42 | 2754086.2474 | 1260609.9397 | 2754074.5856 | 1260606.6327 | 2754068.2116 | 1260603.8305
43 | 2754069.6308 | 1260640.0369 | 2754077.5386 | 1260639.9617
44 | 2754122.1057 | 1260629.4712 | 2754151.9873 | 1260629.3443
45 | 2754122.1057 | 1260629.4712 | 2754122.2323 | 1260634.7354 | 2754122.3483 | 1260639.5433
46 | 2754122.1057 | 1260629.4712 | 2754120.8799 | 1260614.9782
47 | 2754151.9873 | 1260629.3443 | 2754162.4513 | 1260629.2998 | 2754175.5227 | 1260628.8148
48 | 2754122.3483 | 1260639.5433 | 2754124.7617 | 1260639.5205
49 | 2754122.3483 | 1260639.5433 | 2754109.6322 | 1260639.6566
50 | 2754122.3483 | 1260639.5433 | 2754122.2323 | 1260634.7354 | 2754139.7403 | 1260634.4801
51 | 2754120.1407 | 1260606.2383 | 2754120.8799 | 1260614.9782
52 | 2754068.2116 | 1260603.8305 | 2754068.2116 | 1260603.8305 | 2754064.6572 | 1260597.5761 | 2754059.2488 | 1260581.7793
53 | 2754109.6322 | 1260639.6566 | 2754077.5386 | 1260639.9617
54 | 2754109.6322 | 1260639.6566 | 2754109.8321 | 1260653.6569
55 | 2754111.1892 | 1260674.9172 | 2754110.0377 | 1260668.0626 | 2754109.8321 | 1260653.6569
56 | 2754139.7403 | 1260634.4801 | 2754139.5936 | 1260618.2161
57 | 2754124.7617 | 1260639.5205 | 2754158.4532 | 1260639.2028
58 | 2754050.1583 | 1260684.825 | 2754049.7605 | 1260681.6273
59 | 2754175.5227 | 1260628.8148 | 2754178.3696 | 1260628.7091
60 | 2754046.8522 | 1260545.571 | 2754059.2488 | 1260581.7793
61 | 2754046.8522 | 1260545.571 | 2754015.6181 | 1260557.3018
62 | 2754112.2419 | 1260681.1839 | 2754111.1892 | 1260674.9172
63 | 2754202.8908 | 1260639.4083 | 2754203.7785 | 1260660.2828
64 | 2754202.8908 | 1260639.4083 | 2754200.9687 | 1260638.802 | 2754194.173 | 1260638.8661
65 | 2754207.1002 | 1260682.1744 | 2754204.0358 | 1260666.332 | 2754203.7785 | 1260660.2828
66 | 2754182.1053 | 1260638.9798 | 2754194.173 | 1260638.8661
67 | 2754158.4532 | 1260639.2028 | 2754181.634 | 1260638.9843
68 | 2754050.1583 | 1260684.825 | 2754050.6401 | 1260688.6981
69 | 2754207.2897 | 1260839.8817 | 2754184.8245 | 1260845.0837
70 | 2754172.4662 | 1260709.1766 | 2754175.827 | 1260708.3958
71 | 2754146.3476 | 1260715.0783 | 2754147.7239 | 1260714.9251 | 2754172.4662 | 1260709.1766
72 | 2754146.3476 | 1260715.0783 | 2754141.7711 | 1260712.4564 | 2754138.5666 | 1260712.4507
73 | 2754121.4681 | 1260716.3871 | 2754129.8232 | 1260713.1904 | 2754138.5666 | 1260712.4507
74 | 2754138.5666 | 1260712.4507 | 2754138.5699 | 1260701.6427
75 | 2754121.4681 | 1260716.3871 | 2754116.6172 | 1260707.2292 | 2754114.5561 | 1260694.9599
76 | 2754121.4681 | 1260716.3871 | 2754119.611 | 1260718.7856 | 2754118.0817 | 1260723.3615
77 | 2754138.5699 | 1260701.6427 | 2754138.5709 | 1260698.5082
78 | 2754114.5561 | 1260694.9599 | 2754113.308 | 1260687.5298
79 | 2754120.2249 | 1260729.657 | 2754118.0817 | 1260723.3615
80 | 2754139.5715 | 1260688.9531 | 2754138.5722 | 1260694.3102 | 2754138.5709 | 1260698.5082
81 | 2754120.2249 | 1260729.657 | 2754114.9352 | 1260732.9893 | 2754101.121 | 1260736.1437
82 | 2754101.121 | 1260736.1437 | 2754085.1433 | 1260739.7921
83 | 2754076.4972 | 1260741.7664 | 2754085.1433 | 1260739.7921
84 | 2754069.7524 | 1260743.3066 | 2754076.4972 | 1260741.7664
85 | 2754062.6489 | 1260744.9286 | 2754069.7524 | 1260743.3066
86 | 2754052.4033 | 1260702.4141 | 2754052.5122 | 1260702.8658
87 | 2754052.4033 | 1260702.4141 | 2754052.2858 | 1260701.9263 | 2754051.3983 | 1260694.7925
88 | 2754051.3983 | 1260694.7925 | 2754050.6401 | 1260688.6981
89 | 2754113.308 | 1260687.5298 | 2754112.2419 | 1260681.1839
90 | 2754182.1053 | 1260638.9798 | 2754181.634 | 1260638.9843
91 | 2754139.5715 | 1260688.9531 | 2754139.5715 | 1260688.9531 | 2754141.8526 | 1260686.1986 | 2754149.9358 | 1260684.8186
92 | 2754149.9358 | 1260684.8186 | 2754156.8949 | 1260683.6306
93 | 2754157.3946 | 1260683.5453 | 2754156.8949 | 1260683.6306
94 | 2754207.1584 | 1260682.4752 | 2754207.1002 | 1260682.1744

## bus_geodata
| x | y | coords
0 | 2754054.2753 | 1260823.3067
1 | 2754051.709 | 1260816.5562
2 | 2754063.8691 | 1260848.5432
3 | 2754044.2139 | 1260796.8403
4 | 2754085.8149 | 1260839.8109
5 | 2754026.2549 | 1260884.289
6 | 2754021.6157 | 1260776.7259
7 | 2754117.0974 | 1260827.4146
8 | 2754220.3627 | 1260802.0841
9 | 2754211.174 | 1260804.8696
10 | 2754206.7399 | 1260760.6648
11 | 2754169.7711 | 1260810.641
12 | 2754155.7365 | 1260776.6391
13 | 2754208.1269 | 1260805.7689
14 | 2754146.4763 | 1260816.6935
15 | 2754199.9194 | 1260791.1735
16 | 2754015.9046 | 1260862.8295
17 | 2753999.967 | 1260786.5946
18 | 2754008.4274 | 1260756.4843
19 | 2754212.3699 | 1260828.9697
20 | 2753990.7156 | 1260708.5829
21 | 2753993.6594 | 1260717.4981
22 | 2753987.9811 | 1260696.6041
23 | 2754000.4354 | 1260738.0187
24 | 2754022.0439 | 1260751.6116
25 | 2753979.9485 | 1260651.3922
26 | 2753969.6482 | 1260658.3424
27 | 2753981.0275 | 1260641.2323
28 | 2753993.4057 | 1260793.349
29 | 2754040.7622 | 1260749.8784
30 | 2754045.8589 | 1260748.7257
31 | 2754013.3801 | 1260640.7511
32 | 2754046.7901 | 1260640.2541
33 | 2753932.5441 | 1260631.6277
34 | 2754058.0431 | 1260640.147
35 | 2754047.735 | 1260660.1528
36 | 2754057.7155 | 1260630.4398
37 | 2754086.2474 | 1260609.9397
38 | 2754051.3169 | 1260630.5005
39 | 2754069.6308 | 1260640.0369
40 | 2754122.1057 | 1260629.4712
41 | 2754151.9873 | 1260629.3443
42 | 2754122.3483 | 1260639.5432
43 | 2754120.8799 | 1260614.9782
44 | 2754068.2116 | 1260603.8305
45 | 2753983.9454 | 1260631.1399
46 | 2754109.6322 | 1260639.6566
47 | 2754077.5386 | 1260639.9617
48 | 2754109.8321 | 1260653.6569
49 | 2754139.7403 | 1260634.4801
50 | 2754139.5936 | 1260618.2161
51 | 2754124.7617 | 1260639.5205
52 | 2754049.7605 | 1260681.6273
53 | 2754175.5227 | 1260628.8148
54 | 2754120.1407 | 1260606.2383
55 | 2754059.2488 | 1260581.7793
56 | 2754015.6181 | 1260557.3018
57 | 2754046.8522 | 1260545.571
58 | 2754111.1892 | 1260674.9172
59 | 2754202.8908 | 1260639.4083
60 | 2754203.7785 | 1260660.2828
61 | 2754194.173 | 1260638.8661
62 | 2754158.4532 | 1260639.2028
63 | 2754050.1583 | 1260684.825
64 | 2754184.8245 | 1260845.0837
65 | 2754207.2897 | 1260839.8817
66 | 2754175.827 | 1260708.3958
67 | 2754172.4662 | 1260709.1766
68 | 2754146.3476 | 1260715.0783
69 | 2754138.5666 | 1260712.4507
70 | 2754121.4681 | 1260716.3871
71 | 2754138.5699 | 1260701.6427
72 | 2754114.5561 | 1260694.9599
73 | 2754118.0817 | 1260723.3615
74 | 2754138.5709 | 1260698.5082
75 | 2754120.2249 | 1260729.657
76 | 2754101.121 | 1260736.1437
77 | 2754085.1433 | 1260739.7921
78 | 2754076.4972 | 1260741.7664
79 | 2754069.7524 | 1260743.3066
80 | 2754062.6489 | 1260744.9286
81 | 2754052.5122 | 1260702.8658
82 | 2754052.4033 | 1260702.4141
83 | 2754051.3983 | 1260694.7925
84 | 2754050.6401 | 1260688.6981
85 | 2754113.308 | 1260687.5298
86 | 2754112.2419 | 1260681.1839
87 | 2754181.634 | 1260638.9843
88 | 2754182.1053 | 1260638.9798
89 | 2754139.5715 | 1260688.9531
90 | 2754149.9358 | 1260684.8186
91 | 2754156.8949 | 1260683.6306
92 | 2754157.3946 | 1260683.5453
93 | 2754207.1002 | 1260682.1744
94 | 2754178.3696 | 1260628.7091
95 | 2754207.1584 | 1260682.4752
96 | 2754120.2249 | 1260729.657

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1