## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3231-12_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3231-12_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3231-12_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3231-12_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3231-12_0_6_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3231-12_0_6_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3231-12_0_6_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3231-12_0_6_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_3231-12_0_6_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_3231-12_0_6_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_3231-12_0_6_node_40 | 0.4 | n |  | TRUE
11 | bus_LV_3231-12_0_6_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_3231-12_0_6_node_38 | 0.4 | n |  | TRUE
13 | bus_LV_3231-12_0_6_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_3231-12_0_6_node_68 | 0.4 | n |  | TRUE
15 | bus_LV_3231-12_0_6_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_3231-12_0_6_node_69 | 0.4 | n |  | TRUE
17 | bus_LV_3231-12_0_6_node_21 | 0.4 | n |  | TRUE
18 | bus_LV_3231-12_0_6_node_10 | 0.4 | n |  | TRUE
19 | bus_LV_3231-12_0_6_node_11 | 0.4 | n |  | TRUE
20 | bus_LV_3231-12_0_6_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_3231-12_0_6_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_3231-12_0_6_node_37 | 0.4 | n |  | TRUE
23 | bus_LV_3231-12_0_6_node_39 | 0.4 | n |  | TRUE
24 | bus_LV_3231-12_0_6_node_41 | 0.4 | n |  | TRUE
25 | bus_LV_3231-12_0_6_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_3231-12_0_6_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_3231-12_0_6_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_3231-12_0_6_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_3231-12_0_6_node_24 | 0.4 | n |  | TRUE
30 | bus_LV_3231-12_0_6_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_3231-12_0_6_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_3231-12_0_6_node_57 | 0.4 | n |  | TRUE
33 | bus_LV_3231-12_0_6_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_3231-12_0_6_node_52 | 0.4 | n |  | TRUE
35 | bus_LV_3231-12_0_6_node_66 | 0.4 | n |  | TRUE
36 | bus_LV_3231-12_0_6_node_58 | 0.4 | n |  | TRUE
37 | bus_LV_3231-12_0_6_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_3231-12_0_6_node_59 | 0.4 | n |  | TRUE
39 | bus_LV_3231-12_0_6_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_3231-12_0_6_node_64 | 0.4 | n |  | TRUE
41 | bus_LV_3231-12_0_6_node_65 | 0.4 | n |  | TRUE
42 | bus_LV_3231-12_0_6_node_35 | 0.4 | n |  | TRUE
43 | bus_LV_3231-12_0_6_node_93 | 0.4 | n |  | TRUE
44 | bus_LV_3231-12_0_6_node_31 | 0.4 | n |  | TRUE
45 | bus_LV_3231-12_0_6_node_67 | 0.4 | n |  | TRUE
46 | bus_LV_3231-12_0_6_node_27 | 0.4 | n |  | TRUE
47 | bus_LV_3231-12_0_6_node_28 | 0.4 | n |  | TRUE
48 | bus_LV_3231-12_0_6_node_29 | 0.4 | n |  | TRUE
49 | bus_LV_3231-12_0_6_node_32 | 0.4 | n |  | TRUE
50 | bus_LV_3231-12_0_6_node_34 | 0.4 | n |  | TRUE
51 | bus_LV_3231-12_0_6_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_3231-12_0_6_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_3231-12_0_6_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_3231-12_0_6_node_62 | 0.4 | n |  | TRUE
55 | bus_LV_3231-12_0_6_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_3231-12_0_6_node_63 | 0.4 | n |  | TRUE
57 | bus_LV_3231-12_0_6_node_46 | 0.4 | n |  | TRUE
58 | bus_LV_3231-12_0_6_node_42 | 0.4 | n |  | TRUE
59 | bus_LV_3231-12_0_6_node_43 | 0.4 | n |  | TRUE
60 | bus_LV_3231-12_0_6_node_44 | 0.4 | n |  | TRUE
61 | bus_LV_3231-12_0_6_node_45 | 0.4 | n |  | TRUE
62 | bus_LV_3231-12_0_6_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_3231-12_0_6_node_48 | 0.4 | n |  | TRUE
64 | bus_LV_3231-12_0_6_node_88 | 0.4 | n |  | TRUE
65 | bus_LV_3231-12_0_6_node_86 | 0.4 | n |  | TRUE
66 | bus_LV_3231-12_0_6_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_3231-12_0_6_node_54 | 0.4 | n |  | TRUE
68 | bus_LV_3231-12_0_6_node_55 | 0.4 | n |  | TRUE
69 | bus_LV_3231-12_0_6_node_56 | 0.4 | n |  | TRUE
70 | bus_LV_3231-12_0_6_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_3231-12_0_6_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_3231-12_0_6_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_3231-12_0_6_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_3231-12_0_6_node_74 | 0.4 | n |  | TRUE
75 | bus_LV_3231-12_0_6_node_75 | 0.4 | n |  | TRUE
76 | bus_LV_3231-12_0_6_node_76 | 0.4 | n |  | TRUE
77 | bus_LV_3231-12_0_6_node_77 | 0.4 | n |  | TRUE
78 | bus_LV_3231-12_0_6_node_78 | 0.4 | n |  | TRUE
79 | bus_LV_3231-12_0_6_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_3231-12_0_6_node_89 | 0.4 | n |  | TRUE
81 | bus_LV_3231-12_0_6_node_87 | 0.4 | n |  | TRUE
82 | bus_LV_3231-12_0_6_node_90 | 0.4 | n |  | TRUE
83 | bus_LV_3231-12_0_6_node_85 | 0.4 | n |  | TRUE
84 | bus_LV_3231-12_0_6_node_80 | 0.4 | n |  | TRUE
85 | bus_LV_3231-12_0_6_node_81 | 0.4 | n |  | TRUE
86 | bus_LV_3231-12_0_6_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_3231-12_0_6_node_83 | 0.4 | n |  | TRUE
88 | bus_LV_3231-12_0_6_node_84 | 0.4 | n |  | TRUE
89 | bus_LV_3231-12_0_6_node_91 | 0.4 | n |  | TRUE
90 | bus_LV_3231-12_0_6_node_92 | 0.4 | n |  | TRUE
91 | bus_MV_236_0_node_8 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3231-12_0_6_load_0 | 0 | 0.014937 | 0.0037435 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3231-12_0_6_load_1 | 1 | 0.00045767 | 0.0001147 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3231-12_0_6_load_3 | 3 | 0.0033087 | 0.00082924 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3231-12_0_6_load_4 | 4 | 0.005755 | 0.0014423 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3231-12_0_6_load_6 | 6 | 0.0041134 | 0.0010309 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3231-12_0_6_load_7 | 7 | 0.0058555 | 0.0014675 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3231-12_0_6_load_16 | 8 | 0.016555 | 0.0041491 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3231-12_0_6_load_14 | 9 | 0.01785 | 0.0044737 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3231-12_0_6_load_40 | 10 | 0.003981 | 0.00099773 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3231-12_0_6_load_8 | 11 | 0.011158 | 0.0027964 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3231-12_0_6_load_68 | 14 | 0.0049723 | 0.0012462 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3231-12_0_6_load_26 | 15 | 0.0089055 | 0.0022319 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3231-12_0_6_load_69 | 16 | 0.0020337 | 0.0005097 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3231-12_0_6_load_10 | 18 | 0.0065011 | 0.0016293 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3231-12_0_6_load_12 | 20 | 0.0021952 | 0.00055018 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3231-12_0_6_load_37 | 22 | 0.0047645 | 0.0011941 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3231-12_0_6_load_39 | 23 | 0.0042824 | 0.0010733 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3231-12_0_6_load_41 | 24 | 0.00064088 | 0.00016062 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3231-12_0_6_load_17 | 25 | 0.014447 | 0.0036208 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3231-12_0_6_load_18 | 27 | 0.013491 | 0.0033811 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3231-12_0_6_load_24 | 29 | 0.0080132 | 0.0020083 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3231-12_0_6_load_57 | 32 | 0.021383 | 0.0053591 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3231-12_0_6_load_72 | 33 | 0.0083023 | 0.0020808 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3231-12_0_6_load_52 | 34 | 0.0082702 | 0.0020727 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3231-12_0_6_load_59 | 38 | 0.0014104 | 0.00035348 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3231-12_0_6_load_30 | 39 | 0.0021489 | 0.00053857 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3231-12_0_6_load_64 | 40 | 0.016042 | 0.0040205 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3231-12_0_6_load_93 | 43 | 0.0089274 | 0.0022374 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3231-12_0_6_load_67 | 45 | 0.016042 | 0.0040206 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3231-12_0_6_load_27 | 46 | 0.0034638 | 0.0008681 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3231-12_0_6_load_28 | 47 | 0.0017216 | 0.00043147 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3231-12_0_6_load_32 | 49 | 0.00079742 | 0.00019985 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3231-12_0_6_load_34 | 50 | 0.017657 | 0.0044254 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3231-12_0_6_load_36 | 51 | 0.0057171 | 0.0014328 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3231-12_0_6_load_62 | 54 | 0.0039691 | 0.00099474 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3231-12_0_6_load_49 | 55 | 0.0015962 | 0.00040004 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3231-12_0_6_load_63 | 56 | 0.0068022 | 0.0017048 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3231-12_0_6_load_46 | 57 | 0.001092 | 0.00027368 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3231-12_0_6_load_42 | 58 | 0.0018492 | 0.00046345 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3231-12_0_6_load_43 | 59 | 0.0040986 | 0.0010272 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3231-12_0_6_load_44 | 60 | 0.0015569 | 0.00039019 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3231-12_0_6_load_48 | 63 | 0.0021667 | 0.00054302 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3231-12_0_6_load_88 | 64 | 0.0028675 | 0.00071866 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3231-12_0_6_load_86 | 65 | 0.0014846 | 0.00037207 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3231-12_0_6_load_53 | 66 | 0.0030249 | 0.00075811 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3231-12_0_6_load_54 | 67 | 0.0027956 | 0.00070066 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3231-12_0_6_load_55 | 68 | 0.0028593 | 0.00071662 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3231-12_0_6_load_56 | 69 | 0.0015353 | 0.00038477 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3231-12_0_6_load_60 | 70 | 0.0013682 | 0.00034289 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3231-12_0_6_load_61 | 71 | 0.00092757 | 0.00023247 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3231-12_0_6_load_71 | 72 | 0.0013624 | 0.00034146 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3231-12_0_6_load_73 | 73 | 0.0016329 | 0.00040923 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3231-12_0_6_load_74 | 74 | 0.0016081 | 0.00040303 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3231-12_0_6_load_75 | 75 | 0.0013581 | 0.00034036 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3231-12_0_6_load_77 | 77 | 0.0019871 | 0.00049801 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3231-12_0_6_load_78 | 78 | 0.0019884 | 0.00049833 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3231-12_0_6_load_79 | 79 | 0.0019836 | 0.00049713 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3231-12_0_6_load_89 | 80 | 0.0018686 | 0.00046832 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3231-12_0_6_load_87 | 81 | 0.0028865 | 0.00072342 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3231-12_0_6_load_90 | 82 | 0.0013889 | 0.00034808 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3231-12_0_6_load_85 | 83 | 0.0016282 | 0.00040807 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3231-12_0_6_load_80 | 84 | 0.0018181 | 0.00045566 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3231-12_0_6_load_82 | 86 | 0.0012541 | 0.00031429 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3231-12_0_6_load_83 | 87 | 0.0014836 | 0.00037182 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3231-12_0_6_load_91 | 89 | 0.0021908 | 0.00054907 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3231-12_0_6_load_92 | 90 | 0.0015558 | 0.00038993 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3231-12_0_6_line_0 |  | 0 | 1 | 0.030273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
1 | LV_3231-12_0_6_line_1 |  | 0 | 2 | 0.035508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
2 | LV_3231-12_0_6_line_2 |  | 1 | 3 | 0.010075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
3 | LV_3231-12_0_6_line_3 |  | 2 | 4 | 0.025722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
4 | LV_3231-12_0_6_line_4 |  | 2 | 5 | 0.040106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3231-12_0_6_line_5 |  | 3 | 6 | 0.0097771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
6 | LV_3231-12_0_6_line_6 |  | 4 | 7 | 0.023154 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3231-12_0_6_line_7 |  | 5 | 8 | 0.034991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3231-12_0_6_line_8 |  | 5 | 9 | 0.0014072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3231-12_0_6_line_9 |  | 6 | 10 | 0.022012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
10 | LV_3231-12_0_6_line_10 |  | 7 | 11 | 0.027292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3231-12_0_6_line_11 |  | 10 | 12 | 0.015172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
12 | LV_3231-12_0_6_line_12 |  | 12 | 24 | 0.033463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
13 | LV_3231-12_0_6_line_13 |  | 12 | 21 | 0.051573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_3231-12_0_6_line_14 |  | 13 | 14 | 0.042773 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
15 | LV_3231-12_0_6_line_15 |  | 13 | 15 | 0.034581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
16 | LV_3231-12_0_6_line_16 |  | 14 | 16 | 0.03884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
17 | LV_3231-12_0_6_line_17 |  | 15 | 17 | 0.063048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
18 | LV_3231-12_0_6_line_18 |  | 16 | 62 | 0.048363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
19 | LV_3231-12_0_6_line_19 |  | 17 | 31 | 0.032412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
20 | LV_3231-12_0_6_line_20 |  | 17 | 26 | 0.013461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3231-12_0_6_line_21 |  | 18 | 19 | 0.032429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3231-12_0_6_line_22 |  | 19 | 20 | 0.028674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3231-12_0_6_line_23 |  | 20 | 21 | 0.053921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3231-12_0_6_line_24 |  | 21 | 22 | 0.016599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3231-12_0_6_line_25 |  | 22 | 23 | 0.0097502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3231-12_0_6_line_26 |  | 23 | 54 | 0.015624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3231-12_0_6_line_27 |  | 24 | 55 | 0.025333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
28 | LV_3231-12_0_6_line_28 |  | 25 | 26 | 0.019899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3231-12_0_6_line_29 |  | 27 | 28 | 0.050923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_3231-12_0_6_line_30 |  | 28 | 29 | 0.0043605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_3231-12_0_6_line_31 |  | 28 | 30 | 0.033972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
32 | LV_3231-12_0_6_line_32 |  | 29 | 33 | 0.046624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3231-12_0_6_line_33 |  | 30 | 34 | 0.015364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3231-12_0_6_line_34 |  | 30 | 35 | 0.039588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
35 | LV_3231-12_0_6_line_35 |  | 31 | 32 | 0.02868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
36 | LV_3231-12_0_6_line_36 |  | 32 | 36 | 0.030239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
37 | LV_3231-12_0_6_line_37 |  | 35 | 45 | 0.003706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3231-12_0_6_line_38 |  | 35 | 41 | 0.007123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
39 | LV_3231-12_0_6_line_39 |  | 36 | 70 | 0.014928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_3231-12_0_6_line_40 |  | 36 | 38 | 0.035488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
41 | LV_3231-12_0_6_line_41 |  | 37 | 38 | 0.0080912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
42 | LV_3231-12_0_6_line_42 |  | 37 | 39 | 0.02105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
43 | LV_3231-12_0_6_line_43 |  | 39 | 47 | 0.006899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
44 | LV_3231-12_0_6_line_44 |  | 40 | 41 | 0.039901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3231-12_0_6_line_45 |  | 41 | 42 | 0.014196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
46 | LV_3231-12_0_6_line_46 |  | 42 | 43 | 0.024945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3231-12_0_6_line_47 |  | 42 | 44 | 0.017266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
48 | LV_3231-12_0_6_line_48 |  | 44 | 50 | 0.02133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3231-12_0_6_line_49 |  | 44 | 48 | 0.025334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
50 | LV_3231-12_0_6_line_50 |  | 46 | 47 | 0.020635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
51 | LV_3231-12_0_6_line_51 |  | 46 | 48 | 0.017768 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
52 | LV_3231-12_0_6_line_52 |  | 48 | 49 | 0.0035432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
53 | LV_3231-12_0_6_line_53 |  | 49 | 51 | 0.018877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
54 | LV_3231-12_0_6_line_54 |  | 51 | 52 | 0.032431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_3231-12_0_6_line_55 |  | 52 | 53 | 0.050556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3231-12_0_6_line_56 |  | 53 | 66 | 0.026482 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3231-12_0_6_line_57 |  | 54 | 56 | 0.0078941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3231-12_0_6_line_58 |  | 55 | 57 | 0.0087057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
59 | LV_3231-12_0_6_line_59 |  | 57 | 60 | 0.018041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
60 | LV_3231-12_0_6_line_60 |  | 58 | 59 | 0.00501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
61 | LV_3231-12_0_6_line_61 |  | 58 | 60 | 0.018233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
62 | LV_3231-12_0_6_line_62 |  | 59 | 61 | 0.017035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
63 | LV_3231-12_0_6_line_63 |  | 61 | 62 | 0.005304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
64 | LV_3231-12_0_6_line_64 |  | 61 | 63 | 0.041304 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
65 | LV_3231-12_0_6_line_65 |  | 63 | 64 | 0.016379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
66 | LV_3231-12_0_6_line_66 |  | 64 | 65 | 0.027963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
67 | LV_3231-12_0_6_line_67 |  | 65 | 88 | 0.012517 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
68 | LV_3231-12_0_6_line_68 |  | 66 | 67 | 0.024063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3231-12_0_6_line_69 |  | 67 | 68 | 0.023048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3231-12_0_6_line_70 |  | 68 | 69 | 0.045414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3231-12_0_6_line_71 |  | 70 | 71 | 0.051527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3231-12_0_6_line_72 |  | 71 | 72 | 3.2927e-06 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3231-12_0_6_line_73 |  | 73 | 74 | 0.0037299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3231-12_0_6_line_74 |  | 73 | 75 | 0.023143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3231-12_0_6_line_75 |  | 74 | 76 | 0.01903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3231-12_0_6_line_76 |  | 75 | 77 | 0.0065467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3231-12_0_6_line_77 |  | 76 | 78 | 0.01403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3231-12_0_6_line_78 |  | 76 | 79 | 0.019205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_3231-12_0_6_line_79 |  | 78 | 80 | 0.026251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3231-12_0_6_line_80 |  | 79 | 81 | 0.013939 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_3231-12_0_6_line_81 |  | 80 | 82 | 0.002184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3231-12_0_6_line_82 |  | 81 | 83 | 0.013069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
83 | LV_3231-12_0_6_line_83 |  | 82 | 89 | 0.017884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3231-12_0_6_line_84 |  | 83 | 88 | 0.015475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
85 | LV_3231-12_0_6_line_85 |  | 84 | 85 | 0.021095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3231-12_0_6_line_86 |  | 85 | 86 | 0.028548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3231-12_0_6_line_87 |  | 86 | 87 | 0.021857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
88 | LV_3231-12_0_6_line_88 |  | 87 | 88 | 0.037952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 5 | cs | TRUE
89 | LV_3231-12_0_6_line_89 |  | 89 | 90 | 0.0089725 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3231-12_0_6_trafo_4 | 0.63 MVA 20/0.4 kV | 91 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2765495.9245 | 1254396.3209 | 2765489.7648 | 1254396.0762 | 2765467.9051 | 1254406.2428 | 2765467.9051 | 1254406.2428
1 | 2765531.4049 | 1254397.7304 | 2765495.9245 | 1254396.3209
2 | 2765457.8324 | 1254406.0496 | 2765467.9051 | 1254406.2428
3 | 2765531.4049 | 1254397.7304 | 2765530.7102 | 1254423.4426
4 | 2765532.4887 | 1254357.641 | 2765531.4645 | 1254389.935 | 2765531.4049 | 1254397.7304
5 | 2765457.8324 | 1254406.0496 | 2765448.0571 | 1254405.8621
6 | 2765530.7102 | 1254423.4426 | 2765530.3361 | 1254437.2863 | 2765530.487 | 1254446.5908
7 | 2765532.4887 | 1254357.641 | 2765497.7239 | 1254353.6688
8 | 2765532.4887 | 1254357.641 | 2765532.5303 | 1254356.2343
9 | 2765448.0571 | 1254405.8621 | 2765426.0489 | 1254405.4399
10 | 2765531.7904 | 1254473.8422 | 2765531.5803 | 1254472.1464 | 2765530.6132 | 1254454.3674 | 2765530.487 | 1254446.5908
11 | 2765410.8794 | 1254405.149 | 2765426.0489 | 1254405.4399
12 | 2765410.8794 | 1254405.149 | 2765410.2591 | 1254438.6062
13 | 2765411.9734 | 1254353.5923 | 2765410.8794 | 1254405.149
14 | 2765543.7035 | 1254531.2581 | 2765506.7851 | 1254532.7502 | 2765500.9613 | 1254532.8066
15 | 2765543.7035 | 1254531.2581 | 2765578.2115 | 1254529.0169
16 | 2765500.9613 | 1254532.8066 | 2765476.3545 | 1254533.0447 | 2765462.1303 | 1254532.5889
17 | 2765641.1265 | 1254524.9306 | 2765578.2115 | 1254529.0169
18 | 2765413.792 | 1254531.0396 | 2765462.1303 | 1254532.5889
19 | 2765673.5994 | 1254523.415 | 2765641.1265 | 1254524.9306
20 | 2765640.0981 | 1254511.5101 | 2765641.1265 | 1254524.9306
21 | 2765413.1572 | 1254271.0058 | 2765445.5827 | 1254271.5008
22 | 2765413.1572 | 1254271.0058 | 2765412.7462 | 1254299.6767
23 | 2765411.9734 | 1254353.5923 | 2765412.7462 | 1254299.6767
24 | 2765411.9734 | 1254353.5923 | 2765428.5618 | 1254354.1837
25 | 2765438.3058 | 1254354.531 | 2765428.5618 | 1254354.1837
26 | 2765438.3058 | 1254354.531 | 2765453.9202 | 1254355.0876
27 | 2765410.2591 | 1254438.6062 | 2765410.24 | 1254439.6338 | 2765409.7931 | 1254463.935
28 | 2765640.0981 | 1254511.5101 | 2765638.5772 | 1254491.6691
29 | 2765635.9465 | 1254390.4118 | 2765638.09 | 1254412.2723 | 2765638.589 | 1254434.0869 | 2765634.3527 | 1254436.5599 | 2765634.5233 | 1254438.7852
30 | 2765635.9465 | 1254390.4118 | 2765635.2912 | 1254386.1008
31 | 2765666.6987 | 1254382.4301 | 2765640.7248 | 1254383.9497 | 2765635.9465 | 1254390.4118
32 | 2765629.8279 | 1254339.8433 | 2765630.8272 | 1254356.7334 | 2765635.2912 | 1254386.1008
33 | 2765666.6987 | 1254382.4301 | 2765672.2484 | 1254368.1036
34 | 2765666.6987 | 1254382.4301 | 2765673.6678 | 1254389.399 | 2765672.1237 | 1254398.7099 | 2765672.0935 | 1254413.0018 | 2765668.8271 | 1254418.038
35 | 2765673.5994 | 1254523.415 | 2765702.2479 | 1254522.0678
36 | 2765732.4534 | 1254520.6474 | 2765702.2479 | 1254522.0678
37 | 2765668.8271 | 1254418.038 | 2765665.1692 | 1254417.3794
38 | 2765668.8271 | 1254418.038 | 2765673.8256 | 1254423.1275
39 | 2765732.4534 | 1254520.6474 | 2765747.3812 | 1254520.771
40 | 2765732.4534 | 1254520.6474 | 2765730.9629 | 1254485.1903
41 | 2765730.6231 | 1254477.1062 | 2765730.9629 | 1254485.1903
42 | 2765730.6231 | 1254477.1062 | 2765729.4587 | 1254456.0888
43 | 2765729.0771 | 1254449.2004 | 2765729.4587 | 1254456.0888
44 | 2765673.8256 | 1254423.1275 | 2765671.4581 | 1254435.6967 | 2765675.7521 | 1254446.2612 | 2765674.9964 | 1254453.5699 | 2765669.675 | 1254460.0167
45 | 2765673.8256 | 1254423.1275 | 2765678.9686 | 1254416.8537 | 2765685.041 | 1254416.4787
46 | 2765685.041 | 1254416.4787 | 2765684.0224 | 1254426.7054 | 2765687.3125 | 1254433.7603 | 2765693.4761 | 1254436.8693
47 | 2765685.041 | 1254416.4787 | 2765701.5462 | 1254411.2572
48 | 2765696.9607 | 1254391.1523 | 2765696.9867 | 1254403.4326 | 2765701.5462 | 1254411.2572
49 | 2765726.9527 | 1254410.8564 | 2765701.5462 | 1254411.2572
50 | 2765729.0771 | 1254449.2004 | 2765727.9356 | 1254428.5968
51 | 2765726.9527 | 1254410.8564 | 2765727.9356 | 1254428.5968
52 | 2765726.9527 | 1254410.8564 | 2765726.8861 | 1254407.3139
53 | 2765726.5314 | 1254388.4398 | 2765726.8861 | 1254407.3139
54 | 2765725.922 | 1254356.0147 | 2765726.5314 | 1254388.4398
55 | 2765725.922 | 1254356.0147 | 2765725.2685 | 1254321.1266 | 2765720.7066 | 1254309.3422 | 2765719.585 | 1254306.5301
56 | 2765719.585 | 1254306.5301 | 2765693.1208 | 1254307.5119
57 | 2765455.0746 | 1254347.2784 | 2765453.9202 | 1254355.0876 | 2765453.9202 | 1254355.0876
58 | 2765409.7931 | 1254463.935 | 2765409.633 | 1254472.6392
59 | 2765409.3013 | 1254490.677 | 2765409.633 | 1254472.6392
60 | 2765408.8739 | 1254513.916 | 2765408.966 | 1254508.9068
61 | 2765409.3013 | 1254490.677 | 2765408.966 | 1254508.9068
62 | 2765408.4725 | 1254530.9465 | 2765408.7301 | 1254521.733 | 2765408.8739 | 1254513.916
63 | 2765413.792 | 1254531.0396 | 2765408.4725 | 1254530.9465
64 | 2765408.4725 | 1254530.9465 | 2765395.6726 | 1254530.5665 | 2765367.1744 | 1254530.5961
65 | 2765350.8025 | 1254530.8271 | 2765354.2351 | 1254530.6096 | 2765367.1744 | 1254530.5961
66 | 2765322.8957 | 1254531.7314 | 2765329.6273 | 1254532.1688 | 2765350.8025 | 1254530.8271
67 | 2765310.4048 | 1254530.9198 | 2765322.8957 | 1254531.7314
68 | 2765693.1208 | 1254307.5119 | 2765669.0745 | 1254308.4041
69 | 2765646.0421 | 1254309.2586 | 2765669.0745 | 1254308.4041
70 | 2765646.0421 | 1254309.2586 | 2765600.6598 | 1254310.9424
71 | 2765769.4115 | 1254496.2696 | 2765773.3036 | 1254500.614 | 2765776.1292 | 1254509.1576 | 2765776.4266 | 1254515.517 | 2765770.891 | 1254519.3662 | 2765756.6876 | 1254520.848 | 2765747.3812 | 1254520.771
72 | 2765769.4093 | 1254496.2672 | 2765769.4115 | 1254496.2696
73 | 2765334.1793 | 1254469.7854 | 2765330.4505 | 1254469.6959
74 | 2765334.1793 | 1254469.7854 | 2765357.3151 | 1254470.3405
75 | 2765311.426 | 1254469.2395 | 2765330.4505 | 1254469.6959
76 | 2765357.3151 | 1254470.3405 | 2765363.86 | 1254470.4975
77 | 2765311.426 | 1254469.2395 | 2765297.3956 | 1254469.2639
78 | 2765311.426 | 1254469.2395 | 2765311.108 | 1254488.442
79 | 2765271.1446 | 1254469.3096 | 2765297.3956 | 1254469.2639
80 | 2765311.108 | 1254488.442 | 2765310.8773 | 1254502.3791
81 | 2765268.9605 | 1254469.3134 | 2765271.1446 | 1254469.3096
82 | 2765310.661 | 1254515.4467 | 2765310.8773 | 1254502.3791
83 | 2765268.9605 | 1254469.3134 | 2765251.0761 | 1254469.3445
84 | 2765310.4048 | 1254530.9198 | 2765310.661 | 1254515.4467
85 | 2765222.6036 | 1254539.2788 | 2765219.1436 | 1254518.4692
86 | 2765222.6036 | 1254539.2788 | 2765244.8466 | 1254535.0838 | 2765250.734 | 1254534.5369
87 | 2765250.734 | 1254534.5369 | 2765269.0585 | 1254532.8347 | 2765272.5051 | 1254532.6225
88 | 2765310.4048 | 1254530.9198 | 2765300.2441 | 1254530.914 | 2765272.5051 | 1254532.6225
89 | 2765251.0761 | 1254469.3445 | 2765251.0761 | 1254469.3445 | 2765251.0825 | 1254460.372

## bus_geodata
| x | y | coords
0 | 2765495.9245 | 1254396.3209
1 | 2765467.9051 | 1254406.2428
2 | 2765531.4049 | 1254397.7304
3 | 2765457.8324 | 1254406.0496
4 | 2765530.7102 | 1254423.4426
5 | 2765532.4887 | 1254357.641
6 | 2765448.0571 | 1254405.8621
7 | 2765530.487 | 1254446.5908
8 | 2765497.7239 | 1254353.6688
9 | 2765532.5303 | 1254356.2343
10 | 2765426.0489 | 1254405.4399
11 | 2765531.7904 | 1254473.8422
12 | 2765410.8794 | 1254405.149
13 | 2765543.7035 | 1254531.2581
14 | 2765500.9613 | 1254532.8066
15 | 2765578.2115 | 1254529.0169
16 | 2765462.1303 | 1254532.5889
17 | 2765641.1265 | 1254524.9306
18 | 2765445.5827 | 1254271.5008
19 | 2765413.1572 | 1254271.0058
20 | 2765412.7462 | 1254299.6767
21 | 2765411.9734 | 1254353.5923
22 | 2765428.5618 | 1254354.1837
23 | 2765438.3058 | 1254354.531
24 | 2765410.2591 | 1254438.6062
25 | 2765638.5772 | 1254491.6691
26 | 2765640.0981 | 1254511.5101
27 | 2765634.5233 | 1254438.7852
28 | 2765635.9465 | 1254390.4118
29 | 2765635.2912 | 1254386.1008
30 | 2765666.6987 | 1254382.4301
31 | 2765673.5994 | 1254523.415
32 | 2765702.2479 | 1254522.0678
33 | 2765629.8279 | 1254339.8433
34 | 2765672.2484 | 1254368.1036
35 | 2765668.8271 | 1254418.038
36 | 2765732.4534 | 1254520.6474
37 | 2765730.6231 | 1254477.1062
38 | 2765730.9629 | 1254485.1903
39 | 2765729.4587 | 1254456.0888
40 | 2765669.675 | 1254460.0167
41 | 2765673.8256 | 1254423.1275
42 | 2765685.041 | 1254416.4787
43 | 2765693.4761 | 1254436.8693
44 | 2765701.5462 | 1254411.2572
45 | 2765665.1692 | 1254417.3794
46 | 2765727.9356 | 1254428.5968
47 | 2765729.0771 | 1254449.2004
48 | 2765726.9527 | 1254410.8564
49 | 2765726.8861 | 1254407.3139
50 | 2765696.9607 | 1254391.1523
51 | 2765726.5314 | 1254388.4398
52 | 2765725.922 | 1254356.0147
53 | 2765719.585 | 1254306.5301
54 | 2765453.9202 | 1254355.0876
55 | 2765409.7931 | 1254463.935
56 | 2765455.0746 | 1254347.2784
57 | 2765409.633 | 1254472.6392
58 | 2765408.966 | 1254508.9068
59 | 2765408.8739 | 1254513.916
60 | 2765409.3013 | 1254490.677
61 | 2765408.4725 | 1254530.9465
62 | 2765413.792 | 1254531.0396
63 | 2765367.1744 | 1254530.5961
64 | 2765350.8025 | 1254530.8271
65 | 2765322.8957 | 1254531.7314
66 | 2765693.1208 | 1254307.5119
67 | 2765669.0745 | 1254308.4041
68 | 2765646.0421 | 1254309.2586
69 | 2765600.6598 | 1254310.9424
70 | 2765747.3812 | 1254520.771
71 | 2765769.4115 | 1254496.2696
72 | 2765769.4093 | 1254496.2672
73 | 2765334.1793 | 1254469.7854
74 | 2765330.4505 | 1254469.6959
75 | 2765357.3151 | 1254470.3405
76 | 2765311.426 | 1254469.2395
77 | 2765363.86 | 1254470.4975
78 | 2765297.3956 | 1254469.2639
79 | 2765311.108 | 1254488.442
80 | 2765271.1446 | 1254469.3096
81 | 2765310.8773 | 1254502.3791
82 | 2765268.9605 | 1254469.3134
83 | 2765310.661 | 1254515.4467
84 | 2765219.1436 | 1254518.4692
85 | 2765222.6036 | 1254539.2788
86 | 2765250.734 | 1254534.5369
87 | 2765272.5051 | 1254532.6225
88 | 2765310.4048 | 1254530.9198
89 | 2765251.0761 | 1254469.3445
90 | 2765251.0825 | 1254460.372
91 | 2765531.4049 | 1254397.7304

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1