## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3236-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3236-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3236-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3236-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3236-3_0_4_node_8 | 0.4 | n |  | TRUE
5 | bus_LV_3236-3_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_3236-3_0_4_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_3236-3_0_4_node_17 | 0.4 | n |  | TRUE
8 | bus_LV_3236-3_0_4_node_9 | 0.4 | n |  | TRUE
9 | bus_LV_3236-3_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_3236-3_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_3236-3_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_3236-3_0_4_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_3236-3_0_4_node_82 | 0.4 | n |  | TRUE
14 | bus_LV_3236-3_0_4_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_3236-3_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_3236-3_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_3236-3_0_4_node_65 | 0.4 | n |  | TRUE
18 | bus_LV_3236-3_0_4_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_3236-3_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_3236-3_0_4_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_3236-3_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_3236-3_0_4_node_83 | 0.4 | n |  | TRUE
23 | bus_LV_3236-3_0_4_node_80 | 0.4 | n |  | TRUE
24 | bus_LV_3236-3_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_3236-3_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_3236-3_0_4_node_84 | 0.4 | n |  | TRUE
27 | bus_LV_3236-3_0_4_node_78 | 0.4 | n |  | TRUE
28 | bus_LV_3236-3_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_3236-3_0_4_node_19 | 0.4 | n |  | TRUE
30 | bus_LV_3236-3_0_4_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_3236-3_0_4_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_3236-3_0_4_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_3236-3_0_4_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_3236-3_0_4_node_77 | 0.4 | n |  | TRUE
35 | bus_LV_3236-3_0_4_node_79 | 0.4 | n |  | TRUE
36 | bus_LV_3236-3_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_3236-3_0_4_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_3236-3_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_3236-3_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_3236-3_0_4_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_3236-3_0_4_node_32 | 0.4 | n |  | TRUE
42 | bus_LV_3236-3_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_3236-3_0_4_node_39 | 0.4 | n |  | TRUE
44 | bus_LV_3236-3_0_4_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_3236-3_0_4_node_93 | 0.4 | n |  | TRUE
46 | bus_LV_3236-3_0_4_node_35 | 0.4 | n |  | TRUE
47 | bus_LV_3236-3_0_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_3236-3_0_4_node_37 | 0.4 | n |  | TRUE
49 | bus_LV_3236-3_0_4_node_92 | 0.4 | n |  | TRUE
50 | bus_LV_3236-3_0_4_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_3236-3_0_4_node_36 | 0.4 | n |  | TRUE
52 | bus_LV_3236-3_0_4_node_38 | 0.4 | n |  | TRUE
53 | bus_LV_3236-3_0_4_node_40 | 0.4 | n |  | TRUE
54 | bus_LV_3236-3_0_4_node_70 | 0.4 | n |  | TRUE
55 | bus_LV_3236-3_0_4_node_71 | 0.4 | n |  | TRUE
56 | bus_LV_3236-3_0_4_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_3236-3_0_4_node_85 | 0.4 | n |  | TRUE
58 | bus_LV_3236-3_0_4_node_91 | 0.4 | n |  | TRUE
59 | bus_LV_3236-3_0_4_node_86 | 0.4 | n |  | TRUE
60 | bus_LV_3236-3_0_4_node_45 | 0.4 | n |  | TRUE
61 | bus_LV_3236-3_0_4_node_46 | 0.4 | n |  | TRUE
62 | bus_LV_3236-3_0_4_node_47 | 0.4 | n |  | TRUE
63 | bus_LV_3236-3_0_4_node_49 | 0.4 | n |  | TRUE
64 | bus_LV_3236-3_0_4_node_90 | 0.4 | n |  | TRUE
65 | bus_LV_3236-3_0_4_node_89 | 0.4 | n |  | TRUE
66 | bus_LV_3236-3_0_4_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_3236-3_0_4_node_52 | 0.4 | n |  | TRUE
68 | bus_LV_3236-3_0_4_node_53 | 0.4 | n |  | TRUE
69 | bus_LV_3236-3_0_4_node_54 | 0.4 | n |  | TRUE
70 | bus_LV_3236-3_0_4_node_55 | 0.4 | n |  | TRUE
71 | bus_LV_3236-3_0_4_node_74 | 0.4 | n |  | TRUE
72 | bus_LV_3236-3_0_4_node_56 | 0.4 | n |  | TRUE
73 | bus_LV_3236-3_0_4_node_73 | 0.4 | n |  | TRUE
74 | bus_LV_3236-3_0_4_node_57 | 0.4 | n |  | TRUE
75 | bus_LV_3236-3_0_4_node_58 | 0.4 | n |  | TRUE
76 | bus_LV_3236-3_0_4_node_62 | 0.4 | n |  | TRUE
77 | bus_LV_3236-3_0_4_node_60 | 0.4 | n |  | TRUE
78 | bus_LV_3236-3_0_4_node_59 | 0.4 | n |  | TRUE
79 | bus_LV_3236-3_0_4_node_61 | 0.4 | n |  | TRUE
80 | bus_LV_3236-3_0_4_node_63 | 0.4 | n |  | TRUE
81 | bus_LV_3236-3_0_4_node_64 | 0.4 | n |  | TRUE
82 | bus_LV_3236-3_0_4_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_3236-3_0_4_node_81 | 0.4 | n |  | TRUE
84 | bus_LV_3236-3_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_3236-3_0_4_node_67 | 0.4 | n |  | TRUE
86 | bus_LV_3236-3_0_4_node_68 | 0.4 | n |  | TRUE
87 | bus_LV_3236-3_0_4_node_69 | 0.4 | n |  | TRUE
88 | bus_LV_3236-3_0_4_node_72 | 0.4 | n |  | TRUE
89 | bus_LV_3236-3_0_4_node_87 | 0.4 | n |  | TRUE
90 | bus_LV_3236-3_0_4_node_88 | 0.4 | n |  | TRUE
91 | bus_MV_46_0_node_174 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3236-3_0_4_load_0 | 0 | 0.022999 | 0.0057641 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3236-3_0_4_load_1 | 1 | 0.014085 | 0.0035301 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3236-3_0_4_load_2 | 2 | 0.018602 | 0.0046622 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3236-3_0_4_load_3 | 3 | 0.0094593 | 0.0023707 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3236-3_0_4_load_16 | 10 | 0.0043365 | 0.0010868 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3236-3_0_4_load_11 | 11 | 0.0023648 | 0.00059268 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3236-3_0_4_load_82 | 13 | 0.0052171 | 0.0013075 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3236-3_0_4_load_5 | 14 | 0.016444 | 0.0041211 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3236-3_0_4_load_10 | 16 | 0.012824 | 0.003214 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3236-3_0_4_load_65 | 17 | 0.0016252 | 0.00040731 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3236-3_0_4_load_66 | 18 | 0.0022675 | 0.00056828 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3236-3_0_4_load_15 | 21 | 0.0049786 | 0.0012478 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3236-3_0_4_load_83 | 22 | 0.0040774 | 0.0010219 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3236-3_0_4_load_80 | 23 | 0.0021374 | 0.00053569 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3236-3_0_4_load_24 | 24 | 0.0014536 | 0.0003643 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3236-3_0_4_load_18 | 25 | 0.0018652 | 0.00046746 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3236-3_0_4_load_84 | 26 | 0.0016582 | 0.00041559 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3236-3_0_4_load_22 | 28 | 0.0037145 | 0.00093094 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3236-3_0_4_load_19 | 29 | 0.0037548 | 0.00094105 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3236-3_0_4_load_27 | 30 | 0.0051638 | 0.0012942 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3236-3_0_4_load_20 | 31 | 0.0012223 | 0.00030634 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3236-3_0_4_load_21 | 32 | 0.0024519 | 0.0006145 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3236-3_0_4_load_23 | 33 | 0.0021509 | 0.00053906 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3236-3_0_4_load_79 | 35 | 0.0030882 | 0.00077397 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3236-3_0_4_load_25 | 36 | 0.0013299 | 0.0003333 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3236-3_0_4_load_29 | 38 | 0.018984 | 0.0047579 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3236-3_0_4_load_30 | 39 | 0.0064028 | 0.0016047 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3236-3_0_4_load_32 | 41 | 0.011219 | 0.0028117 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3236-3_0_4_load_39 | 43 | 0.0052569 | 0.0013175 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3236-3_0_4_load_93 | 45 | 0.0030248 | 0.00075808 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3236-3_0_4_load_41 | 47 | 0.0029257 | 0.00073326 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3236-3_0_4_load_37 | 48 | 0.0060893 | 0.0015261 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3236-3_0_4_load_92 | 49 | 0.0019014 | 0.00047653 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3236-3_0_4_load_36 | 51 | 0.02172 | 0.0054437 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3236-3_0_4_load_38 | 52 | 0.0021022 | 0.00052686 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3236-3_0_4_load_40 | 53 | 0.001991 | 0.000499 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3236-3_0_4_load_70 | 54 | 0.027499 | 0.006892 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3236-3_0_4_load_71 | 55 | 0.0053074 | 0.0013302 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3236-3_0_4_load_44 | 56 | 0.0043972 | 0.001102 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3236-3_0_4_load_85 | 57 | 0.0042221 | 0.0010581 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3236-3_0_4_load_91 | 58 | 0.010872 | 0.0027249 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3236-3_0_4_load_86 | 59 | 0.0047992 | 0.0012028 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3236-3_0_4_load_45 | 60 | 0.012861 | 0.0032233 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3236-3_0_4_load_46 | 61 | 0.016683 | 0.0041812 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3236-3_0_4_load_47 | 62 | 0.0050391 | 0.0012629 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3236-3_0_4_load_49 | 63 | 0.0045331 | 0.0011361 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3236-3_0_4_load_90 | 64 | 0.0041908 | 0.0010503 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3236-3_0_4_load_89 | 65 | 0.004382 | 0.0010982 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3236-3_0_4_load_50 | 66 | 0.024517 | 0.0061445 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3236-3_0_4_load_53 | 68 | 0.0014653 | 0.00036724 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3236-3_0_4_load_54 | 69 | 0.0012904 | 0.0003234 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3236-3_0_4_load_55 | 70 | 0.0045737 | 0.0011463 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3236-3_0_4_load_74 | 71 | 0.00169 | 0.00042355 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3236-3_0_4_load_73 | 73 | 0.016884 | 0.0042315 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3236-3_0_4_load_57 | 74 | 0.0056964 | 0.0014276 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3236-3_0_4_load_58 | 75 | 0.0025031 | 0.00062734 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3236-3_0_4_load_62 | 76 | 0.0024054 | 0.00060284 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3236-3_0_4_load_60 | 77 | 0.0026422 | 0.00066221 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3236-3_0_4_load_59 | 78 | 0.0063562 | 0.001593 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3236-3_0_4_load_63 | 80 | 0.0026765 | 0.0006708 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3236-3_0_4_load_64 | 81 | 0.0015375 | 0.00038532 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3236-3_0_4_load_75 | 82 | 0.0039542 | 0.00099101 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3236-3_0_4_load_81 | 83 | 0.0034579 | 0.00086662 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3236-3_0_4_load_76 | 84 | 0.0047062 | 0.0011795 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3236-3_0_4_load_67 | 85 | 0.0032089 | 0.00080423 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3236-3_0_4_load_68 | 86 | 0.0033152 | 0.00083087 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3236-3_0_4_load_69 | 87 | 0.0032984 | 0.00082667 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3236-3_0_4_load_72 | 88 | 0.0014799 | 0.00037089 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3236-3_0_4_load_87 | 89 | 0.0044694 | 0.0011201 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3236-3_0_4_load_88 | 90 | 0.0044987 | 0.0011275 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 84 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3236-3_0_4_line_0 |  | 0 | 1 | 0.053761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3236-3_0_4_line_1 |  | 0 | 2 | 0.051188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3236-3_0_4_line_2 |  | 1 | 3 | 0.038173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3236-3_0_4_line_3 |  | 3 | 4 | 0.13003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3236-3_0_4_line_4 |  | 4 | 8 | 0.01025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3236-3_0_4_line_5 |  | 4 | 9 | 0.094425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3236-3_0_4_line_6 |  | 5 | 6 | 0.07414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3236-3_0_4_line_7 |  | 5 | 7 | 0.037577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3236-3_0_4_line_8 |  | 6 | 10 | 0.018038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3236-3_0_4_line_9 |  | 6 | 11 | 0.041022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3236-3_0_4_line_10 |  | 7 | 12 | 0.021147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3236-3_0_4_line_11 |  | 7 | 13 | 0.05353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3236-3_0_4_line_12 |  | 8 | 17 | 0.080859 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3236-3_0_4_line_13 |  | 9 | 14 | 0.053033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3236-3_0_4_line_14 |  | 10 | 25 | 0.022217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3236-3_0_4_line_15 |  | 11 | 19 | 0.027241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3236-3_0_4_line_16 |  | 12 | 30 | 0.031616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3236-3_0_4_line_17 |  | 14 | 15 | 0.028565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3236-3_0_4_line_18 |  | 15 | 16 | 0.020544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3236-3_0_4_line_19 |  | 17 | 18 | 0.018431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
20 | LV_3236-3_0_4_line_20 |  | 18 | 85 | 0.01855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_3236-3_0_4_line_21 |  | 19 | 20 | 0.057036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3236-3_0_4_line_22 |  | 19 | 21 | 0.023813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3236-3_0_4_line_23 |  | 20 | 22 | 0.013081 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3236-3_0_4_line_24 |  | 20 | 23 | 0.022699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3236-3_0_4_line_25 |  | 21 | 24 | 0.020002 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3236-3_0_4_line_26 |  | 22 | 26 | 0.021293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3236-3_0_4_line_27 |  | 23 | 27 | 0.021734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3236-3_0_4_line_28 |  | 24 | 28 | 0.014637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3236-3_0_4_line_29 |  | 25 | 29 | 0.017114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3236-3_0_4_line_30 |  | 27 | 83 | 0.025334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
31 | LV_3236-3_0_4_line_31 |  | 27 | 87 | 0.014574 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_3236-3_0_4_line_32 |  | 28 | 31 | 0.0092801 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3236-3_0_4_line_33 |  | 30 | 37 | 0.016462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3236-3_0_4_line_34 |  | 31 | 32 | 0.026142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3236-3_0_4_line_35 |  | 32 | 33 | 0.027682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3236-3_0_4_line_36 |  | 33 | 34 | 0.0096764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3236-3_0_4_line_37 |  | 34 | 35 | 0.021244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3236-3_0_4_line_38 |  | 36 | 37 | 0.025739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3236-3_0_4_line_39 |  | 38 | 39 | 0.048274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_3236-3_0_4_line_40 |  | 38 | 40 | 0.033845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_3236-3_0_4_line_41 |  | 39 | 41 | 0.0011448 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_3236-3_0_4_line_42 |  | 40 | 42 | 0.05802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_3236-3_0_4_line_43 |  | 41 | 43 | 0.013097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_3236-3_0_4_line_44 |  | 42 | 44 | 0.01716 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_3236-3_0_4_line_45 |  | 42 | 45 | 0.023961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3236-3_0_4_line_46 |  | 43 | 48 | 0.0091293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_3236-3_0_4_line_47 |  | 44 | 49 | 0.028101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3236-3_0_4_line_48 |  | 44 | 46 | 0.004316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_3236-3_0_4_line_49 |  | 46 | 47 | 0.010933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_3236-3_0_4_line_50 |  | 47 | 50 | 0.0018162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_3236-3_0_4_line_51 |  | 48 | 51 | 0.013991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_3236-3_0_4_line_52 |  | 49 | 58 | 0.01265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3236-3_0_4_line_53 |  | 50 | 56 | 0.022815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
54 | LV_3236-3_0_4_line_54 |  | 51 | 52 | 0.0073094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_3236-3_0_4_line_55 |  | 52 | 53 | 0.021083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_3236-3_0_4_line_56 |  | 53 | 54 | 0.013161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
57 | LV_3236-3_0_4_line_57 |  | 54 | 55 | 0.010885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_3236-3_0_4_line_58 |  | 55 | 88 | 0.024194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_3236-3_0_4_line_59 |  | 56 | 57 | 0.0050278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3236-3_0_4_line_60 |  | 57 | 59 | 0.0053234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3236-3_0_4_line_61 |  | 59 | 89 | 0.0054709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3236-3_0_4_line_62 |  | 60 | 61 | 0.022264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3236-3_0_4_line_63 |  | 60 | 62 | 0.044296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3236-3_0_4_line_64 |  | 62 | 63 | 0.0042965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3236-3_0_4_line_65 |  | 63 | 64 | 0.0052201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3236-3_0_4_line_66 |  | 64 | 65 | 0.0051292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3236-3_0_4_line_67 |  | 65 | 90 | 0.0058211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3236-3_0_4_line_68 |  | 66 | 67 | 0.02887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3236-3_0_4_line_69 |  | 67 | 68 | 0.026108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_3236-3_0_4_line_70 |  | 67 | 69 | 0.033288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_3236-3_0_4_line_71 |  | 68 | 70 | 0.013254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_3236-3_0_4_line_72 |  | 69 | 71 | 0.019329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
73 | LV_3236-3_0_4_line_73 |  | 70 | 72 | 0.021978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_3236-3_0_4_line_74 |  | 71 | 73 | 0.016566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_3236-3_0_4_line_75 |  | 72 | 74 | 0.010993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3236-3_0_4_line_76 |  | 72 | 75 | 0.0146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_3236-3_0_4_line_77 |  | 73 | 88 | 0.0087298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_3236-3_0_4_line_78 |  | 75 | 76 | 0.0064407 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_3236-3_0_4_line_79 |  | 76 | 77 | 0.026678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_3236-3_0_4_line_80 |  | 77 | 78 | 0.0017344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_3236-3_0_4_line_81 |  | 78 | 79 | 0.035365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_3236-3_0_4_line_82 |  | 79 | 80 | 0.014109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_3236-3_0_4_line_83 |  | 79 | 81 | 0.0082141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_3236-3_0_4_line_84 |  | 80 | 82 | 0.0028029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_3236-3_0_4_line_85 |  | 81 | 83 | 0.021998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
86 | LV_3236-3_0_4_line_86 |  | 82 | 84 | 0.025842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_3236-3_0_4_line_87 |  | 85 | 86 | 0.020399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
88 | LV_3236-3_0_4_line_88 |  | 86 | 87 | 0.023844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_3236-3_0_4_line_89 |  | 89 | 90 | 0.0052916 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3236-3_0_4_trafo_76 | 0.63 MVA 20/0.4 kV | 91 | 84 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2766516.3429 | 1257640.8856 | 2766535.2298 | 1257615.9625 | 2766548.4637 | 1257597.7779
1 | 2766516.3429 | 1257640.8856 | 2766489.7562 | 1257675.9693 | 2766485.1631 | 1257681.4736
2 | 2766570.9257 | 1257566.913 | 2766548.4637 | 1257597.7779
3 | 2766682.6186 | 1257534.2237 | 2766680.6483 | 1257529.9748 | 2766676.4085 | 1257527.2748 | 2766667.4147 | 1257524.8635 | 2766648.6764 | 1257523.9128 | 2766626.5906 | 1257527.1613 | 2766609.5964 | 1257533.1338 | 2766590.0475 | 1257545.697 | 2766577.8571 | 1257557.3886 | 2766570.9257 | 1257566.913
4 | 2766682.6186 | 1257534.2237 | 2766685.4466 | 1257524.3707
5 | 2766682.6186 | 1257534.2237 | 2766672.2905 | 1257564.9655 | 2766661.4423 | 1257592.2112 | 2766646.9074 | 1257621.4998
6 | 2766392.7259 | 1257785.6909 | 2766389.608 | 1257783.6122 | 2766417.549 | 1257750.8184 | 2766436.5338 | 1257731.1869
7 | 2766361.4797 | 1257768.895 | 2766387.9993 | 1257785.5468 | 2766389.608 | 1257783.6122 | 2766392.7259 | 1257785.6909
8 | 2766436.5338 | 1257731.1869 | 2766424.0202 | 1257718.1956
9 | 2766436.5338 | 1257731.1869 | 2766463.4002 | 1257700.1866
10 | 2766342.2979 | 1257759.8687 | 2766361.4797 | 1257768.895
11 | 2766361.4797 | 1257768.895 | 2766375.1594 | 1257738.0245 | 2766376.5376 | 1257732.2126 | 2766375.6431 | 1257720.831 | 2766376.9587 | 1257718.8548
12 | 2766685.4466 | 1257524.3707 | 2766676.2793 | 1257521.4205 | 2766658.4742 | 1257518.6831 | 2766644.8222 | 1257518.7766 | 2766623.8195 | 1257522.9455 | 2766606.7463 | 1257529.1035
13 | 2766646.9074 | 1257621.4998 | 2766643.8838 | 1257627.5878 | 2766620.9117 | 1257667.713
14 | 2766424.0202 | 1257718.1956 | 2766408.6076 | 1257702.1947
15 | 2766481.2413 | 1257679.6004 | 2766463.4002 | 1257700.1866
16 | 2766342.2979 | 1257759.8687 | 2766346.9877 | 1257743.0827 | 2766345.2744 | 1257728.9995
17 | 2766604.6537 | 1257691.1733 | 2766607.4623 | 1257687.6264 | 2766619.2675 | 1257670.585 | 2766620.9117 | 1257667.713
18 | 2766588.2307 | 1257678.7647 | 2766604.6537 | 1257691.1733
19 | 2766606.7463 | 1257529.1035 | 2766603.7109 | 1257530.1984 | 2766591.5349 | 1257539.3044
20 | 2766577.8791 | 1257551.7391 | 2766584.3186 | 1257544.7014 | 2766591.5349 | 1257539.3044
21 | 2766481.2413 | 1257679.6004 | 2766515.4915 | 1257633.9263
22 | 2766481.2413 | 1257679.6004 | 2766461.372 | 1257666.4745
23 | 2766515.4915 | 1257633.9263 | 2766503.0873 | 1257629.7732
24 | 2766515.4915 | 1257633.9263 | 2766528.7267 | 1257615.4851
25 | 2766443.6914 | 1257657.4148 | 2766452.575 | 1257660.6631 | 2766461.372 | 1257666.4745
26 | 2766503.0873 | 1257629.7732 | 2766482.896 | 1257623.0128
27 | 2766541.3993 | 1257597.8279 | 2766528.7267 | 1257615.4851
28 | 2766443.6914 | 1257657.4148 | 2766432.142 | 1257653.1919 | 2766429.8665 | 1257652.6484
29 | 2766396.7348 | 1257689.8688 | 2766408.6076 | 1257702.1947
30 | 2766541.3993 | 1257597.8279 | 2766532.6085 | 1257593.2981 | 2766518.1383 | 1257587.8998
31 | 2766541.3993 | 1257597.8279 | 2766550.2348 | 1257586.2381
32 | 2766429.8665 | 1257652.6484 | 2766420.8402 | 1257650.4927
33 | 2766343.2863 | 1257712.6575 | 2766345.2744 | 1257728.9995
34 | 2766395.413 | 1257644.4201 | 2766420.8402 | 1257650.4927
35 | 2766395.413 | 1257644.4201 | 2766368.4879 | 1257637.9897
36 | 2766359.0762 | 1257635.742 | 2766368.4879 | 1257637.9897
37 | 2766359.0762 | 1257635.742 | 2766354.4524 | 1257656.477
38 | 2766343.2863 | 1257712.6575 | 2766359.5698 | 1257709.3894 | 2766358.0213 | 1257700.3912
39 | 2766621.4147 | 1257441.3081 | 2766603.6454 | 1257471.7234 | 2766598.3707 | 1257475.4901 | 2766591.8923 | 1257476.563
40 | 2766638.4874 | 1257412.0853 | 2766621.4147 | 1257441.3081
41 | 2766591.8923 | 1257476.563 | 2766590.7629 | 1257476.75
42 | 2766604.8565 | 1257369.5381 | 2766606.9899 | 1257373.6247 | 2766607.2562 | 1257376.2239 | 2766607.5131 | 1257382.3709 | 2766607.2 | 1257386.2551 | 2766611.8913 | 1257389.0012 | 2766617.246 | 1257393.3787 | 2766626.4421 | 1257402.8142 | 2766629.6867 | 1257405.4861 | 2766634.7159 | 1257409.6321 | 2766638.4874 | 1257412.0853
43 | 2766577.8416 | 1257478.8899 | 2766590.7629 | 1257476.75
44 | 2766604.8565 | 1257369.5381 | 2766595.7982 | 1257373.4207 | 2766590.114 | 1257378.0657
45 | 2766604.8565 | 1257369.5381 | 2766626.8464 | 1257360.0211
46 | 2766568.835 | 1257480.3815 | 2766577.8416 | 1257478.8899
47 | 2766590.114 | 1257378.0657 | 2766576.3163 | 1257353.5848
48 | 2766592.2338 | 1257381.8293 | 2766590.114 | 1257378.0657
49 | 2766592.2338 | 1257381.8293 | 2766581.9451 | 1257385.5265
50 | 2766580.2359 | 1257386.1407 | 2766581.9451 | 1257385.5265
51 | 2766555.0321 | 1257482.6674 | 2766568.835 | 1257480.3815
52 | 2766564.2233 | 1257349.8736 | 2766576.3163 | 1257353.5848 | 2766576.3163 | 1257353.5848
53 | 2766580.2359 | 1257386.1407 | 2766558.4882 | 1257393.0358
54 | 2766555.0321 | 1257482.6674 | 2766547.821 | 1257483.8616
55 | 2766527.021 | 1257487.3063 | 2766547.821 | 1257483.8616
56 | 2766527.021 | 1257487.3063 | 2766514.037 | 1257489.4566
57 | 2766503.2984 | 1257491.235 | 2766514.037 | 1257489.4566
58 | 2766479.4294 | 1257495.1879 | 2766503.2984 | 1257491.235
59 | 2766553.6955 | 1257394.5553 | 2766558.4882 | 1257393.0358
60 | 2766553.6955 | 1257394.5553 | 2766548.6211 | 1257396.1641
61 | 2766548.6211 | 1257396.1641 | 2766543.406 | 1257397.8175
62 | 2766476.6277 | 1257418.9894 | 2766455.4051 | 1257425.718
63 | 2766476.6277 | 1257418.9894 | 2766518.852 | 1257405.6023
64 | 2766522.9475 | 1257404.3038 | 2766518.852 | 1257405.6023
65 | 2766527.9236 | 1257402.7262 | 2766522.9475 | 1257404.3038
66 | 2766532.8129 | 1257401.176 | 2766527.9236 | 1257402.7262
67 | 2766538.3618 | 1257399.4168 | 2766532.8129 | 1257401.176
68 | 2766402.5636 | 1257507.9177 | 2766395.0987 | 1257480.0298
69 | 2766402.5636 | 1257507.9177 | 2766405.3121 | 1257533.8807
70 | 2766402.5636 | 1257507.9177 | 2766435.4042 | 1257502.4789
71 | 2766405.5965 | 1257547.103 | 2766405.842 | 1257538.887 | 2766405.3121 | 1257533.8807
72 | 2766454.4734 | 1257499.3209 | 2766435.4042 | 1257502.4789
73 | 2766404.9399 | 1257569.0714 | 2766405.5965 | 1257547.103
74 | 2766454.4734 | 1257499.3209 | 2766470.8169 | 1257496.6143
75 | 2766404.9399 | 1257569.0714 | 2766393.9899 | 1257568.0971
76 | 2766404.9399 | 1257569.0714 | 2766419.4393 | 1257570.7861
77 | 2766479.4294 | 1257495.1879 | 2766470.8169 | 1257496.6143
78 | 2766419.4393 | 1257570.7861 | 2766425.8354 | 1257571.5425
79 | 2766425.8354 | 1257571.5425 | 2766452.3292 | 1257574.6756
80 | 2766454.0516 | 1257574.8793 | 2766452.3292 | 1257574.6756
81 | 2766488.9667 | 1257580.1901 | 2766478.9981 | 1257577.8295 | 2766454.0516 | 1257574.8793
82 | 2766488.9667 | 1257580.1901 | 2766491.9644 | 1257566.4031
83 | 2766488.9667 | 1257580.1901 | 2766496.9604 | 1257582.0802
84 | 2766491.9644 | 1257566.4031 | 2766492.5599 | 1257563.6642
85 | 2766518.1383 | 1257587.8998 | 2766512.1945 | 1257585.6825 | 2766496.9604 | 1257582.0802
86 | 2766498.0502 | 1257538.4124 | 2766492.5599 | 1257563.6642
87 | 2766577.8791 | 1257551.7391 | 2766569.8232 | 1257560.5436 | 2766564.691 | 1257567.2757
88 | 2766564.691 | 1257567.2757 | 2766550.2348 | 1257586.2381
89 | 2766543.406 | 1257397.8175 | 2766538.3618 | 1257399.4168

## bus_geodata
| x | y | coords
0 | 2766516.3429 | 1257640.8856
1 | 2766548.4637 | 1257597.7779
2 | 2766485.1631 | 1257681.4736
3 | 2766570.9257 | 1257566.913
4 | 2766682.6186 | 1257534.2237
5 | 2766392.7259 | 1257785.6909
6 | 2766436.5338 | 1257731.1869
7 | 2766361.4797 | 1257768.895
8 | 2766685.4466 | 1257524.3707
9 | 2766646.9074 | 1257621.4998
10 | 2766424.0202 | 1257718.1956
11 | 2766463.4002 | 1257700.1866
12 | 2766342.2979 | 1257759.8687
13 | 2766376.9587 | 1257718.8548
14 | 2766620.9117 | 1257667.713
15 | 2766604.6537 | 1257691.1733
16 | 2766588.2307 | 1257678.7647
17 | 2766606.7463 | 1257529.1035
18 | 2766591.5349 | 1257539.3044
19 | 2766481.2413 | 1257679.6004
20 | 2766515.4915 | 1257633.9263
21 | 2766461.372 | 1257666.4745
22 | 2766503.0873 | 1257629.7732
23 | 2766528.7268 | 1257615.4851
24 | 2766443.6914 | 1257657.4148
25 | 2766408.6076 | 1257702.1947
26 | 2766482.896 | 1257623.0128
27 | 2766541.3993 | 1257597.8279
28 | 2766429.8665 | 1257652.6484
29 | 2766396.7348 | 1257689.8688
30 | 2766345.2744 | 1257728.9995
31 | 2766420.8402 | 1257650.4927
32 | 2766395.413 | 1257644.4201
33 | 2766368.4879 | 1257637.9897
34 | 2766359.0762 | 1257635.742
35 | 2766354.4524 | 1257656.477
36 | 2766358.0213 | 1257700.3912
37 | 2766343.2863 | 1257712.6575
38 | 2766621.4147 | 1257441.3081
39 | 2766591.8923 | 1257476.563
40 | 2766638.4874 | 1257412.0853
41 | 2766590.7629 | 1257476.75
42 | 2766604.8565 | 1257369.5381
43 | 2766577.8416 | 1257478.8899
44 | 2766590.114 | 1257378.0657
45 | 2766626.8464 | 1257360.0211
46 | 2766592.2338 | 1257381.8293
47 | 2766581.9451 | 1257385.5265
48 | 2766568.835 | 1257480.3815
49 | 2766576.3163 | 1257353.5848
50 | 2766580.2359 | 1257386.1407
51 | 2766555.0321 | 1257482.6674
52 | 2766547.821 | 1257483.8616
53 | 2766527.021 | 1257487.3063
54 | 2766514.037 | 1257489.4566
55 | 2766503.2984 | 1257491.235
56 | 2766558.4882 | 1257393.0358
57 | 2766553.6955 | 1257394.5553
58 | 2766564.2233 | 1257349.8736
59 | 2766548.6211 | 1257396.1641
60 | 2766476.6277 | 1257418.9894
61 | 2766455.4051 | 1257425.718
62 | 2766518.852 | 1257405.6023
63 | 2766522.9475 | 1257404.3038
64 | 2766527.9236 | 1257402.7262
65 | 2766532.8129 | 1257401.176
66 | 2766395.0987 | 1257480.0298
67 | 2766402.5636 | 1257507.9177
68 | 2766405.3121 | 1257533.8807
69 | 2766435.4042 | 1257502.4789
70 | 2766405.5965 | 1257547.103
71 | 2766454.4734 | 1257499.3209
72 | 2766404.9399 | 1257569.0714
73 | 2766470.8169 | 1257496.6143
74 | 2766393.9899 | 1257568.0971
75 | 2766419.4393 | 1257570.7861
76 | 2766425.8354 | 1257571.5425
77 | 2766452.3292 | 1257574.6756
78 | 2766454.0516 | 1257574.8793
79 | 2766488.9667 | 1257580.1901
80 | 2766491.9644 | 1257566.4031
81 | 2766496.9604 | 1257582.0802
82 | 2766492.5599 | 1257563.6642
83 | 2766518.1383 | 1257587.8998
84 | 2766498.0502 | 1257538.4124
85 | 2766577.8791 | 1257551.7391
86 | 2766564.691 | 1257567.2757
87 | 2766550.2348 | 1257586.2381
88 | 2766479.4294 | 1257495.1879
89 | 2766543.406 | 1257397.8175
90 | 2766538.3618 | 1257399.4168
91 | 2766488.9667 | 1257580.1901

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1