## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3251-8_1_2_node_19 | 0.4 | n |  | TRUE
1 | bus_LV_3251-8_1_2_node_176 | 0.4 | n |  | TRUE
2 | bus_LV_3251-8_1_2_node_175 | 0.4 | n |  | TRUE
3 | bus_LV_3251-8_1_2_node_22 | 0.4 | n |  | TRUE
4 | bus_LV_3251-8_1_2_node_23 | 0.4 | n |  | TRUE
5 | bus_LV_3251-8_1_2_node_24 | 0.4 | n |  | TRUE
6 | bus_LV_3251-8_1_2_node_25 | 0.4 | n |  | TRUE
7 | bus_LV_3251-8_1_2_node_27 | 0.4 | n |  | TRUE
8 | bus_LV_3251-8_1_2_node_28 | 0.4 | n |  | TRUE
9 | bus_LV_3251-8_1_2_node_26 | 0.4 | n |  | TRUE
10 | bus_LV_3251-8_1_2_node_29 | 0.4 | n |  | TRUE
11 | bus_LV_3251-8_1_2_node_30 | 0.4 | n |  | TRUE
12 | bus_LV_3251-8_1_2_node_106 | 0.4 | n |  | TRUE
13 | bus_LV_3251-8_1_2_node_109 | 0.4 | n |  | TRUE
14 | bus_LV_3251-8_1_2_node_124 | 0.4 | n |  | TRUE
15 | bus_LV_3251-8_1_2_node_120 | 0.4 | n |  | TRUE
16 | bus_LV_3251-8_1_2_node_71 | 0.4 | n |  | TRUE
17 | bus_LV_3251-8_1_2_node_76 | 0.4 | n |  | TRUE
18 | bus_LV_3251-8_1_2_node_73 | 0.4 | n |  | TRUE
19 | bus_LV_3251-8_1_2_node_74 | 0.4 | n |  | TRUE
20 | bus_LV_3251-8_1_2_node_75 | 0.4 | n |  | TRUE
21 | bus_LV_3251-8_1_2_node_134 | 0.4 | n |  | TRUE
22 | bus_LV_3251-8_1_2_node_80 | 0.4 | n |  | TRUE
23 | bus_LV_3251-8_1_2_node_77 | 0.4 | n |  | TRUE
24 | bus_LV_3251-8_1_2_node_78 | 0.4 | n |  | TRUE
25 | bus_LV_3251-8_1_2_node_79 | 0.4 | n |  | TRUE
26 | bus_LV_3251-8_1_2_node_83 | 0.4 | n |  | TRUE
27 | bus_LV_3251-8_1_2_node_82 | 0.4 | n |  | TRUE
28 | bus_LV_3251-8_1_2_node_81 | 0.4 | n |  | TRUE
29 | bus_LV_3251-8_1_2_node_85 | 0.4 | n |  | TRUE
30 | bus_LV_3251-8_1_2_node_84 | 0.4 | n |  | TRUE
31 | bus_LV_3251-8_1_2_node_86 | 0.4 | n |  | TRUE
32 | bus_LV_3251-8_1_2_node_87 | 0.4 | n |  | TRUE
33 | bus_LV_3251-8_1_2_node_88 | 0.4 | n |  | TRUE
34 | bus_LV_3251-8_1_2_node_89 | 0.4 | n |  | TRUE
35 | bus_LV_3251-8_1_2_node_90 | 0.4 | n |  | TRUE
36 | bus_LV_3251-8_1_2_node_91 | 0.4 | n |  | TRUE
37 | bus_LV_3251-8_1_2_node_92 | 0.4 | n |  | TRUE
38 | bus_LV_3251-8_1_2_node_93 | 0.4 | n |  | TRUE
39 | bus_LV_3251-8_1_2_node_94 | 0.4 | n |  | TRUE
40 | bus_LV_3251-8_1_2_node_95 | 0.4 | n |  | TRUE
41 | bus_LV_3251-8_1_2_node_96 | 0.4 | n |  | TRUE
42 | bus_LV_3251-8_1_2_node_97 | 0.4 | n |  | TRUE
43 | bus_LV_3251-8_1_2_node_98 | 0.4 | n |  | TRUE
44 | bus_LV_3251-8_1_2_node_99 | 0.4 | n |  | TRUE
45 | bus_LV_3251-8_1_2_node_100 | 0.4 | n |  | TRUE
46 | bus_LV_3251-8_1_2_node_101 | 0.4 | n |  | TRUE
47 | bus_LV_3251-8_1_2_node_102 | 0.4 | n |  | TRUE
48 | bus_LV_3251-8_1_2_node_103 | 0.4 | n |  | TRUE
49 | bus_LV_3251-8_1_2_node_104 | 0.4 | n |  | TRUE
50 | bus_LV_3251-8_1_2_node_105 | 0.4 | n |  | TRUE
51 | bus_LV_3251-8_1_2_node_107 | 0.4 | n |  | TRUE
52 | bus_LV_3251-8_1_2_node_108 | 0.4 | n |  | TRUE
53 | bus_LV_3251-8_1_2_node_115 | 0.4 | n |  | TRUE
54 | bus_LV_3251-8_1_2_node_114 | 0.4 | n |  | TRUE
55 | bus_LV_3251-8_1_2_node_110 | 0.4 | n |  | TRUE
56 | bus_LV_3251-8_1_2_node_111 | 0.4 | n |  | TRUE
57 | bus_LV_3251-8_1_2_node_112 | 0.4 | n |  | TRUE
58 | bus_LV_3251-8_1_2_node_116 | 0.4 | n |  | TRUE
59 | bus_LV_3251-8_1_2_node_113 | 0.4 | n |  | TRUE
60 | bus_LV_3251-8_1_2_node_117 | 0.4 | n |  | TRUE
61 | bus_LV_3251-8_1_2_node_118 | 0.4 | n |  | TRUE
62 | bus_LV_3251-8_1_2_node_119 | 0.4 | n |  | TRUE
63 | bus_LV_3251-8_1_2_node_125 | 0.4 | n |  | TRUE
64 | bus_LV_3251-8_1_2_node_121 | 0.4 | n |  | TRUE
65 | bus_LV_3251-8_1_2_node_122 | 0.4 | n |  | TRUE
66 | bus_LV_3251-8_1_2_node_123 | 0.4 | n |  | TRUE
67 | bus_LV_3251-8_1_2_node_126 | 0.4 | n |  | TRUE
68 | bus_LV_3251-8_1_2_node_127 | 0.4 | n |  | TRUE
69 | bus_LV_3251-8_1_2_node_132 | 0.4 | n |  | TRUE
70 | bus_LV_3251-8_1_2_node_128 | 0.4 | n |  | TRUE
71 | bus_LV_3251-8_1_2_node_129 | 0.4 | n |  | TRUE
72 | bus_LV_3251-8_1_2_node_131 | 0.4 | n |  | TRUE
73 | bus_LV_3251-8_1_2_node_130 | 0.4 | n |  | TRUE
74 | bus_LV_3251-8_1_2_node_140 | 0.4 | n |  | TRUE
75 | bus_LV_3251-8_1_2_node_135 | 0.4 | n |  | TRUE
76 | bus_LV_3251-8_1_2_node_254 | 0.4 | n |  | TRUE
77 | bus_LV_3251-8_1_2_node_133 | 0.4 | n |  | TRUE
78 | bus_LV_3251-8_1_2_node_136 | 0.4 | n |  | TRUE
79 | bus_LV_3251-8_1_2_node_170 | 0.4 | n |  | TRUE
80 | bus_LV_3251-8_1_2_node_166 | 0.4 | n |  | TRUE
81 | bus_LV_3251-8_1_2_node_169 | 0.4 | n |  | TRUE
82 | bus_LV_3251-8_1_2_node_171 | 0.4 | n |  | TRUE
83 | bus_LV_3251-8_1_2_node_172 | 0.4 | n |  | TRUE
84 | bus_LV_3251-8_1_2_node_173 | 0.4 | n |  | TRUE
85 | bus_LV_3251-8_1_2_node_174 | 0.4 | n |  | TRUE
86 | bus_LV_3251-8_1_2_node_255 | 0.4 | n |  | TRUE
87 | bus_LV_3251-8_1_2_node_256 | 0.4 | n |  | TRUE
88 | bus_MV_50_0_node_85 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3251-8_1_2_load_176 | 1 | 0.0014682 | 0.00036796 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3251-8_1_2_load_175 | 2 | 0.017427 | 0.0043675 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3251-8_1_2_load_22 | 3 | 0.024038 | 0.0060245 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3251-8_1_2_load_23 | 4 | 0.0014184 | 0.00035548 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3251-8_1_2_load_24 | 5 | 0.0041914 | 0.0010505 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3251-8_1_2_load_28 | 8 | 0.0033164 | 0.00083118 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3251-8_1_2_load_29 | 10 | 0.0080422 | 0.0020156 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3251-8_1_2_load_30 | 11 | 0.0023554 | 0.00059031 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3251-8_1_2_load_106 | 12 | 0.0024701 | 0.00061907 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3251-8_1_2_load_109 | 13 | 0.0025668 | 0.00064329 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3251-8_1_2_load_124 | 14 | 0.0041205 | 0.0010327 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3251-8_1_2_load_120 | 15 | 0.0046292 | 0.0011602 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3251-8_1_2_load_71 | 16 | 0.0028438 | 0.00071271 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3251-8_1_2_load_75 | 20 | 0.0026345 | 0.00066026 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3251-8_1_2_load_134 | 21 | 0.0012684 | 0.0003179 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3251-8_1_2_load_80 | 22 | 0.00049889 | 0.00012503 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3251-8_1_2_load_77 | 23 | 0.00099172 | 0.00024855 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3251-8_1_2_load_78 | 24 | 0.0013487 | 0.00033801 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3251-8_1_2_load_79 | 25 | 0.0010441 | 0.00026168 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3251-8_1_2_load_83 | 26 | 0.00038799 | 9.724e-05 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3251-8_1_2_load_82 | 27 | 0.00033064 | 8.2866e-05 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3251-8_1_2_load_81 | 28 | 0.0033952 | 0.00085091 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3251-8_1_2_load_84 | 30 | 0.00035232 | 8.83e-05 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3251-8_1_2_load_86 | 31 | 0.00032263 | 8.0859e-05 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3251-8_1_2_load_88 | 33 | 0.00063509 | 0.00015917 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3251-8_1_2_load_89 | 34 | 0.0020414 | 0.00051162 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3251-8_1_2_load_93 | 38 | 0.0073466 | 0.0018412 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3251-8_1_2_load_94 | 39 | 0.0016298 | 0.00040846 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3251-8_1_2_load_95 | 40 | 0.0014401 | 0.00036092 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3251-8_1_2_load_96 | 41 | 0.001035 | 0.0002594 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3251-8_1_2_load_97 | 42 | 0.0011342 | 0.00028425 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3251-8_1_2_load_99 | 44 | 0.00090972 | 0.000228 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3251-8_1_2_load_101 | 46 | 0.00098813 | 0.00024765 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3251-8_1_2_load_102 | 47 | 0.0048011 | 0.0012033 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3251-8_1_2_load_104 | 49 | 0.0009113 | 0.00022839 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3251-8_1_2_load_105 | 50 | 0.0031072 | 0.00077875 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3251-8_1_2_load_107 | 51 | 0.0012488 | 0.00031297 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3251-8_1_2_load_108 | 52 | 0.0024167 | 0.00060568 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3251-8_1_2_load_115 | 53 | 0.0011474 | 0.00028756 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3251-8_1_2_load_114 | 54 | 0.0032174 | 0.00080635 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3251-8_1_2_load_111 | 56 | 0.0064734 | 0.0016224 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3251-8_1_2_load_112 | 57 | 0.0055717 | 0.0013964 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3251-8_1_2_load_116 | 58 | 0.0042032 | 0.0010534 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3251-8_1_2_load_113 | 59 | 0.0036162 | 0.0009063 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3251-8_1_2_load_117 | 60 | 0.0017707 | 0.00044377 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3251-8_1_2_load_118 | 61 | 0.0019917 | 0.00049917 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3251-8_1_2_load_119 | 62 | 0.0021156 | 0.00053022 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3251-8_1_2_load_125 | 63 | 0.0014464 | 0.00036249 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3251-8_1_2_load_123 | 66 | 0.0048245 | 0.0012091 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3251-8_1_2_load_126 | 67 | 0.0015486 | 0.00038811 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3251-8_1_2_load_127 | 68 | 0.0020563 | 0.00051535 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3251-8_1_2_load_132 | 69 | 0.0011305 | 0.00028333 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3251-8_1_2_load_128 | 70 | 0.0023927 | 0.00059967 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3251-8_1_2_load_131 | 72 | 0.00092449 | 0.0002317 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3251-8_1_2_load_140 | 74 | 0.0023351 | 0.00058522 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3251-8_1_2_load_254 | 76 | 0.0014276 | 0.00035779 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3251-8_1_2_load_133 | 77 | 0.0045928 | 0.0011511 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3251-8_1_2_load_136 | 78 | 0.0015427 | 0.00038663 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3251-8_1_2_load_170 | 79 | 0.0010776 | 0.00027008 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3251-8_1_2_load_166 | 80 | 0.0013571 | 0.00034011 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3251-8_1_2_load_171 | 82 | 0.0013325 | 0.00033395 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3251-8_1_2_load_172 | 83 | 0.0019307 | 0.00048388 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3251-8_1_2_load_173 | 84 | 0.0012069 | 0.00030247 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3251-8_1_2_load_174 | 85 | 0.00099338 | 0.00024897 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3251-8_1_2_load_255 | 86 | 0.00090749 | 0.00022744 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3251-8_1_2_load_256 | 87 | 0.0032595 | 0.0008169 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 11 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3251-8_1_2_line_0 |  | 0 | 1 | 0.017278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3251-8_1_2_line_1 |  | 0 | 2 | 0.050501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3251-8_1_2_line_2 |  | 2 | 85 | 0.0079434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3251-8_1_2_line_3 |  | 3 | 4 | 0.016279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3251-8_1_2_line_4 |  | 3 | 5 | 0.0025534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3251-8_1_2_line_5 |  | 4 | 6 | 0.036094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3251-8_1_2_line_6 |  | 6 | 7 | 0.017263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3251-8_1_2_line_7 |  | 6 | 8 | 0.018706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3251-8_1_2_line_8 |  | 7 | 12 | 0.013661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3251-8_1_2_line_9 |  | 8 | 13 | 0.0036761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3251-8_1_2_line_10 |  | 9 | 10 | 0.036277 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3251-8_1_2_line_11 |  | 9 | 11 | 0.018153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3251-8_1_2_line_12 |  | 10 | 14 | 0.023846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3251-8_1_2_line_13 |  | 11 | 15 | 0.0099224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3251-8_1_2_line_14 |  | 12 | 50 | 0.0046274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3251-8_1_2_line_15 |  | 14 | 19 | 0.038852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3251-8_1_2_line_16 |  | 14 | 28 | 0.059076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3251-8_1_2_line_17 |  | 15 | 64 | 0.02292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3251-8_1_2_line_18 |  | 16 | 17 | 0.019869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3251-8_1_2_line_19 |  | 17 | 22 | 0.027777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3251-8_1_2_line_20 |  | 18 | 19 | 0.026207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3251-8_1_2_line_21 |  | 18 | 20 | 0.0098623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3251-8_1_2_line_22 |  | 19 | 21 | 0.0086973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3251-8_1_2_line_23 |  | 21 | 75 | 0.037978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3251-8_1_2_line_24 |  | 22 | 27 | 0.068342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3251-8_1_2_line_25 |  | 22 | 28 | 0.1167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3251-8_1_2_line_26 |  | 23 | 24 | 0.019301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3251-8_1_2_line_27 |  | 24 | 25 | 0.021415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3251-8_1_2_line_28 |  | 25 | 26 | 0.018946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3251-8_1_2_line_29 |  | 26 | 30 | 0.02409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3251-8_1_2_line_30 |  | 27 | 29 | 0.020536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3251-8_1_2_line_31 |  | 29 | 31 | 0.065285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3251-8_1_2_line_32 |  | 30 | 31 | 0.022229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3251-8_1_2_line_33 |  | 31 | 32 | 0.04402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3251-8_1_2_line_34 |  | 32 | 33 | 0.020308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3251-8_1_2_line_35 |  | 32 | 34 | 0.022874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3251-8_1_2_line_36 |  | 34 | 35 | 0.035989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3251-8_1_2_line_37 |  | 35 | 36 | 0.012791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3251-8_1_2_line_38 |  | 36 | 37 | 0.047263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3251-8_1_2_line_39 |  | 37 | 38 | 0.011668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3251-8_1_2_line_40 |  | 39 | 40 | 0.01209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3251-8_1_2_line_41 |  | 39 | 41 | 0.01816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3251-8_1_2_line_42 |  | 40 | 42 | 0.022084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3251-8_1_2_line_43 |  | 41 | 43 | 0.012377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3251-8_1_2_line_44 |  | 42 | 44 | 0.023791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3251-8_1_2_line_45 |  | 43 | 45 | 0.010309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3251-8_1_2_line_46 |  | 43 | 46 | 0.015499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3251-8_1_2_line_47 |  | 44 | 47 | 0.015907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3251-8_1_2_line_48 |  | 45 | 48 | 0.016057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3251-8_1_2_line_49 |  | 45 | 49 | 0.028912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3251-8_1_2_line_50 |  | 47 | 50 | 0.014145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3251-8_1_2_line_51 |  | 48 | 51 | 0.021713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3251-8_1_2_line_52 |  | 48 | 52 | 0.017202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3251-8_1_2_line_53 |  | 51 | 53 | 0.012021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3251-8_1_2_line_54 |  | 52 | 54 | 0.015278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3251-8_1_2_line_55 |  | 54 | 59 | 0.011794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3251-8_1_2_line_56 |  | 55 | 56 | 0.012431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3251-8_1_2_line_57 |  | 55 | 57 | 0.022704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3251-8_1_2_line_58 |  | 56 | 58 | 0.022749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3251-8_1_2_line_59 |  | 57 | 59 | 0.029191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3251-8_1_2_line_60 |  | 58 | 60 | 0.012694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3251-8_1_2_line_61 |  | 60 | 61 | 0.0020235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3251-8_1_2_line_62 |  | 61 | 62 | 0.023045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3251-8_1_2_line_63 |  | 62 | 63 | 3.3111e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3251-8_1_2_line_64 |  | 63 | 66 | 0.00079504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3251-8_1_2_line_65 |  | 64 | 65 | 0.019564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3251-8_1_2_line_66 |  | 64 | 66 | 0.030703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3251-8_1_2_line_67 |  | 65 | 67 | 0.016798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3251-8_1_2_line_68 |  | 65 | 68 | 0.020499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3251-8_1_2_line_69 |  | 67 | 69 | 0.0034461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3251-8_1_2_line_70 |  | 68 | 70 | 0.025783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3251-8_1_2_line_71 |  | 69 | 77 | 0.018082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3251-8_1_2_line_72 |  | 70 | 71 | 0.0020364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3251-8_1_2_line_73 |  | 71 | 72 | 0.018012 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3251-8_1_2_line_74 |  | 72 | 76 | 0.0048155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3251-8_1_2_line_75 |  | 73 | 74 | 0.0015505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3251-8_1_2_line_76 |  | 73 | 75 | 0.028235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3251-8_1_2_line_77 |  | 74 | 79 | 0.02746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3251-8_1_2_line_78 |  | 75 | 78 | 0.012764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3251-8_1_2_line_79 |  | 76 | 86 | 0.0014804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3251-8_1_2_line_80 |  | 79 | 81 | 0.012543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3251-8_1_2_line_81 |  | 80 | 81 | 0.01665 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3251-8_1_2_line_82 |  | 81 | 82 | 0.011976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3251-8_1_2_line_83 |  | 82 | 83 | 0.013236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3251-8_1_2_line_84 |  | 83 | 84 | 0.023633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3251-8_1_2_line_85 |  | 84 | 85 | 0.034721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3251-8_1_2_line_86 |  | 86 | 87 | 0.0031024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3251-8_1_2_trafo_30 | 0.63 MVA 20/0.4 kV | 88 | 11 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2760393.304 | 1249151.4192 | 2760380.544 | 1249163.0683
1 | 2760393.304 | 1249151.4192 | 2760385.2359 | 1249141.8913 | 2760357.6333 | 1249115.7517 | 2760357.6333 | 1249115.7517
2 | 2760357.6333 | 1249115.7517 | 2760351.2872 | 1249110.9742
3 | 2760295.2678 | 1248885.4488 | 2760303.673 | 1248871.5079
4 | 2760295.2678 | 1248885.4488 | 2760293.9493 | 1248887.6355
5 | 2760322.3096 | 1248840.5976 | 2760303.673 | 1248871.5079
6 | 2760330.392 | 1248825.3341 | 2760322.3096 | 1248840.5976
7 | 2760322.3096 | 1248840.5976 | 2760338.7975 | 1248849.4333
8 | 2760330.392 | 1248825.3341 | 2760318.6295 | 1248818.3868
9 | 2760338.7975 | 1248849.4333 | 2760342.0376 | 1248851.1697
10 | 2760274.1559 | 1248920.4647 | 2760259.2852 | 1248940.6052 | 2760251.338 | 1248948.5554
11 | 2760274.1559 | 1248920.4647 | 2760289.4058 | 1248930.3123
12 | 2760233.2675 | 1248963.9604 | 2760241.7265 | 1248958.1705 | 2760251.338 | 1248948.5554
13 | 2760289.4058 | 1248930.3123 | 2760297.7414 | 1248935.6949
14 | 2760318.6295 | 1248818.3868 | 2760314.6452 | 1248816.0336
15 | 2760201.0216 | 1248985.6313 | 2760224.8288 | 1248969.7365 | 2760233.2675 | 1248963.9604
16 | 2760233.2675 | 1248963.9604 | 2760193.7514 | 1248920.0468
17 | 2760316.9962 | 1248948.1286 | 2760297.7414 | 1248935.6949
18 | 2760088.8452 | 1248861.7101 | 2760075.3919 | 1248876.3316
19 | 2760088.8452 | 1248861.7101 | 2760107.6506 | 1248841.2674
20 | 2760174.7736 | 1248986.1782 | 2760187.7183 | 1248985.2715 | 2760201.0216 | 1248985.6313
21 | 2760174.7736 | 1248986.1782 | 2760166.155 | 1248990.9725
22 | 2760201.0216 | 1248985.6313 | 2760207.014 | 1248991.9349
23 | 2760237.1765 | 1249014.9156 | 2760209.8229 | 1248994.8896 | 2760207.014 | 1248991.9349
24 | 2760107.6506 | 1248841.2674 | 2760112.7749 | 1248835.6969 | 2760142.8245 | 1248782.8732
25 | 2760193.7514 | 1248920.0468 | 2760107.6506 | 1248841.2674
26 | 2760037.4356 | 1248816.2645 | 2760049.0221 | 1248800.8283
27 | 2760049.0221 | 1248800.8283 | 2760061.8775 | 1248783.7017
28 | 2760061.8775 | 1248783.7017 | 2760071.6214 | 1248770.7204 | 2760073.1137 | 1248768.4526
29 | 2760086.3561 | 1248748.3291 | 2760073.1137 | 1248768.4526
30 | 2760152.979 | 1248765.0229 | 2760142.8245 | 1248782.8732
31 | 2760098.1944 | 1248729.5152 | 2760152.979 | 1248765.0229
32 | 2760086.3561 | 1248748.3291 | 2760098.1944 | 1248729.5152
33 | 2760118.8894 | 1248690.85 | 2760114.9149 | 1248701.7536 | 2760107.0966 | 1248715.3672 | 2760098.1944 | 1248729.5152
34 | 2760118.8894 | 1248690.85 | 2760137.0662 | 1248699.9055
35 | 2760118.8894 | 1248690.85 | 2760121.8438 | 1248682.7439 | 2760124.1247 | 1248668.6818
36 | 2760130.556 | 1248633.274 | 2760125.235 | 1248661.8367 | 2760124.1247 | 1248668.6818
37 | 2760130.556 | 1248633.274 | 2760141.8865 | 1248639.2749
38 | 2760167.0061 | 1248599.2021 | 2760141.8865 | 1248639.2749
39 | 2760167.0061 | 1248599.2021 | 2760177.0857 | 1248605.0803
40 | 2760338.679 | 1248744.4547 | 2760338.679 | 1248744.4547 | 2760332.7524 | 1248754.9921
41 | 2760338.679 | 1248744.4547 | 2760354.7763 | 1248752.8609
42 | 2760332.7524 | 1248754.9921 | 2760321.9266 | 1248774.2401
43 | 2760365.7472 | 1248758.5899 | 2760354.7763 | 1248752.8609
44 | 2760321.9266 | 1248774.2401 | 2760310.2639 | 1248794.9758
45 | 2760365.7472 | 1248758.5899 | 2760360.914 | 1248767.7017
46 | 2760365.7472 | 1248758.5899 | 2760373.4089 | 1248745.1176
47 | 2760310.2639 | 1248794.9758 | 2760302.4661 | 1248808.8402
48 | 2760360.914 | 1248767.7017 | 2760374.8483 | 1248775.7533
49 | 2760360.914 | 1248767.7017 | 2760347.3825 | 1248793.2522
50 | 2760302.4661 | 1248808.8402 | 2760302.4661 | 1248808.8402 | 2760314.6452 | 1248816.0336
51 | 2760374.8483 | 1248775.7533 | 2760395.1928 | 1248768.166
52 | 2760374.8483 | 1248775.7533 | 2760375.8243 | 1248790.4946 | 2760375.9033 | 1248792.9219
53 | 2760395.1928 | 1248768.166 | 2760397.9535 | 1248767.1364 | 2760402.5975 | 1248759.3401
54 | 2760375.9033 | 1248792.9219 | 2760376.4003 | 1248808.1915
55 | 2760376.784 | 1248819.9797 | 2760376.4003 | 1248808.1915
56 | 2760378.4723 | 1248871.8479 | 2760372.1488 | 1248882.5502
57 | 2760378.4723 | 1248871.8479 | 2760377.7337 | 1248849.1557
58 | 2760372.1488 | 1248882.5502 | 2760360.5766 | 1248902.1356
59 | 2760376.784 | 1248819.9797 | 2760377.7337 | 1248849.1557
60 | 2760360.5766 | 1248902.1356 | 2760354.1189 | 1248913.0649
61 | 2760353.0896 | 1248914.807 | 2760354.1189 | 1248913.0649
62 | 2760341.3132 | 1248934.6157 | 2760344.8893 | 1248928.6856 | 2760353.0896 | 1248914.807
63 | 2760341.3132 | 1248934.6157 | 2760341.2961 | 1248934.6441
64 | 2760341.2961 | 1248934.6441 | 2760340.8855 | 1248935.3249
65 | 2760316.9962 | 1248948.1286 | 2760306.5295 | 1248964.6733
66 | 2760316.9962 | 1248948.1286 | 2760323.1766 | 1248949.5305 | 2760331.7534 | 1248947.8162 | 2760335.2144 | 1248944.729 | 2760340.8855 | 1248935.3249
67 | 2760306.5295 | 1248964.6733 | 2760320.5624 | 1248973.9058
68 | 2760306.5295 | 1248964.6733 | 2760295.5692 | 1248981.9959
69 | 2760320.5624 | 1248973.9058 | 2760323.4413 | 1248975.7999
70 | 2760281.7835 | 1249003.7839 | 2760295.5692 | 1248981.9959
71 | 2760338.5469 | 1248985.7381 | 2760323.4413 | 1248975.7999
72 | 2760280.6947 | 1249005.5047 | 2760281.7835 | 1249003.7839
73 | 2760280.6947 | 1249005.5047 | 2760296.0343 | 1249014.9463
74 | 2760300.1353 | 1249017.4704 | 2760296.0343 | 1249014.9463
75 | 2760253.83 | 1249036.9434 | 2760254.5101 | 1249038.3368
76 | 2760253.83 | 1249036.9434 | 2760247.0082 | 1249022.945 | 2760237.1765 | 1249014.9156
77 | 2760269.6937 | 1249060.6176 | 2760264.681 | 1249057.0014 | 2760259.3923 | 1249048.3386 | 2760254.5101 | 1249038.3368
78 | 2760237.1765 | 1249014.9156 | 2760228.9643 | 1249024.6874
79 | 2760300.1353 | 1249017.4704 | 2760301.3961 | 1249018.2464
80 | 2760279.866 | 1249067.9562 | 2760269.6937 | 1249060.6176
81 | 2760279.866 | 1249067.9562 | 2760268.9646 | 1249080.5409
82 | 2760279.866 | 1249067.9562 | 2760290.3884 | 1249073.6754
83 | 2760290.3884 | 1249073.6754 | 2760302.0179 | 1249079.9964
84 | 2760302.0179 | 1249079.9964 | 2760322.7821 | 1249091.2823
85 | 2760322.7821 | 1249091.2823 | 2760331.2285 | 1249095.8731 | 2760351.2872 | 1249110.9742
86 | 2760304.0381 | 1249019.8725 | 2760301.3961 | 1249018.2464

## bus_geodata
| x | y | coords
0 | 2760393.304 | 1249151.4192
1 | 2760380.544 | 1249163.0683
2 | 2760357.6333 | 1249115.7517
3 | 2760295.2678 | 1248885.4488
4 | 2760303.6731 | 1248871.5079
5 | 2760293.9493 | 1248887.6355
6 | 2760322.3096 | 1248840.5975
7 | 2760330.392 | 1248825.3341
8 | 2760338.7975 | 1248849.4333
9 | 2760274.1559 | 1248920.4647
10 | 2760251.338 | 1248948.5554
11 | 2760289.4058 | 1248930.3123
12 | 2760318.6295 | 1248818.3868
13 | 2760342.0376 | 1248851.1697
14 | 2760233.2675 | 1248963.9604
15 | 2760297.7414 | 1248935.6949
16 | 2760075.3919 | 1248876.3316
17 | 2760088.8452 | 1248861.7101
18 | 2760174.7736 | 1248986.1782
19 | 2760201.0216 | 1248985.6313
20 | 2760166.155 | 1248990.9725
21 | 2760207.014 | 1248991.9349
22 | 2760107.6506 | 1248841.2674
23 | 2760037.4356 | 1248816.2645
24 | 2760049.0221 | 1248800.8283
25 | 2760061.8775 | 1248783.7017
26 | 2760073.1137 | 1248768.4526
27 | 2760142.8245 | 1248782.8732
28 | 2760193.7514 | 1248920.0468
29 | 2760152.979 | 1248765.0229
30 | 2760086.3561 | 1248748.3291
31 | 2760098.1944 | 1248729.5152
32 | 2760118.8894 | 1248690.85
33 | 2760137.0662 | 1248699.9055
34 | 2760124.1247 | 1248668.6818
35 | 2760130.556 | 1248633.274
36 | 2760141.8865 | 1248639.2749
37 | 2760167.0061 | 1248599.2021
38 | 2760177.0857 | 1248605.0803
39 | 2760338.679 | 1248744.4547
40 | 2760332.7524 | 1248754.9921
41 | 2760354.7763 | 1248752.8609
42 | 2760321.9266 | 1248774.2401
43 | 2760365.7472 | 1248758.5899
44 | 2760310.2639 | 1248794.9758
45 | 2760360.914 | 1248767.7017
46 | 2760373.4089 | 1248745.1176
47 | 2760302.4661 | 1248808.8402
48 | 2760374.8483 | 1248775.7533
49 | 2760347.3825 | 1248793.2522
50 | 2760314.6452 | 1248816.0335
51 | 2760395.1928 | 1248768.166
52 | 2760375.9033 | 1248792.9219
53 | 2760402.5975 | 1248759.3401
54 | 2760376.4003 | 1248808.1915
55 | 2760378.4723 | 1248871.8479
56 | 2760372.1488 | 1248882.5502
57 | 2760377.7337 | 1248849.1557
58 | 2760360.5766 | 1248902.1356
59 | 2760376.784 | 1248819.9797
60 | 2760354.1189 | 1248913.0649
61 | 2760353.0896 | 1248914.807
62 | 2760341.3132 | 1248934.6157
63 | 2760341.2961 | 1248934.6441
64 | 2760316.9962 | 1248948.1286
65 | 2760306.5295 | 1248964.6733
66 | 2760340.8855 | 1248935.3249
67 | 2760320.5624 | 1248973.9058
68 | 2760295.5692 | 1248981.9959
69 | 2760323.4413 | 1248975.7999
70 | 2760281.7835 | 1249003.7839
71 | 2760280.6947 | 1249005.5047
72 | 2760296.0343 | 1249014.9463
73 | 2760253.83 | 1249036.9434
74 | 2760254.5101 | 1249038.3368
75 | 2760237.1765 | 1249014.9156
76 | 2760300.1353 | 1249017.4704
77 | 2760338.5469 | 1248985.7381
78 | 2760228.9643 | 1249024.6874
79 | 2760269.6937 | 1249060.6176
80 | 2760268.9646 | 1249080.5409
81 | 2760279.866 | 1249067.9562
82 | 2760290.3884 | 1249073.6754
83 | 2760302.0179 | 1249079.9964
84 | 2760322.7821 | 1249091.2823
85 | 2760351.2872 | 1249110.9742
86 | 2760301.3961 | 1249018.2464
87 | 2760304.0381 | 1249019.8725
88 | 2760274.1559 | 1248920.4647

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1