## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3253-1_1_3_node_23 | 0.4 | n |  | TRUE
1 | bus_LV_3253-1_1_3_node_24 | 0.4 | n |  | TRUE
2 | bus_LV_3253-1_1_3_node_25 | 0.4 | n |  | TRUE
3 | bus_LV_3253-1_1_3_node_26 | 0.4 | n |  | TRUE
4 | bus_LV_3253-1_1_3_node_27 | 0.4 | n |  | TRUE
5 | bus_LV_3253-1_1_3_node_39 | 0.4 | n |  | TRUE
6 | bus_LV_3253-1_1_3_node_40 | 0.4 | n |  | TRUE
7 | bus_LV_3253-1_1_3_node_57 | 0.4 | n |  | TRUE
8 | bus_LV_3253-1_1_3_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_3253-1_1_3_node_45 | 0.4 | n |  | TRUE
10 | bus_LV_3253-1_1_3_node_77 | 0.4 | n |  | TRUE
11 | bus_LV_3253-1_1_3_node_52 | 0.4 | n |  | TRUE
12 | bus_LV_3253-1_1_3_node_28 | 0.4 | n |  | TRUE
13 | bus_LV_3253-1_1_3_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_3253-1_1_3_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_3253-1_1_3_node_31 | 0.4 | n |  | TRUE
16 | bus_LV_3253-1_1_3_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_3253-1_1_3_node_50 | 0.4 | n |  | TRUE
18 | bus_LV_3253-1_1_3_node_66 | 0.4 | n |  | TRUE
19 | bus_LV_3253-1_1_3_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_3253-1_1_3_node_65 | 0.4 | n |  | TRUE
21 | bus_LV_3253-1_1_3_node_33 | 0.4 | n |  | TRUE
22 | bus_LV_3253-1_1_3_node_34 | 0.4 | n |  | TRUE
23 | bus_LV_3253-1_1_3_node_35 | 0.4 | n |  | TRUE
24 | bus_LV_3253-1_1_3_node_36 | 0.4 | n |  | TRUE
25 | bus_LV_3253-1_1_3_node_38 | 0.4 | n |  | TRUE
26 | bus_LV_3253-1_1_3_node_64 | 0.4 | n |  | TRUE
27 | bus_LV_3253-1_1_3_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_3253-1_1_3_node_60 | 0.4 | n |  | TRUE
29 | bus_LV_3253-1_1_3_node_91 | 0.4 | n |  | TRUE
30 | bus_LV_3253-1_1_3_node_193 | 0.4 | n |  | TRUE
31 | bus_LV_3253-1_1_3_node_63 | 0.4 | n |  | TRUE
32 | bus_LV_3253-1_1_3_node_194 | 0.4 | n |  | TRUE
33 | bus_LV_3253-1_1_3_node_59 | 0.4 | n |  | TRUE
34 | bus_LV_3253-1_1_3_node_190 | 0.4 | n |  | TRUE
35 | bus_LV_3253-1_1_3_node_89 | 0.4 | n |  | TRUE
36 | bus_LV_3253-1_1_3_node_195 | 0.4 | n |  | TRUE
37 | bus_LV_3253-1_1_3_node_78 | 0.4 | n |  | TRUE
38 | bus_LV_3253-1_1_3_node_76 | 0.4 | n |  | TRUE
39 | bus_LV_3253-1_1_3_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_3253-1_1_3_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_3253-1_1_3_node_43 | 0.4 | n |  | TRUE
42 | bus_LV_3253-1_1_3_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_3253-1_1_3_node_46 | 0.4 | n |  | TRUE
44 | bus_LV_3253-1_1_3_node_198 | 0.4 | n |  | TRUE
45 | bus_LV_3253-1_1_3_node_87 | 0.4 | n |  | TRUE
46 | bus_LV_3253-1_1_3_node_86 | 0.4 | n |  | TRUE
47 | bus_LV_3253-1_1_3_node_49 | 0.4 | n |  | TRUE
48 | bus_LV_3253-1_1_3_node_51 | 0.4 | n |  | TRUE
49 | bus_LV_3253-1_1_3_node_54 | 0.4 | n |  | TRUE
50 | bus_LV_3253-1_1_3_node_58 | 0.4 | n |  | TRUE
51 | bus_LV_3253-1_1_3_node_53 | 0.4 | n |  | TRUE
52 | bus_LV_3253-1_1_3_node_62 | 0.4 | n |  | TRUE
53 | bus_LV_3253-1_1_3_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_3253-1_1_3_node_73 | 0.4 | n |  | TRUE
55 | bus_LV_3253-1_1_3_node_67 | 0.4 | n |  | TRUE
56 | bus_LV_3253-1_1_3_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_3253-1_1_3_node_61 | 0.4 | n |  | TRUE
58 | bus_LV_3253-1_1_3_node_74 | 0.4 | n |  | TRUE
59 | bus_LV_3253-1_1_3_node_118 | 0.4 | n |  | TRUE
60 | bus_LV_3253-1_1_3_node_119 | 0.4 | n |  | TRUE
61 | bus_LV_3253-1_1_3_node_68 | 0.4 | n |  | TRUE
62 | bus_LV_3253-1_1_3_node_69 | 0.4 | n |  | TRUE
63 | bus_LV_3253-1_1_3_node_70 | 0.4 | n |  | TRUE
64 | bus_LV_3253-1_1_3_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_3253-1_1_3_node_72 | 0.4 | n |  | TRUE
66 | bus_LV_3253-1_1_3_node_83 | 0.4 | n |  | TRUE
67 | bus_LV_3253-1_1_3_node_80 | 0.4 | n |  | TRUE
68 | bus_LV_3253-1_1_3_node_85 | 0.4 | n |  | TRUE
69 | bus_LV_3253-1_1_3_node_84 | 0.4 | n |  | TRUE
70 | bus_LV_3253-1_1_3_node_79 | 0.4 | n |  | TRUE
71 | bus_LV_3253-1_1_3_node_75 | 0.4 | n |  | TRUE
72 | bus_LV_3253-1_1_3_node_81 | 0.4 | n |  | TRUE
73 | bus_LV_3253-1_1_3_node_82 | 0.4 | n |  | TRUE
74 | bus_LV_3253-1_1_3_node_88 | 0.4 | n |  | TRUE
75 | bus_LV_3253-1_1_3_node_90 | 0.4 | n |  | TRUE
76 | bus_LV_3253-1_1_3_node_93 | 0.4 | n |  | TRUE
77 | bus_LV_3253-1_1_3_node_105 | 0.4 | n |  | TRUE
78 | bus_LV_3253-1_1_3_node_107 | 0.4 | n |  | TRUE
79 | bus_LV_3253-1_1_3_node_109 | 0.4 | n |  | TRUE
80 | bus_LV_3253-1_1_3_node_110 | 0.4 | n |  | TRUE
81 | bus_LV_3253-1_1_3_node_128 | 0.4 | n |  | TRUE
82 | bus_LV_3253-1_1_3_node_161 | 0.4 | n |  | TRUE
83 | bus_LV_3253-1_1_3_node_129 | 0.4 | n |  | TRUE
84 | bus_LV_3253-1_1_3_node_130 | 0.4 | n |  | TRUE
85 | bus_LV_3253-1_1_3_node_159 | 0.4 | n |  | TRUE
86 | bus_LV_3253-1_1_3_node_121 | 0.4 | n |  | TRUE
87 | bus_LV_3253-1_1_3_node_122 | 0.4 | n |  | TRUE
88 | bus_LV_3253-1_1_3_node_135 | 0.4 | n |  | TRUE
89 | bus_LV_3253-1_1_3_node_149 | 0.4 | n |  | TRUE
90 | bus_LV_3253-1_1_3_node_162 | 0.4 | n |  | TRUE
91 | bus_LV_3253-1_1_3_node_158 | 0.4 | n |  | TRUE
92 | bus_LV_3253-1_1_3_node_160 | 0.4 | n |  | TRUE
93 | bus_LV_3253-1_1_3_node_176 | 0.4 | n |  | TRUE
94 | bus_LV_3253-1_1_3_node_174 | 0.4 | n |  | TRUE
95 | bus_LV_3253-1_1_3_node_168 | 0.4 | n |  | TRUE
96 | bus_LV_3253-1_1_3_node_169 | 0.4 | n |  | TRUE
97 | bus_LV_3253-1_1_3_node_170 | 0.4 | n |  | TRUE
98 | bus_LV_3253-1_1_3_node_175 | 0.4 | n |  | TRUE
99 | bus_MV_51_0_node_91 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3253-1_1_3_load_23 | 0 | 0.0038138 | 0.00095582 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3253-1_1_3_load_24 | 1 | 0.0038852 | 0.00097373 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3253-1_1_3_load_25 | 2 | 0.0040753 | 0.0010214 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3253-1_1_3_load_27 | 4 | 0.004039 | 0.0010123 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3253-1_1_3_load_40 | 6 | 0.0027383 | 0.00068629 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3253-1_1_3_load_57 | 7 | 0.0020873 | 0.00052314 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3253-1_1_3_load_47 | 8 | 0.0034472 | 0.00086394 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3253-1_1_3_load_45 | 9 | 0.0049043 | 0.0012291 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3253-1_1_3_load_77 | 10 | 0.0033159 | 0.00083103 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3253-1_1_3_load_28 | 12 | 0.0025463 | 0.00063816 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3253-1_1_3_load_29 | 13 | 0.0007266 | 0.0001821 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3253-1_1_3_load_31 | 15 | 0.00497 | 0.0012456 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3253-1_1_3_load_32 | 16 | 0.0012106 | 0.00030341 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3253-1_1_3_load_66 | 18 | 0.0022464 | 0.00056299 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3253-1_1_3_load_48 | 19 | 0.0018731 | 0.00046946 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3253-1_1_3_load_33 | 21 | 0.0078242 | 0.0019609 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3253-1_1_3_load_34 | 22 | 0.0013348 | 0.00033454 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3253-1_1_3_load_36 | 24 | 0.0016547 | 0.0004147 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3253-1_1_3_load_38 | 25 | 0.0020458 | 0.00051271 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3253-1_1_3_load_64 | 26 | 0.0027554 | 0.00069058 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3253-1_1_3_load_60 | 28 | 0.005639 | 0.0014133 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3253-1_1_3_load_63 | 31 | 0.0025544 | 0.00064019 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3253-1_1_3_load_194 | 32 | 0.0018437 | 0.00046208 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3253-1_1_3_load_59 | 33 | 0.0067544 | 0.0016928 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3253-1_1_3_load_190 | 34 | 0.0037777 | 0.00094677 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3253-1_1_3_load_89 | 35 | 0.006324 | 0.0015849 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3253-1_1_3_load_195 | 36 | 0.0015687 | 0.00039316 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3253-1_1_3_load_78 | 37 | 0.0036643 | 0.00091836 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3253-1_1_3_load_76 | 38 | 0.0027967 | 0.00070092 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3253-1_1_3_load_41 | 39 | 0.00068887 | 0.00017265 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3253-1_1_3_load_46 | 43 | 0.00074834 | 0.00018755 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3253-1_1_3_load_198 | 44 | 0.0041663 | 0.0010442 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3253-1_1_3_load_87 | 45 | 0.00070154 | 0.00017582 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3253-1_1_3_load_86 | 46 | 0.00085658 | 0.00021468 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3253-1_1_3_load_49 | 47 | 0.0064062 | 0.0016055 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3253-1_1_3_load_51 | 48 | 0.0032054 | 0.00080335 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3253-1_1_3_load_54 | 49 | 0.0050588 | 0.0012679 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3253-1_1_3_load_58 | 50 | 0.0029947 | 0.00075055 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3253-1_1_3_load_62 | 52 | 0.0023443 | 0.00058753 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3253-1_1_3_load_55 | 53 | 0.0069575 | 0.0017437 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3253-1_1_3_load_73 | 54 | 0.002593 | 0.00064986 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3253-1_1_3_load_67 | 55 | 0.0012176 | 0.00030516 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3253-1_1_3_load_56 | 56 | 0.0033739 | 0.00084557 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3253-1_1_3_load_74 | 58 | 0.0070455 | 0.0017658 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3253-1_1_3_load_119 | 60 | 0.0011281 | 0.00028273 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3253-1_1_3_load_68 | 61 | 0.0038821 | 0.00097295 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3253-1_1_3_load_69 | 62 | 0.0037749 | 0.00094608 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3253-1_1_3_load_70 | 63 | 0.0032619 | 0.0008175 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3253-1_1_3_load_72 | 65 | 0.0031724 | 0.00079509 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3253-1_1_3_load_80 | 67 | 0.0016047 | 0.00040218 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3253-1_1_3_load_85 | 68 | 0.004545 | 0.0011391 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3253-1_1_3_load_84 | 69 | 0.0011983 | 0.00030033 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3253-1_1_3_load_79 | 70 | 0.0014723 | 0.000369 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3253-1_1_3_load_75 | 71 | 0.015576 | 0.0039038 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3253-1_1_3_load_82 | 73 | 0.001054 | 0.00026417 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3253-1_1_3_load_88 | 74 | 0.014245 | 0.0035701 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3253-1_1_3_load_93 | 76 | 0.0012391 | 0.00031056 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3253-1_1_3_load_105 | 77 | 0.0048817 | 0.0012235 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3253-1_1_3_load_109 | 79 | 0.0031283 | 0.00078401 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3253-1_1_3_load_110 | 80 | 0.0016316 | 0.00040893 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3253-1_1_3_load_161 | 82 | 0.0016317 | 0.00040895 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3253-1_1_3_load_129 | 83 | 0.0033714 | 0.00084494 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3253-1_1_3_load_130 | 84 | 0.0042552 | 0.0010665 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3253-1_1_3_load_121 | 86 | 0.0019256 | 0.0004826 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3253-1_1_3_load_122 | 87 | 0.0026906 | 0.00067434 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3253-1_1_3_load_162 | 90 | 0.0016315 | 0.0004089 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3253-1_1_3_load_158 | 91 | 0.0016328 | 0.00040922 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3253-1_1_3_load_160 | 92 | 0.0016315 | 0.00040889 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3253-1_1_3_load_176 | 93 | 0.0016326 | 0.00040916 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3253-1_1_3_load_174 | 94 | 0.001633 | 0.00040927 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3253-1_1_3_load_168 | 95 | 0.0016328 | 0.00040921 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3253-1_1_3_load_169 | 96 | 0.0016321 | 0.00040905 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3253-1_1_3_load_170 | 97 | 0.0016309 | 0.00040874 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3253-1_1_3_load_175 | 98 | 0.0016313 | 0.00040884 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 47 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3253-1_1_3_line_0 |  | 0 | 1 | 0.018663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3253-1_1_3_line_1 |  | 0 | 2 | 0.024691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3253-1_1_3_line_2 |  | 1 | 3 | 0.0029195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3253-1_1_3_line_3 |  | 2 | 4 | 0.035855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3253-1_1_3_line_4 |  | 3 | 5 | 0.029982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3253-1_1_3_line_5 |  | 3 | 6 | 0.011809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3253-1_1_3_line_6 |  | 4 | 7 | 0.005932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3253-1_1_3_line_7 |  | 5 | 8 | 0.014362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3253-1_1_3_line_8 |  | 5 | 9 | 0.023421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3253-1_1_3_line_9 |  | 6 | 10 | 0.022746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3253-1_1_3_line_10 |  | 7 | 11 | 0.011548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3253-1_1_3_line_11 |  | 8 | 37 | 0.002989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3253-1_1_3_line_12 |  | 10 | 38 | 0.017907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3253-1_1_3_line_13 |  | 11 | 50 | 0.0074246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3253-1_1_3_line_14 |  | 11 | 17 | 0.030192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3253-1_1_3_line_15 |  | 12 | 13 | 0.0017412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3253-1_1_3_line_16 |  | 12 | 14 | 0.0091523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3253-1_1_3_line_17 |  | 14 | 15 | 0.0058816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3253-1_1_3_line_18 |  | 14 | 16 | 0.01645 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3253-1_1_3_line_19 |  | 15 | 17 | 0.037736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3253-1_1_3_line_20 |  | 16 | 18 | 0.020543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3253-1_1_3_line_21 |  | 17 | 19 | 0.016174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_3253-1_1_3_line_22 |  | 18 | 20 | 0.019659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3253-1_1_3_line_23 |  | 19 | 47 | 0.034009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
24 | LV_3253-1_1_3_line_24 |  | 20 | 55 | 0.0045259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3253-1_1_3_line_25 |  | 20 | 51 | 0.033568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3253-1_1_3_line_26 |  | 21 | 22 | 0.022036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3253-1_1_3_line_27 |  | 21 | 23 | 0.0077669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3253-1_1_3_line_28 |  | 22 | 24 | 0.016424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3253-1_1_3_line_29 |  | 23 | 25 | 0.015809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3253-1_1_3_line_30 |  | 24 | 26 | 0.02 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3253-1_1_3_line_31 |  | 25 | 30 | 0.018953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3253-1_1_3_line_32 |  | 26 | 31 | 0.0017591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3253-1_1_3_line_33 |  | 27 | 28 | 0.0052453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3253-1_1_3_line_34 |  | 27 | 29 | 0.01007 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3253-1_1_3_line_35 |  | 28 | 33 | 0.026991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3253-1_1_3_line_36 |  | 29 | 34 | 0.0025681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3253-1_1_3_line_37 |  | 29 | 35 | 0.021875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3253-1_1_3_line_38 |  | 30 | 36 | 0.027964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3253-1_1_3_line_39 |  | 30 | 32 | 0.013306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3253-1_1_3_line_40 |  | 31 | 52 | 0.031307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3253-1_1_3_line_41 |  | 33 | 57 | 0.023709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3253-1_1_3_line_42 |  | 35 | 74 | 0.017454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3253-1_1_3_line_43 |  | 38 | 65 | 0.0040646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3253-1_1_3_line_44 |  | 39 | 40 | 0.012549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3253-1_1_3_line_45 |  | 39 | 41 | 0.012711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3253-1_1_3_line_46 |  | 40 | 42 | 0.010624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3253-1_1_3_line_47 |  | 41 | 43 | 0.023329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3253-1_1_3_line_48 |  | 42 | 44 | 0.010655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3253-1_1_3_line_49 |  | 43 | 45 | 0.026199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3253-1_1_3_line_50 |  | 45 | 46 | 0.02374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3253-1_1_3_line_51 |  | 46 | 73 | 0.019361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3253-1_1_3_line_52 |  | 47 | 48 | 0.020532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3253-1_1_3_line_53 |  | 48 | 49 | 0.0078594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3253-1_1_3_line_54 |  | 49 | 53 | 0.017585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3253-1_1_3_line_55 |  | 50 | 54 | 0.013575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3253-1_1_3_line_56 |  | 51 | 52 | 0.01917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3253-1_1_3_line_57 |  | 53 | 56 | 0.030103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3253-1_1_3_line_58 |  | 54 | 58 | 0.00027827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3253-1_1_3_line_59 |  | 55 | 59 | 0.024404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3253-1_1_3_line_60 |  | 56 | 57 | 0.017019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3253-1_1_3_line_61 |  | 58 | 71 | 0.01692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3253-1_1_3_line_62 |  | 59 | 60 | 0.016757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3253-1_1_3_line_63 |  | 60 | 86 | 0.014534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3253-1_1_3_line_64 |  | 61 | 62 | 0.0073182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3253-1_1_3_line_65 |  | 61 | 63 | 0.012624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3253-1_1_3_line_66 |  | 62 | 64 | 0.029806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3253-1_1_3_line_67 |  | 63 | 65 | 0.013354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3253-1_1_3_line_68 |  | 64 | 66 | 0.02042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3253-1_1_3_line_69 |  | 64 | 67 | 0.014788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3253-1_1_3_line_70 |  | 66 | 68 | 0.05242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3253-1_1_3_line_71 |  | 66 | 69 | 0.0057191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3253-1_1_3_line_72 |  | 67 | 70 | 0.032157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3253-1_1_3_line_73 |  | 70 | 72 | 0.010611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3253-1_1_3_line_74 |  | 72 | 73 | 0.029535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3253-1_1_3_line_75 |  | 74 | 75 | 0.010506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3253-1_1_3_line_76 |  | 75 | 76 | 0.023338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3253-1_1_3_line_77 |  | 77 | 78 | 0.014492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3253-1_1_3_line_78 |  | 78 | 79 | 0.028595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3253-1_1_3_line_79 |  | 78 | 80 | 0.05095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3253-1_1_3_line_80 |  | 79 | 81 | 0.01376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3253-1_1_3_line_81 |  | 80 | 82 | 0.0017387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3253-1_1_3_line_82 |  | 81 | 83 | 0.005546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3253-1_1_3_line_83 |  | 81 | 84 | 0.02395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3253-1_1_3_line_84 |  | 82 | 85 | 0.016988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3253-1_1_3_line_85 |  | 85 | 90 | 0.013438 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3253-1_1_3_line_86 |  | 85 | 91 | 0.01181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3253-1_1_3_line_87 |  | 85 | 89 | 0.028216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3253-1_1_3_line_88 |  | 86 | 87 | 0.00075336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3253-1_1_3_line_89 |  | 87 | 88 | 0.020027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3253-1_1_3_line_90 |  | 88 | 89 | 0.06324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3253-1_1_3_line_91 |  | 90 | 93 | 0.0082884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3253-1_1_3_line_92 |  | 91 | 92 | 0.010474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3253-1_1_3_line_93 |  | 93 | 94 | 0.0042269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3253-1_1_3_line_94 |  | 94 | 98 | 0.014374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3253-1_1_3_line_95 |  | 95 | 96 | 0.0042699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3253-1_1_3_line_96 |  | 96 | 97 | 0.008244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3253-1_1_3_line_97 |  | 97 | 98 | 0.0042689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3253-1_1_3_trafo_49 | 0.63 MVA 20/0.4 kV | 99 | 47 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2760347.1274 | 1251036.4139 | 2760346.2012 | 1251038.2146 | 2760344.2091 | 1251046.7916 | 2760344.0905 | 1251054.6234
1 | 2760363.4665 | 1251018.4572 | 2760350.8335 | 1251029.2086 | 2760347.1274 | 1251036.4139
2 | 2760344.0463 | 1251057.5425 | 2760344.0905 | 1251054.6234
3 | 2760395.2183 | 1251008.6587 | 2760384.3303 | 1251006.1027 | 2760377.762 | 1251007.671 | 2760366.729 | 1251015.6806 | 2760363.4665 | 1251018.4572
4 | 2760344.0463 | 1251057.5425 | 2760340.7318 | 1251087.3385
5 | 2760344.0463 | 1251057.5425 | 2760355.6803 | 1251059.5679
6 | 2760400.9933 | 1251010.0144 | 2760395.2183 | 1251008.6587
7 | 2760340.7318 | 1251087.3385 | 2760355.0223 | 1251088.7659
8 | 2760340.7318 | 1251087.3385 | 2760317.3225 | 1251086.5857
9 | 2760355.6803 | 1251059.5679 | 2760378.089 | 1251063.4691
10 | 2760412.2353 | 1251012.6535 | 2760400.9933 | 1251010.0144
11 | 2760357.9965 | 1251089.063 | 2760355.0223 | 1251088.7659
12 | 2760395.6011 | 1251067.0527 | 2760392.2415 | 1251065.9329 | 2760378.089 | 1251063.4691
13 | 2760412.2353 | 1251012.6535 | 2760417.3773 | 1251018.0092
14 | 2760412.2353 | 1251012.6535 | 2760416.6985 | 1251010.7279 | 2760422.8608 | 1250996.269 | 2760423.2499 | 1250986.6475
15 | 2760372.3698 | 1250968.1555 | 2760373.9032 | 1250968.9804
16 | 2760381.9631 | 1250973.3166 | 2760373.9032 | 1250968.9804
17 | 2760381.9631 | 1250973.3166 | 2760387.3317 | 1250975.7189
18 | 2760381.9631 | 1250973.3166 | 2760387.7859 | 1250957.9316
19 | 2760423.2499 | 1250986.6475 | 2760400.881 | 1250981.7816 | 2760387.3317 | 1250975.7189
20 | 2760387.7859 | 1250957.9316 | 2760393.5968 | 1250942.5782 | 2760396.7821 | 1250939.9543
21 | 2760423.2499 | 1250986.6475 | 2760438.7533 | 1250991.257
22 | 2760407.3532 | 1250923.5423 | 2760398.7343 | 1250938.3463 | 2760396.7821 | 1250939.9543
23 | 2760438.7533 | 1250991.257 | 2760457.207 | 1250996.7437 | 2760469.6663 | 1251004.6505
24 | 2760407.3532 | 1250923.5423 | 2760403.3925 | 1250921.3522
25 | 2760436.967 | 1250939.5156 | 2760407.3532 | 1250923.5423
26 | 2760514.2334 | 1250982.9944 | 2760533.4852 | 1250993.7151
27 | 2760540.271 | 1250997.4939 | 2760533.4852 | 1250993.7151
28 | 2760514.2334 | 1250982.9944 | 2760499.8842 | 1250975.0038
29 | 2760540.271 | 1250997.4939 | 2760550.3889 | 1250985.3462
30 | 2760482.4873 | 1250965.1378 | 2760498.3644 | 1250974.1575 | 2760499.8842 | 1250975.0038
31 | 2760565.7397 | 1250976.3402 | 2760556.5414 | 1250977.9593 | 2760550.3889 | 1250985.3462
32 | 2760482.4873 | 1250965.1378 | 2760480.9578 | 1250964.2688
33 | 2760581.28 | 1251022.4412 | 2760578.5558 | 1251026.5271 | 2760578.2464 | 1251026.4
34 | 2760581.28 | 1251022.4412 | 2760589.9783 | 1251027.5599
35 | 2760578.2464 | 1251026.4 | 2760566.1707 | 1251021.442 | 2760559.3539 | 1251033.5982
36 | 2760589.9783 | 1251027.5599 | 2760592.2018 | 1251028.8449
37 | 2760589.9783 | 1251027.5599 | 2760603.5658 | 1251010.4161
38 | 2760565.7397 | 1250976.3402 | 2760567.0527 | 1250976.1089 | 2760584.6682 | 1250956.1368
39 | 2760565.7397 | 1250976.3402 | 2760568.8575 | 1250982.5309 | 2760571.8271 | 1250988.1713
40 | 2760453.6865 | 1250948.8928 | 2760469.8076 | 1250957.9345 | 2760480.9578 | 1250964.2688
41 | 2760548.2484 | 1251054.5455 | 2760558.8291 | 1251034.5341 | 2760559.3539 | 1251033.5982
42 | 2760603.5658 | 1251010.4161 | 2760614.4071 | 1250996.7375
43 | 2760395.6011 | 1251067.0527 | 2760399.4571 | 1251068.338
44 | 2760280.9053 | 1251116.0493 | 2760285.1461 | 1251117.0317 | 2760293.3296 | 1251117.4799
45 | 2760306.0217 | 1251118.1752 | 2760293.3296 | 1251117.4799
46 | 2760274.4835 | 1251107.745 | 2760277.9658 | 1251113.5895 | 2760280.9053 | 1251116.0493
47 | 2760306.0217 | 1251118.1752 | 2760329.2372 | 1251120.4758
48 | 2760274.4835 | 1251107.745 | 2760273.6532 | 1251097.1229
49 | 2760329.2372 | 1251120.4758 | 2760334.5934 | 1251121.0065 | 2760355.1181 | 1251124.4831
50 | 2760355.1181 | 1251124.4831 | 2760360.0734 | 1251125.3225 | 2760378.4087 | 1251129.0669
51 | 2760396.4111 | 1251136.1916 | 2760378.4087 | 1251129.0669 | 2760378.4087 | 1251129.0669
52 | 2760469.6663 | 1251004.6505 | 2760487.0023 | 1251015.652
53 | 2760493.6382 | 1251019.8632 | 2760487.0023 | 1251015.652
54 | 2760493.6382 | 1251019.8632 | 2760497.4303 | 1251022.2697 | 2760508.3985 | 1251029.4216
55 | 2760429.3242 | 1251024.4562 | 2760417.3773 | 1251018.0092
56 | 2760436.967 | 1250939.5156 | 2760453.6865 | 1250948.8928
57 | 2760508.3985 | 1251029.4216 | 2760533.6145 | 1251045.8638
58 | 2760429.3242 | 1251024.4562 | 2760429.5691 | 1251024.5883
59 | 2760382.0365 | 1250909.543 | 2760403.3925 | 1250921.3522
60 | 2760548.2484 | 1251054.5455 | 2760536.0685 | 1251047.4639 | 2760533.6145 | 1251045.8638
61 | 2760444.4594 | 1251032.6237 | 2760429.5691 | 1251024.5883
62 | 2760382.0365 | 1250909.543 | 2760387.2125 | 1250899.7065 | 2760390.8176 | 1250895.3673
63 | 2760390.8176 | 1250895.3673 | 2760400.1052 | 1250884.1885
64 | 2760423.3649 | 1251078.4091 | 2760428.2327 | 1251080.6664 | 2760429.9454 | 1251081.6039
65 | 2760423.3649 | 1251078.4091 | 2760411.9126 | 1251073.0986
66 | 2760452.2769 | 1251097.0005 | 2760453.6492 | 1251094.5797 | 2760429.9454 | 1251081.6039
67 | 2760399.4571 | 1251068.338 | 2760407.2423 | 1251070.9329 | 2760411.9126 | 1251073.0986
68 | 2760452.2769 | 1251097.0005 | 2760469.6028 | 1251107.8918
69 | 2760452.2769 | 1251097.0005 | 2760444.979 | 1251109.8626
70 | 2760469.6028 | 1251107.8918 | 2760486.2584 | 1251085.8315 | 2760501.1679 | 1251095.8677 | 2760507.9506 | 1251095.3064
71 | 2760469.6028 | 1251107.8918 | 2760473.1524 | 1251112.3761
72 | 2760429.1096 | 1251137.8313 | 2760444.979 | 1251109.8626
73 | 2760423.8732 | 1251147.06 | 2760429.1096 | 1251137.8313
74 | 2760423.8732 | 1251147.06 | 2760396.4111 | 1251136.1916
75 | 2760620.933 | 1250988.5036 | 2760614.4071 | 1250996.7375
76 | 2760620.933 | 1250988.5036 | 2760641.3863 | 1250999.7431
77 | 2760529.0567 | 1250882.3625 | 2760542.137 | 1250876.1225
78 | 2760529.0567 | 1250882.3625 | 2760531.6813 | 1250891.1425 | 2760517.0993 | 1250903.9845
79 | 2760529.0567 | 1250882.3625 | 2760522.1683 | 1250874.5569 | 2760492.5127 | 1250846.9165
80 | 2760506.7727 | 1250913.0789 | 2760517.0993 | 1250903.9845
81 | 2760491.2409 | 1250845.7311 | 2760492.5127 | 1250846.9165
82 | 2760506.7727 | 1250913.0789 | 2760502.6021 | 1250916.7475
83 | 2760490.0709 | 1250895.8648 | 2760506.7727 | 1250913.0789
84 | 2760476.6615 | 1250837.4315 | 2760487.2995 | 1250842.0575 | 2760491.2409 | 1250845.7311
85 | 2760476.6615 | 1250837.4315 | 2760467.9246 | 1250847.6415
86 | 2760476.6615 | 1250837.4315 | 2760484.2719 | 1250828.4009
87 | 2760454.495 | 1250820.0582 | 2760473.9442 | 1250836.2456 | 2760476.6615 | 1250837.4315
88 | 2760400.5866 | 1250883.609 | 2760400.1052 | 1250884.1885
89 | 2760413.3844 | 1250868.2052 | 2760400.5866 | 1250883.609
90 | 2760454.495 | 1250820.0582 | 2760413.3844 | 1250868.2052
91 | 2760467.9246 | 1250847.6415 | 2760462.5358 | 1250853.939
92 | 2760491.0214 | 1250820.392 | 2760484.2719 | 1250828.4009
93 | 2760459.7876 | 1250857.1506 | 2760462.5358 | 1250853.939
94 | 2760459.7876 | 1250857.1506 | 2760450.4424 | 1250868.0715
95 | 2760439.5308 | 1250880.8231 | 2760442.307 | 1250877.5788
96 | 2760447.667 | 1250871.315 | 2760442.307 | 1250877.5788
97 | 2760447.667 | 1250871.315 | 2760450.4424 | 1250868.0715

## bus_geodata
| x | y | coords
0 | 2760347.1274 | 1251036.4139
1 | 2760344.0905 | 1251054.6234
2 | 2760363.4665 | 1251018.4572
3 | 2760344.0463 | 1251057.5425
4 | 2760395.2183 | 1251008.6587
5 | 2760340.7318 | 1251087.3385
6 | 2760355.6803 | 1251059.5679
7 | 2760400.9933 | 1251010.0144
8 | 2760355.0223 | 1251088.7659
9 | 2760317.3225 | 1251086.5857
10 | 2760378.089 | 1251063.4691
11 | 2760412.2353 | 1251012.6535
12 | 2760373.9032 | 1250968.9804
13 | 2760372.3698 | 1250968.1555
14 | 2760381.9631 | 1250973.3166
15 | 2760387.3317 | 1250975.7189
16 | 2760387.7859 | 1250957.9316
17 | 2760423.2499 | 1250986.6475
18 | 2760396.7821 | 1250939.9543
19 | 2760438.7533 | 1250991.257
20 | 2760407.3532 | 1250923.5423
21 | 2760533.4852 | 1250993.7151
22 | 2760514.2334 | 1250982.9944
23 | 2760540.271 | 1250997.4939
24 | 2760499.8842 | 1250975.0038
25 | 2760550.3889 | 1250985.3462
26 | 2760482.4873 | 1250965.1378
27 | 2760581.28 | 1251022.4412
28 | 2760578.2464 | 1251026.4
29 | 2760589.9783 | 1251027.5599
30 | 2760565.7397 | 1250976.3402
31 | 2760480.9578 | 1250964.2688
32 | 2760571.8271 | 1250988.1713
33 | 2760559.3539 | 1251033.5982
34 | 2760592.2018 | 1251028.8449
35 | 2760603.5658 | 1251010.4161
36 | 2760584.6682 | 1250956.1368
37 | 2760357.9965 | 1251089.063
38 | 2760395.6011 | 1251067.0527
39 | 2760293.3296 | 1251117.4799
40 | 2760280.9053 | 1251116.0493
41 | 2760306.0217 | 1251118.1752
42 | 2760274.4835 | 1251107.745
43 | 2760329.2372 | 1251120.4758
44 | 2760273.6532 | 1251097.1229
45 | 2760355.1181 | 1251124.4831
46 | 2760378.4087 | 1251129.0669
47 | 2760469.6663 | 1251004.6505
48 | 2760487.0023 | 1251015.652
49 | 2760493.6382 | 1251019.8632
50 | 2760417.3773 | 1251018.0092
51 | 2760436.967 | 1250939.5156
52 | 2760453.6865 | 1250948.8928
53 | 2760508.3985 | 1251029.4216
54 | 2760429.3242 | 1251024.4562
55 | 2760403.3925 | 1250921.3522
56 | 2760533.6145 | 1251045.8638
57 | 2760548.2484 | 1251054.5455
58 | 2760429.5691 | 1251024.5883
59 | 2760382.0365 | 1250909.543
60 | 2760390.8176 | 1250895.3673
61 | 2760423.3649 | 1251078.4091
62 | 2760429.9454 | 1251081.6039
63 | 2760411.9126 | 1251073.0986
64 | 2760452.2769 | 1251097.0005
65 | 2760399.4571 | 1251068.338
66 | 2760469.6028 | 1251107.8918
67 | 2760444.979 | 1251109.8626
68 | 2760507.9506 | 1251095.3064
69 | 2760473.1524 | 1251112.3761
70 | 2760429.1096 | 1251137.8313
71 | 2760444.4594 | 1251032.6237
72 | 2760423.8732 | 1251147.06
73 | 2760396.4111 | 1251136.1916
74 | 2760614.4071 | 1250996.7375
75 | 2760620.933 | 1250988.5036
76 | 2760641.3863 | 1250999.7431
77 | 2760542.137 | 1250876.1225
78 | 2760529.0567 | 1250882.3625
79 | 2760517.0993 | 1250903.9845
80 | 2760492.5127 | 1250846.9165
81 | 2760506.7727 | 1250913.0789
82 | 2760491.2409 | 1250845.7311
83 | 2760502.6021 | 1250916.7475
84 | 2760490.0709 | 1250895.8648
85 | 2760476.6615 | 1250837.4315
86 | 2760400.1052 | 1250884.1885
87 | 2760400.5866 | 1250883.609
88 | 2760413.3844 | 1250868.2052
89 | 2760454.495 | 1250820.0582
90 | 2760467.9246 | 1250847.6415
91 | 2760484.2719 | 1250828.4009
92 | 2760491.0214 | 1250820.392
93 | 2760462.5358 | 1250853.939
94 | 2760459.7876 | 1250857.1506
95 | 2760439.5308 | 1250880.8231
96 | 2760442.307 | 1250877.5788
97 | 2760447.667 | 1250871.315
98 | 2760450.4424 | 1250868.0716
99 | 2760423.2499 | 1250986.6475

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1