## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3273-13_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3273-13_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3273-13_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3273-13_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3273-13_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3273-13_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3273-13_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3273-13_0_3_node_20 | 0.4 | n |  | TRUE
8 | bus_LV_3273-13_0_3_node_29 | 0.4 | n |  | TRUE
9 | bus_LV_3273-13_0_3_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_3273-13_0_3_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_3273-13_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_3273-13_0_3_node_17 | 0.4 | n |  | TRUE
13 | bus_LV_3273-13_0_3_node_30 | 0.4 | n |  | TRUE
14 | bus_LV_3273-13_0_3_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_3273-13_0_3_node_33 | 0.4 | n |  | TRUE
16 | bus_LV_3273-13_0_3_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_3273-13_0_3_node_31 | 0.4 | n |  | TRUE
18 | bus_LV_3273-13_0_3_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_3273-13_0_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_3273-13_0_3_node_25 | 0.4 | n |  | TRUE
21 | bus_LV_3273-13_0_3_node_23 | 0.4 | n |  | TRUE
22 | bus_LV_3273-13_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_3273-13_0_3_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_3273-13_0_3_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_3273-13_0_3_node_16 | 0.4 | n |  | TRUE
26 | bus_LV_3273-13_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_3273-13_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_3273-13_0_3_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_3273-13_0_3_node_22 | 0.4 | n |  | TRUE
30 | bus_LV_3273-13_0_3_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_3273-13_0_3_node_32 | 0.4 | n |  | TRUE
32 | bus_LV_3273-13_0_3_node_37 | 0.4 | n |  | TRUE
33 | bus_LV_3273-13_0_3_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_3273-13_0_3_node_36 | 0.4 | n |  | TRUE
35 | bus_LV_3273-13_0_3_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_3273-13_0_3_node_35 | 0.4 | n |  | TRUE
37 | bus_LV_3273-13_0_3_node_39 | 0.4 | n |  | TRUE
38 | bus_LV_3273-13_0_3_node_40 | 0.4 | n |  | TRUE
39 | bus_LV_3273-13_0_3_node_41 | 0.4 | n |  | TRUE
40 | bus_LV_3273-13_0_3_node_42 | 0.4 | n |  | TRUE
41 | bus_LV_3273-13_0_3_node_134 | 0.4 | n |  | TRUE
42 | bus_LV_3273-13_0_3_node_43 | 0.4 | n |  | TRUE
43 | bus_LV_3273-13_0_3_node_135 | 0.4 | n |  | TRUE
44 | bus_LV_3273-13_0_3_node_44 | 0.4 | n |  | TRUE
45 | bus_LV_3273-13_0_3_node_133 | 0.4 | n |  | TRUE
46 | bus_LV_3273-13_0_3_node_132 | 0.4 | n |  | TRUE
47 | bus_LV_3273-13_0_3_node_137 | 0.4 | n |  | TRUE
48 | bus_LV_3273-13_0_3_node_130 | 0.4 | n |  | TRUE
49 | bus_LV_3273-13_0_3_node_47 | 0.4 | n |  | TRUE
50 | bus_LV_3273-13_0_3_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_3273-13_0_3_node_49 | 0.4 | n |  | TRUE
52 | bus_LV_3273-13_0_3_node_50 | 0.4 | n |  | TRUE
53 | bus_LV_3273-13_0_3_node_51 | 0.4 | n |  | TRUE
54 | bus_LV_3273-13_0_3_node_52 | 0.4 | n |  | TRUE
55 | bus_LV_3273-13_0_3_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_3273-13_0_3_node_60 | 0.4 | n |  | TRUE
57 | bus_LV_3273-13_0_3_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_3273-13_0_3_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_3273-13_0_3_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_3273-13_0_3_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_3273-13_0_3_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_3273-13_0_3_node_67 | 0.4 | n |  | TRUE
63 | bus_LV_3273-13_0_3_node_68 | 0.4 | n |  | TRUE
64 | bus_LV_3273-13_0_3_node_69 | 0.4 | n |  | TRUE
65 | bus_LV_3273-13_0_3_node_58 | 0.4 | n |  | TRUE
66 | bus_LV_3273-13_0_3_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_3273-13_0_3_node_65 | 0.4 | n |  | TRUE
68 | bus_LV_3273-13_0_3_node_66 | 0.4 | n |  | TRUE
69 | bus_LV_3273-13_0_3_node_62 | 0.4 | n |  | TRUE
70 | bus_LV_3273-13_0_3_node_63 | 0.4 | n |  | TRUE
71 | bus_LV_3273-13_0_3_node_64 | 0.4 | n |  | TRUE
72 | bus_LV_3273-13_0_3_node_76 | 0.4 | n |  | TRUE
73 | bus_LV_3273-13_0_3_node_95 | 0.4 | n |  | TRUE
74 | bus_LV_3273-13_0_3_node_77 | 0.4 | n |  | TRUE
75 | bus_LV_3273-13_0_3_node_94 | 0.4 | n |  | TRUE
76 | bus_LV_3273-13_0_3_node_71 | 0.4 | n |  | TRUE
77 | bus_LV_3273-13_0_3_node_72 | 0.4 | n |  | TRUE
78 | bus_LV_3273-13_0_3_node_73 | 0.4 | n |  | TRUE
79 | bus_LV_3273-13_0_3_node_74 | 0.4 | n |  | TRUE
80 | bus_LV_3273-13_0_3_node_75 | 0.4 | n |  | TRUE
81 | bus_LV_3273-13_0_3_node_116 | 0.4 | n |  | TRUE
82 | bus_LV_3273-13_0_3_node_117 | 0.4 | n |  | TRUE
83 | bus_LV_3273-13_0_3_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_3273-13_0_3_node_79 | 0.4 | n |  | TRUE
85 | bus_LV_3273-13_0_3_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_3273-13_0_3_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_3273-13_0_3_node_92 | 0.4 | n |  | TRUE
88 | bus_LV_3273-13_0_3_node_91 | 0.4 | n |  | TRUE
89 | bus_LV_3273-13_0_3_node_82 | 0.4 | n |  | TRUE
90 | bus_LV_3273-13_0_3_node_83 | 0.4 | n |  | TRUE
91 | bus_LV_3273-13_0_3_node_84 | 0.4 | n |  | TRUE
92 | bus_LV_3273-13_0_3_node_85 | 0.4 | n |  | TRUE
93 | bus_LV_3273-13_0_3_node_86 | 0.4 | n |  | TRUE
94 | bus_LV_3273-13_0_3_node_87 | 0.4 | n |  | TRUE
95 | bus_LV_3273-13_0_3_node_88 | 0.4 | n |  | TRUE
96 | bus_LV_3273-13_0_3_node_121 | 0.4 | n |  | TRUE
97 | bus_LV_3273-13_0_3_node_89 | 0.4 | n |  | TRUE
98 | bus_LV_3273-13_0_3_node_90 | 0.4 | n |  | TRUE
99 | bus_LV_3273-13_0_3_node_93 | 0.4 | n |  | TRUE
100 | bus_LV_3273-13_0_3_node_122 | 0.4 | n |  | TRUE
101 | bus_LV_3273-13_0_3_node_129 | 0.4 | n |  | TRUE
102 | bus_LV_3273-13_0_3_node_131 | 0.4 | n |  | TRUE
103 | bus_LV_3273-13_0_3_node_96 | 0.4 | n |  | TRUE
104 | bus_LV_3273-13_0_3_node_97 | 0.4 | n |  | TRUE
105 | bus_LV_3273-13_0_3_node_98 | 0.4 | n |  | TRUE
106 | bus_LV_3273-13_0_3_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_3273-13_0_3_node_100 | 0.4 | n |  | TRUE
108 | bus_LV_3273-13_0_3_node_101 | 0.4 | n |  | TRUE
109 | bus_LV_3273-13_0_3_node_104 | 0.4 | n |  | TRUE
110 | bus_LV_3273-13_0_3_node_102 | 0.4 | n |  | TRUE
111 | bus_LV_3273-13_0_3_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_3273-13_0_3_node_111 | 0.4 | n |  | TRUE
113 | bus_LV_3273-13_0_3_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_3273-13_0_3_node_105 | 0.4 | n |  | TRUE
115 | bus_LV_3273-13_0_3_node_106 | 0.4 | n |  | TRUE
116 | bus_LV_3273-13_0_3_node_107 | 0.4 | n |  | TRUE
117 | bus_LV_3273-13_0_3_node_109 | 0.4 | n |  | TRUE
118 | bus_LV_3273-13_0_3_node_112 | 0.4 | n |  | TRUE
119 | bus_LV_3273-13_0_3_node_108 | 0.4 | n |  | TRUE
120 | bus_LV_3273-13_0_3_node_115 | 0.4 | n |  | TRUE
121 | bus_LV_3273-13_0_3_node_114 | 0.4 | n |  | TRUE
122 | bus_LV_3273-13_0_3_node_118 | 0.4 | n |  | TRUE
123 | bus_LV_3273-13_0_3_node_119 | 0.4 | n |  | TRUE
124 | bus_LV_3273-13_0_3_node_120 | 0.4 | n |  | TRUE
125 | bus_LV_3273-13_0_3_node_123 | 0.4 | n |  | TRUE
126 | bus_LV_3273-13_0_3_node_124 | 0.4 | n |  | TRUE
127 | bus_LV_3273-13_0_3_node_125 | 0.4 | n |  | TRUE
128 | bus_LV_3273-13_0_3_node_126 | 0.4 | n |  | TRUE
129 | bus_LV_3273-13_0_3_node_136 | 0.4 | n |  | TRUE
130 | bus_LV_3273-13_0_3_node_138 | 0.4 | n |  | TRUE
131 | bus_MV_52_0_node_46 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3273-13_0_3_load_0 | 0 | 0.00056219 | 0.0001409 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3273-13_0_3_load_1 | 1 | 0.00067303 | 0.00016868 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3273-13_0_3_load_2 | 2 | 0.0031708 | 0.00079467 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3273-13_0_3_load_4 | 4 | 0.00061667 | 0.00015455 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3273-13_0_3_load_5 | 5 | 0.0029587 | 0.00074152 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3273-13_0_3_load_6 | 6 | 0.0018254 | 0.0004575 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3273-13_0_3_load_7 | 9 | 0.0021459 | 0.00053782 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3273-13_0_3_load_8 | 10 | 0.0015505 | 0.00038859 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3273-13_0_3_load_30 | 13 | 0.002261 | 0.00056666 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3273-13_0_3_load_10 | 14 | 0.0010019 | 0.0002511 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3273-13_0_3_load_33 | 15 | 0.00106 | 0.00026566 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3273-13_0_3_load_11 | 16 | 0.0016557 | 0.00041496 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3273-13_0_3_load_31 | 17 | 0.0012246 | 0.00030693 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3273-13_0_3_load_14 | 18 | 0.0022534 | 0.00056475 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3273-13_0_3_load_24 | 19 | 0.0008585 | 0.00021516 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3273-13_0_3_load_25 | 20 | 0.0016488 | 0.00041323 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3273-13_0_3_load_23 | 21 | 0.00041939 | 0.00010511 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3273-13_0_3_load_13 | 22 | 0.0012982 | 0.00032537 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3273-13_0_3_load_12 | 23 | 0.00089908 | 0.00022533 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3273-13_0_3_load_15 | 24 | 0.0040487 | 0.0010147 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3273-13_0_3_load_18 | 26 | 0.00098787 | 0.00024758 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3273-13_0_3_load_19 | 27 | 0.0013229 | 0.00033154 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3273-13_0_3_load_21 | 28 | 0.0022389 | 0.00056112 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3273-13_0_3_load_22 | 29 | 0.0004938 | 0.00012376 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3273-13_0_3_load_32 | 31 | 0.0035699 | 0.00089471 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3273-13_0_3_load_38 | 33 | 0.0014075 | 0.00035275 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3273-13_0_3_load_36 | 34 | 0.0017293 | 0.0004334 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3273-13_0_3_load_34 | 35 | 0.0010421 | 0.00026119 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3273-13_0_3_load_35 | 36 | 0.0013247 | 0.000332 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3273-13_0_3_load_39 | 37 | 0.0013259 | 0.0003323 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3273-13_0_3_load_42 | 40 | 0.0034789 | 0.0008719 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3273-13_0_3_load_134 | 41 | 0.00075642 | 0.00018958 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3273-13_0_3_load_43 | 42 | 0.00079766 | 0.00019991 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3273-13_0_3_load_135 | 43 | 0.00030722 | 7.6998e-05 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3273-13_0_3_load_133 | 45 | 0.00057273 | 0.00014354 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3273-13_0_3_load_132 | 46 | 0.0035658 | 0.00089367 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3273-13_0_3_load_137 | 47 | 0.00050577 | 0.00012676 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3273-13_0_3_load_130 | 48 | 0.0036015 | 0.00090261 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3273-13_0_3_load_47 | 49 | 0.0039674 | 0.00099433 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3273-13_0_3_load_48 | 50 | 0.0056467 | 0.0014152 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3273-13_0_3_load_49 | 51 | 0.0015049 | 0.00037715 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3273-13_0_3_load_51 | 53 | 0.0015578 | 0.00039042 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3273-13_0_3_load_52 | 54 | 0.001434 | 0.0003594 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3273-13_0_3_load_53 | 55 | 0.0031414 | 0.0007873 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3273-13_0_3_load_54 | 57 | 0.0032872 | 0.00082384 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3273-13_0_3_load_61 | 58 | 0.0014966 | 0.00037509 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3273-13_0_3_load_55 | 59 | 0.0015375 | 0.00038533 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3273-13_0_3_load_56 | 60 | 0.0025967 | 0.0006508 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3273-13_0_3_load_57 | 61 | 0.0015571 | 0.00039025 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3273-13_0_3_load_67 | 62 | 0.011834 | 0.0029658 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3273-13_0_3_load_68 | 63 | 0.013645 | 0.0034197 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3273-13_0_3_load_69 | 64 | 0.007777 | 0.0019491 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3273-13_0_3_load_58 | 65 | 0.0016598 | 0.00041599 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3273-13_0_3_load_59 | 66 | 0.0016421 | 0.00041156 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3273-13_0_3_load_65 | 67 | 0.0028708 | 0.00071949 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3273-13_0_3_load_66 | 68 | 0.0016547 | 0.00041472 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3273-13_0_3_load_63 | 70 | 0.0031123 | 0.00078002 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3273-13_0_3_load_64 | 71 | 0.0037439 | 0.0009383 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3273-13_0_3_load_76 | 72 | 0.0024033 | 0.00060232 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3273-13_0_3_load_95 | 73 | 0.0014347 | 0.00035956 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3273-13_0_3_load_77 | 74 | 0.0021629 | 0.00054208 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3273-13_0_3_load_94 | 75 | 0.0010663 | 0.00026725 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3273-13_0_3_load_71 | 76 | 0.015514 | 0.0038881 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3273-13_0_3_load_72 | 77 | 0.0017151 | 0.00042984 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3273-13_0_3_load_73 | 78 | 0.0020183 | 0.00050583 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3273-13_0_3_load_74 | 79 | 0.0026055 | 0.000653 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3273-13_0_3_load_75 | 80 | 0.0020014 | 0.0005016 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3273-13_0_3_load_116 | 81 | 0.0023911 | 0.00059925 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3273-13_0_3_load_117 | 82 | 0.004356 | 0.0010917 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3273-13_0_3_load_78 | 83 | 0.0028684 | 0.00071889 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3273-13_0_3_load_79 | 84 | 0.0015962 | 0.00040005 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3273-13_0_3_load_80 | 85 | 0.0017036 | 0.00042696 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3273-13_0_3_load_81 | 86 | 0.0016757 | 0.00041996 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3273-13_0_3_load_82 | 89 | 0.0036403 | 0.00091234 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3273-13_0_3_load_83 | 90 | 0.0046668 | 0.0011696 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3273-13_0_3_load_85 | 92 | 0.0029305 | 0.00073445 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3273-13_0_3_load_86 | 93 | 0.0019023 | 0.00047677 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3273-13_0_3_load_87 | 94 | 0.0012246 | 0.00030691 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3273-13_0_3_load_121 | 96 | 0.0022396 | 0.00056129 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3273-13_0_3_load_89 | 97 | 0.0021401 | 0.00053636 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3273-13_0_3_load_90 | 98 | 0.00096475 | 0.00024179 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3273-13_0_3_load_93 | 99 | 0.0019685 | 0.00049336 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3273-13_0_3_load_122 | 100 | 0.0006834 | 0.00017128 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3273-13_0_3_load_129 | 101 | 0.0022826 | 0.00057208 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3273-13_0_3_load_131 | 102 | 0.0016237 | 0.00040694 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3273-13_0_3_load_96 | 103 | 0.0017512 | 0.00043889 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3273-13_0_3_load_97 | 104 | 0.0018007 | 0.00045129 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3273-13_0_3_load_98 | 105 | 0.0073564 | 0.0018437 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3273-13_0_3_load_101 | 108 | 0.0043721 | 0.0010957 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3273-13_0_3_load_104 | 109 | 0.0042435 | 0.0010635 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3273-13_0_3_load_102 | 110 | 0.0027376 | 0.0006861 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3273-13_0_3_load_113 | 111 | 0.010128 | 0.0025384 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3273-13_0_3_load_111 | 112 | 0.0025026 | 0.00062722 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3273-13_0_3_load_103 | 113 | 0.0032318 | 0.00080997 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3273-13_0_3_load_105 | 114 | 0.0020682 | 0.00051833 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3273-13_0_3_load_106 | 115 | 0.0046601 | 0.0011679 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3273-13_0_3_load_109 | 117 | 0.0061437 | 0.0015398 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3273-13_0_3_load_112 | 118 | 0.0061429 | 0.0015396 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3273-13_0_3_load_108 | 119 | 0.0079048 | 0.0019811 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3273-13_0_3_load_115 | 120 | 0.00284 | 0.00071177 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3273-13_0_3_load_114 | 121 | 0.0024444 | 0.00061263 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3273-13_0_3_load_118 | 122 | 0.004422 | 0.0011083 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3273-13_0_3_load_120 | 124 | 0.0026215 | 0.00065702 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3273-13_0_3_load_123 | 125 | 0.0011192 | 0.0002805 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3273-13_0_3_load_124 | 126 | 0.00056066 | 0.00014052 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3273-13_0_3_load_125 | 127 | 0.0003813 | 9.5563e-05 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3273-13_0_3_load_126 | 128 | 0.0010085 | 0.00025274 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_3273-13_0_3_load_136 | 129 | 0.00044206 | 0.00011079 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_3273-13_0_3_load_138 | 130 | 0.00060499 | 0.00015162 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 71 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3273-13_0_3_line_0 |  | 0 | 1 | 0.0080175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3273-13_0_3_line_1 |  | 0 | 2 | 0.019405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3273-13_0_3_line_2 |  | 1 | 3 | 0.077055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3273-13_0_3_line_3 |  | 2 | 4 | 0.023347 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3273-13_0_3_line_4 |  | 3 | 5 | 0.051244 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3273-13_0_3_line_5 |  | 3 | 6 | 0.0051149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3273-13_0_3_line_6 |  | 5 | 7 | 0.021635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3273-13_0_3_line_7 |  | 6 | 8 | 0.063816 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3273-13_0_3_line_8 |  | 7 | 12 | 0.023382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3273-13_0_3_line_9 |  | 8 | 13 | 0.072162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3273-13_0_3_line_10 |  | 9 | 10 | 0.055743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3273-13_0_3_line_11 |  | 9 | 11 | 0.039386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3273-13_0_3_line_12 |  | 11 | 14 | 0.0391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3273-13_0_3_line_13 |  | 12 | 28 | 0.018833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3273-13_0_3_line_14 |  | 12 | 24 | 0.021617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3273-13_0_3_line_15 |  | 14 | 18 | 0.0041755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3273-13_0_3_line_16 |  | 15 | 16 | 0.06287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3273-13_0_3_line_17 |  | 15 | 17 | 0.054445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3273-13_0_3_line_18 |  | 16 | 23 | 0.020599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3273-13_0_3_line_19 |  | 17 | 30 | 0.017758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3273-13_0_3_line_20 |  | 18 | 22 | 0.011062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3273-13_0_3_line_21 |  | 19 | 20 | 0.061537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3273-13_0_3_line_22 |  | 19 | 21 | 0.010624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3273-13_0_3_line_23 |  | 20 | 30 | 0.056694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3273-13_0_3_line_24 |  | 21 | 29 | 0.026311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3273-13_0_3_line_25 |  | 22 | 23 | 0.021693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3273-13_0_3_line_26 |  | 24 | 25 | 0.023073 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3273-13_0_3_line_27 |  | 25 | 26 | 0.033657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3273-13_0_3_line_28 |  | 25 | 27 | 0.037639 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3273-13_0_3_line_29 |  | 26 | 29 | 0.0047325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3273-13_0_3_line_30 |  | 30 | 31 | 0.032199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3273-13_0_3_line_31 |  | 31 | 32 | 0.017188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3273-13_0_3_line_32 |  | 32 | 33 | 0.011258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3273-13_0_3_line_33 |  | 32 | 34 | 0.023492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3273-13_0_3_line_34 |  | 33 | 37 | 0.008903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3273-13_0_3_line_35 |  | 34 | 36 | 0.010723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3273-13_0_3_line_36 |  | 35 | 36 | 0.00080847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3273-13_0_3_line_37 |  | 37 | 38 | 0.020912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3273-13_0_3_line_38 |  | 38 | 39 | 0.00575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3273-13_0_3_line_39 |  | 38 | 40 | 0.017653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3273-13_0_3_line_40 |  | 39 | 41 | 0.011309 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3273-13_0_3_line_41 |  | 40 | 42 | 0.0044215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3273-13_0_3_line_42 |  | 41 | 43 | 0.023622 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3273-13_0_3_line_43 |  | 42 | 44 | 0.014988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3273-13_0_3_line_44 |  | 43 | 129 | 0.062064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3273-13_0_3_line_45 |  | 44 | 45 | 0.0090234 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3273-13_0_3_line_46 |  | 44 | 46 | 0.011546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3273-13_0_3_line_47 |  | 45 | 47 | 0.017943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3273-13_0_3_line_48 |  | 46 | 48 | 0.0086483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3273-13_0_3_line_49 |  | 47 | 130 | 0.011875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3273-13_0_3_line_50 |  | 48 | 102 | 0.014871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3273-13_0_3_line_51 |  | 49 | 50 | 0.01478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3273-13_0_3_line_52 |  | 50 | 51 | 0.038689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3273-13_0_3_line_53 |  | 51 | 52 | 0.018967 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3273-13_0_3_line_54 |  | 52 | 53 | 0.01862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3273-13_0_3_line_55 |  | 52 | 54 | 0.044173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3273-13_0_3_line_56 |  | 53 | 55 | 0.02597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3273-13_0_3_line_57 |  | 54 | 56 | 0.032305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3273-13_0_3_line_58 |  | 55 | 57 | 0.009206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3273-13_0_3_line_59 |  | 56 | 58 | 0.0061821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3273-13_0_3_line_60 |  | 57 | 59 | 0.0097805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3273-13_0_3_line_61 |  | 58 | 69 | 0.021885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3273-13_0_3_line_62 |  | 59 | 60 | 0.0098485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3273-13_0_3_line_63 |  | 60 | 61 | 0.012022 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3273-13_0_3_line_64 |  | 61 | 65 | 0.01484 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3273-13_0_3_line_65 |  | 62 | 63 | 0.04284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3273-13_0_3_line_66 |  | 62 | 64 | 0.03978 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3273-13_0_3_line_67 |  | 64 | 74 | 0.040257 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3273-13_0_3_line_68 |  | 65 | 66 | 0.0065348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3273-13_0_3_line_69 |  | 66 | 67 | 0.013049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3273-13_0_3_line_70 |  | 67 | 68 | 0.0026164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3273-13_0_3_line_71 |  | 69 | 70 | 0.020589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3273-13_0_3_line_72 |  | 69 | 71 | 0.03453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3273-13_0_3_line_73 |  | 70 | 72 | 0.044483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3273-13_0_3_line_74 |  | 71 | 73 | 0.02362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
75 | LV_3273-13_0_3_line_75 |  | 72 | 74 | 0.023636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3273-13_0_3_line_76 |  | 73 | 75 | 0.0043331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_3273-13_0_3_line_77 |  | 74 | 79 | 0.022501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3273-13_0_3_line_78 |  | 75 | 87 | 0.0098877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
79 | LV_3273-13_0_3_line_79 |  | 76 | 77 | 0.0097135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3273-13_0_3_line_80 |  | 76 | 78 | 0.0072322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3273-13_0_3_line_81 |  | 77 | 79 | 0.011077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3273-13_0_3_line_82 |  | 78 | 80 | 0.022229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3273-13_0_3_line_83 |  | 80 | 81 | 0.012291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3273-13_0_3_line_84 |  | 81 | 82 | 0.0098815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3273-13_0_3_line_85 |  | 82 | 122 | 0.018334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3273-13_0_3_line_86 |  | 83 | 84 | 0.014444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3273-13_0_3_line_87 |  | 84 | 85 | 0.046158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3273-13_0_3_line_88 |  | 85 | 86 | 0.0037687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3273-13_0_3_line_89 |  | 86 | 87 | 0.020392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3273-13_0_3_line_90 |  | 87 | 88 | 0.014127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
91 | LV_3273-13_0_3_line_91 |  | 88 | 99 | 0.015792 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3273-13_0_3_line_92 |  | 88 | 93 | 0.030223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3273-13_0_3_line_93 |  | 89 | 90 | 0.014558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3273-13_0_3_line_94 |  | 89 | 91 | 0.039355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3273-13_0_3_line_95 |  | 90 | 92 | 0.0076478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3273-13_0_3_line_96 |  | 91 | 93 | 0.023239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3273-13_0_3_line_97 |  | 91 | 94 | 0.0087018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_3273-13_0_3_line_98 |  | 92 | 95 | 0.007529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_3273-13_0_3_line_99 |  | 94 | 96 | 0.007181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_3273-13_0_3_line_100 |  | 95 | 97 | 0.016902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3273-13_0_3_line_101 |  | 95 | 98 | 0.0045899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_3273-13_0_3_line_102 |  | 96 | 100 | 0.019215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3273-13_0_3_line_103 |  | 97 | 101 | 0.018963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3273-13_0_3_line_104 |  | 98 | 102 | 0.015144 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3273-13_0_3_line_105 |  | 99 | 103 | 0.0048239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3273-13_0_3_line_106 |  | 100 | 125 | 0.01534 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3273-13_0_3_line_107 |  | 103 | 104 | 0.030563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3273-13_0_3_line_108 |  | 104 | 105 | 0.0081934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3273-13_0_3_line_109 |  | 105 | 106 | 0.0047869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3273-13_0_3_line_110 |  | 106 | 107 | 0.036513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_3273-13_0_3_line_111 |  | 106 | 108 | 0.04235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3273-13_0_3_line_112 |  | 107 | 109 | 0.019686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3273-13_0_3_line_113 |  | 107 | 110 | 0.0020533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3273-13_0_3_line_114 |  | 108 | 111 | 0.016011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3273-13_0_3_line_115 |  | 109 | 112 | 0.021673 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3273-13_0_3_line_116 |  | 110 | 113 | 0.013269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3273-13_0_3_line_117 |  | 112 | 118 | 0.021559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_3273-13_0_3_line_118 |  | 113 | 114 | 0.026346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_3273-13_0_3_line_119 |  | 113 | 115 | 0.021584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_3273-13_0_3_line_120 |  | 114 | 116 | 0.031115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_3273-13_0_3_line_121 |  | 115 | 117 | 0.0064754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_3273-13_0_3_line_122 |  | 116 | 119 | 0.066367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_3273-13_0_3_line_123 |  | 118 | 120 | 0.0030906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_3273-13_0_3_line_124 |  | 120 | 121 | 0.0055005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_3273-13_0_3_line_125 |  | 122 | 123 | 0.020727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_3273-13_0_3_line_126 |  | 123 | 124 | 0.029325 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_3273-13_0_3_line_127 |  | 125 | 126 | 0.0084376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_3273-13_0_3_line_128 |  | 126 | 127 | 0.0035485 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_3273-13_0_3_line_129 |  | 127 | 128 | 0.020371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3273-13_0_3_trafo_64 | 0.63 MVA 20/0.4 kV | 131 | 71 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2751922.7625 | 1226894.5313 | 2751922.7625 | 1226894.5313 | 2751925.0067 | 1226902.2283
1 | 2751922.7625 | 1226894.5313 | 2751926.2696 | 1226875.446
2 | 2751951.1504 | 1226973.8951 | 2751947.3561 | 1226952.045 | 2751930.3482 | 1226920.5486 | 2751925.0067 | 1226902.2283
3 | 2751931.0687 | 1226852.6204 | 2751929.4303 | 1226858.2463 | 2751926.2696 | 1226875.446
4 | 2751951.1504 | 1226973.8951 | 2751954.3308 | 1226962.7995 | 2751973.929 | 1226928.2728
5 | 2751951.1504 | 1226973.8951 | 2751951.2476 | 1226979.009
6 | 2751984.6091 | 1226909.4576 | 2751973.929 | 1226928.2728
7 | 2751952.46 | 1227042.8135 | 2751951.2476 | 1226979.009
8 | 2751984.6091 | 1226909.4576 | 2751993.4215 | 1226912.3964 | 2752005.5013 | 1226912.7053 | 2752007.2511 | 1226911.5934
9 | 2751952.46 | 1227042.8135 | 2751952.0544 | 1227048.297 | 2751951.1325 | 1227114.9538
10 | 2751930.9131 | 1226726.631 | 2751927.3827 | 1226716.9987 | 2751930.0017 | 1226701.4626 | 2751939.4524 | 1226681.5191 | 2751942.641 | 1226674.5552
11 | 2751961.6845 | 1226747.4913 | 2751939.6123 | 1226740.2433 | 2751930.9131 | 1226726.631
12 | 2751961.6845 | 1226747.4913 | 2751978.5255 | 1226712.2042
13 | 2752007.2511 | 1226911.5934 | 2752020.1429 | 1226925.3228
14 | 2752007.2511 | 1226911.5934 | 2752012.3852 | 1226908.3216 | 2752022.3594 | 1226896.4193
15 | 2751978.5255 | 1226712.2042 | 2751979.2562 | 1226710.6732 | 2751980.9467 | 1226708.8599
16 | 2752064.1738 | 1226693.1645 | 2752008.4718 | 1226664.0114
17 | 2752064.1738 | 1226693.1645 | 2752069.0121 | 1226692.3829 | 2752079.4653 | 1226693.1508 | 2752088.1842 | 1226697.0883 | 2752094.4381 | 1226704.2992 | 2752107.3535 | 1226719.506
18 | 2752008.4718 | 1226664.0114 | 2752001.4183 | 1226683.3655
19 | 2752121.3453 | 1226730.344 | 2752108.9113 | 1226721.3402 | 2752107.3535 | 1226719.506
20 | 2751988.3574 | 1226700.6562 | 2751987.2562 | 1226702.0919 | 2751980.9467 | 1226708.8599
21 | 2752041.86 | 1226807.5751 | 2752044.3106 | 1226803.6531 | 2752051.7598 | 1226799.117 | 2752069.0956 | 1226770.9455 | 2752066.7756 | 1226764.4025 | 2752072.6101 | 1226758.6829
22 | 2752041.86 | 1226807.5751 | 2752036.2302 | 1226816.5851
23 | 2752121.3453 | 1226730.344 | 2752099.4703 | 1226741.773 | 2752091.4688 | 1226745.9612 | 2752078.8711 | 1226752.5452 | 2752072.6101 | 1226758.6829
24 | 2752028.8419 | 1226840.7327 | 2752028.1401 | 1226836.3808 | 2752029.0581 | 1226828.0634 | 2752036.2302 | 1226816.5851
25 | 2752001.4183 | 1226683.3655 | 2752001.236 | 1226683.8657 | 2751988.3574 | 1226700.6562
26 | 2752036.6455 | 1226878.3141 | 2752029.7577 | 1226887.591 | 2752022.3594 | 1226896.4193
27 | 2752036.6455 | 1226878.3141 | 2752029.7175 | 1226846.1634 | 2752029.5952 | 1226845.4049
28 | 2752036.6455 | 1226878.3141 | 2752061.1277 | 1226875.2146 | 2752063.5203 | 1226877.7336 | 2752066.657 | 1226879.3264 | 2752072.1394 | 1226876.9643
29 | 2752029.5952 | 1226845.4049 | 2752028.8419 | 1226840.7327
30 | 2752121.3453 | 1226730.344 | 2752123.6236 | 1226731.9927 | 2752150.924 | 1226742.8675
31 | 2752166.7482 | 1226749.578 | 2752151.5795 | 1226743.1287 | 2752150.924 | 1226742.8675
32 | 2752166.7482 | 1226749.578 | 2752176.3415 | 1226755.4701
33 | 2752166.7482 | 1226749.578 | 2752152.5773 | 1226768.3151
34 | 2752176.3415 | 1226755.4701 | 2752181.8072 | 1226758.8271 | 2752184.1611 | 1226759.635
35 | 2752146.1089 | 1226776.8677 | 2752152.5773 | 1226768.3151
36 | 2752145.6212 | 1226777.5125 | 2752146.1089 | 1226776.8677
37 | 2752204.1961 | 1226760.8015 | 2752194.4816 | 1226763.1774 | 2752184.1611 | 1226759.635
38 | 2752204.1961 | 1226760.8015 | 2752203.3254 | 1226755.1185
39 | 2752204.1961 | 1226760.8015 | 2752211.3172 | 1226776.9546
40 | 2752203.3254 | 1226755.1185 | 2752214.5768 | 1226753.9816
41 | 2752213.1008 | 1226781.0004 | 2752211.3172 | 1226776.9546
42 | 2752214.5768 | 1226753.9816 | 2752216.5852 | 1226753.7787 | 2752237.9041 | 1226757.2713
43 | 2752219.1468 | 1226794.7148 | 2752213.1008 | 1226781.0004
44 | 2752237.9041 | 1226757.2713 | 2752247.0793 | 1226758.7744 | 2752251.5146 | 1226758.2208 | 2752261.6787 | 1226750.7296 | 2752270.9856 | 1226744.7289 | 2752273.4922 | 1226743.9812 | 2752276.084 | 1226744.0476 | 2752277.6835 | 1226745.2563 | 2752283.0041 | 1226755.7354 | 2752284.0351 | 1226757.2298 | 2752287.3937 | 1226759.0396
45 | 2752219.1468 | 1226794.7148 | 2752226.7351 | 1226789.8323
46 | 2752219.1468 | 1226794.7148 | 2752223.8018 | 1226805.2812
47 | 2752242.598 | 1226783.0375 | 2752237.6981 | 1226782.7785 | 2752226.7351 | 1226789.8323
48 | 2752223.8018 | 1226805.2812 | 2752227.2884 | 1226813.1955
49 | 2752252.2489 | 1226789.9574 | 2752242.598 | 1226783.0375
50 | 2752227.2884 | 1226813.1955 | 2752227.2884 | 1226813.1955 | 2752232.9487 | 1226826.9467
51 | 2752085.0697 | 1227142.8264 | 2752090.8026 | 1227129.2037
52 | 2752090.8026 | 1227129.2037 | 2752105.8095 | 1227093.5433
53 | 2752113.1665 | 1227076.0611 | 2752105.8095 | 1227093.5433
54 | 2752113.1665 | 1227076.0611 | 2752128.1704 | 1227087.0885
55 | 2752113.1665 | 1227076.0611 | 2752121.116 | 1227063.5196 | 2752131.6334 | 1227049.8983 | 2752140.9797 | 1227042.19
56 | 2752149.0967 | 1227102.4687 | 2752128.1704 | 1227087.0885
57 | 2752167.0052 | 1227023.0672 | 2752144.7251 | 1227039.1009 | 2752140.9797 | 1227042.19
58 | 2752149.0967 | 1227102.4687 | 2752156.5147 | 1227107.9207 | 2752156.5147 | 1227107.9207
59 | 2752167.0052 | 1227023.0672 | 2752172.0693 | 1227019.5213
60 | 2752156.5147 | 1227107.9207 | 2752162.5644 | 1227100.2358
61 | 2752189.941 | 1227006.8946 | 2752188.7695 | 1227007.6319 | 2752181.3752 | 1227012.9921 | 2752180.7803 | 1227013.4218 | 2752172.0693 | 1227019.5213
62 | 2752168.6563 | 1227092.4974 | 2752162.5644 | 1227100.2358
63 | 2752168.6563 | 1227092.4974 | 2752176.0923 | 1227083.0515
64 | 2752176.0923 | 1227083.0515 | 2752185.2716 | 1227071.3911
65 | 2752209.2367 | 1227134.3197 | 2752201.5507 | 1227144.9174 | 2752228.1812 | 1227158.1766
66 | 2752232.5918 | 1227102.1169 | 2752209.2367 | 1227134.3197
67 | 2752254.1254 | 1227068.1029 | 2752232.5918 | 1227102.1169
68 | 2752189.3137 | 1227066.2564 | 2752185.2716 | 1227071.3911
69 | 2752189.3137 | 1227066.2564 | 2752197.3855 | 1227056.0029
70 | 2752199.0039 | 1227053.9471 | 2752197.3855 | 1227056.0029
71 | 2752189.941 | 1227006.8946 | 2752201.444 | 1227018.7663 | 2752204.373 | 1227021.5756
72 | 2752189.941 | 1227006.8946 | 2752217.8371 | 1226986.5451 | 2752217.8371 | 1226986.5451
73 | 2752204.373 | 1227021.5756 | 2752209.9259 | 1227026.9018 | 2752236.8365 | 1227051.9868
74 | 2752217.8371 | 1226986.5451 | 2752223.8557 | 1226980.1266 | 2752228.7914 | 1226972.7572 | 2752231.3156 | 1226967.3679
75 | 2752236.8365 | 1227051.9868 | 2752254.1254 | 1227068.1029
76 | 2752231.3156 | 1226967.3679 | 2752233.1535 | 1226963.4438
77 | 2752254.1254 | 1227068.1029 | 2752270.5845 | 1227083.4455
78 | 2752237.4402 | 1226954.5397 | 2752236.9496 | 1226955.3389 | 2752233.1535 | 1226963.4438
79 | 2752285.7925 | 1227097.6218 | 2752278.6872 | 1227090.9985
80 | 2752285.7925 | 1227097.6218 | 2752291.0827 | 1227102.5531
81 | 2752270.5845 | 1227083.4455 | 2752278.6872 | 1227090.9985
82 | 2752291.0827 | 1227102.5531 | 2752293.5054 | 1227104.8114 | 2752307.486 | 1227117.5546
83 | 2752307.486 | 1227117.5546 | 2752316.57 | 1227125.8346
84 | 2752324.1483 | 1227132.1717 | 2752318.262 | 1227127.3768 | 2752316.57 | 1227125.8346
85 | 2752324.1483 | 1227132.1717 | 2752326.9453 | 1227134.45 | 2752337.4812 | 1227142.3158 | 2752338.8074 | 1227143.1715
86 | 2752182.1224 | 1226899.096 | 2752193.6048 | 1226897.8444 | 2752196.4414 | 1226898.4175
87 | 2752196.4414 | 1226898.4175 | 2752196.4414 | 1226898.4175 | 2752198.9412 | 1226900.0051 | 2752203.0001 | 1226907.3378 | 2752208.186 | 1226919.2257 | 2752210.833 | 1226923.3528 | 2752221.1132 | 1226936.8202
88 | 2752221.1132 | 1226936.8202 | 2752223.4 | 1226939.8159
89 | 2752237.4402 | 1226954.5397 | 2752230.5327 | 1226948.2906 | 2752223.6216 | 1226940.1063 | 2752223.4 | 1226939.8159
90 | 2752248.5609 | 1226946.6948 | 2752244.9532 | 1226947.8035 | 2752242.3614 | 1226948.9271 | 2752239.1581 | 1226951.7144 | 2752237.4402 | 1226954.5397
91 | 2752248.5609 | 1226946.6948 | 2752249.9623 | 1226950.0115 | 2752252.4824 | 1226953.468 | 2752256.804 | 1226956.4591 | 2752259.2016 | 1226957.6075
92 | 2752248.5609 | 1226946.6948 | 2752248.7556 | 1226941.4617 | 2752250.7464 | 1226936.864 | 2752263.5726 | 1226921.5499
93 | 2752254.3115 | 1226871.4135 | 2752251.6066 | 1226867.7452 | 2752246.9413 | 1226858.8996
94 | 2752277.6675 | 1226903.0887 | 2752254.3115 | 1226871.4135
95 | 2752243.3736 | 1226852.135 | 2752246.9413 | 1226858.8996
96 | 2752277.6675 | 1226903.0887 | 2752268.7928 | 1226915.3172 | 2752263.5726 | 1226921.5499
97 | 2752277.6675 | 1226903.0887 | 2752283.9068 | 1226897.0231
98 | 2752240.4602 | 1226845.195 | 2752243.116 | 1226851.6466 | 2752243.3736 | 1226852.135
99 | 2752283.9068 | 1226897.0231 | 2752287.2642 | 1226893.7592 | 2752289.2963 | 1226892.3054
100 | 2752240.4602 | 1226845.195 | 2752254.0925 | 1226835.2037
101 | 2752240.4602 | 1226845.195 | 2752238.7131 | 1226840.9506
102 | 2752305.5754 | 1226882.1452 | 2752301.6433 | 1226884.2407 | 2752294.8732 | 1226888.3156 | 2752289.2963 | 1226892.3054
103 | 2752269.3877 | 1226823.9936 | 2752254.0925 | 1226835.2037
104 | 2752232.9487 | 1226826.9467 | 2752238.7131 | 1226840.9506
105 | 2752263.5522 | 1226959.6913 | 2752259.2016 | 1226957.6075
106 | 2752305.5754 | 1226882.1452 | 2752319.1129 | 1226874.9308
107 | 2752263.5522 | 1226959.6913 | 2752291.1162 | 1226972.894
108 | 2752291.1162 | 1226972.894 | 2752298.5057 | 1226976.4335
109 | 2752302.8229 | 1226978.5013 | 2752298.5057 | 1226976.4335
110 | 2752302.8229 | 1226978.5013 | 2752335.0482 | 1226992.2388 | 2752336.553 | 1226992.7
111 | 2752302.8229 | 1226978.5013 | 2752291.1814 | 1227001.3464 | 2752290.1788 | 1227004.6683 | 2752287.4683 | 1227015.4532 | 2752286.6986 | 1227017.4279
112 | 2752336.553 | 1226992.7 | 2752327.6744 | 1227010.2704
113 | 2752336.553 | 1226992.7 | 2752338.5184 | 1226993.2943
114 | 2752286.6986 | 1227017.4279 | 2752285.8287 | 1227019.6595 | 2752278.3916 | 1227031.0644
115 | 2752327.6744 | 1227010.2704 | 2752317.8998 | 1227029.6142
116 | 2752351.2189 | 1226997.1351 | 2752338.5184 | 1226993.2943
117 | 2752317.8998 | 1227029.6142 | 2752308.1766 | 1227048.8562
118 | 2752351.2189 | 1226997.1351 | 2752358.3372 | 1226978.8784 | 2752362.6251 | 1226973.665
119 | 2752351.2189 | 1226997.1351 | 2752371.8694 | 1227003.4133
120 | 2752382.3899 | 1226949.6343 | 2752362.6251 | 1226973.665
121 | 2752371.8694 | 1227003.4133 | 2752378.0649 | 1227005.2968
122 | 2752333.2986 | 1226936.5209 | 2752345.1616 | 1226921.0216 | 2752382.3899 | 1226949.6343
123 | 2752306.7828 | 1227051.6146 | 2752308.1766 | 1227048.8562
124 | 2752304.302 | 1227056.5239 | 2752306.7828 | 1227051.6146
125 | 2752355.983 | 1227154.7676 | 2752350.0397 | 1227150.556 | 2752345.6122 | 1227147.5621 | 2752338.8074 | 1227143.1715
126 | 2752355.983 | 1227154.7676 | 2752357.7672 | 1227153.2007 | 2752368.4726 | 1227144.6893 | 2752378.2159 | 1227135.6743
127 | 2752326.5591 | 1226870.9626 | 2752319.1129 | 1226874.9308
128 | 2752329.6906 | 1226869.2938 | 2752326.5591 | 1226870.9626
129 | 2752329.6906 | 1226869.2938 | 2752334.1186 | 1226866.934 | 2752347.2956 | 1226859.0531

## bus_geodata
| x | y | coords
0 | 2751922.7625 | 1226894.5313
1 | 2751925.0067 | 1226902.2283
2 | 2751926.2696 | 1226875.446
3 | 2751951.1504 | 1226973.8951
4 | 2751931.0687 | 1226852.6204
5 | 2751973.929 | 1226928.2728
6 | 2751951.2476 | 1226979.009
7 | 2751984.6091 | 1226909.4576
8 | 2751952.46 | 1227042.8135
9 | 2751930.9131 | 1226726.631
10 | 2751942.641 | 1226674.5552
11 | 2751961.6845 | 1226747.4913
12 | 2752007.2511 | 1226911.5934
13 | 2751951.1325 | 1227114.9538
14 | 2751978.5255 | 1226712.2042
15 | 2752064.1738 | 1226693.1645
16 | 2752008.4718 | 1226664.0114
17 | 2752107.3535 | 1226719.506
18 | 2751980.9467 | 1226708.8599
19 | 2752041.86 | 1226807.5751
20 | 2752072.6101 | 1226758.6829
21 | 2752036.2302 | 1226816.5851
22 | 2751988.3574 | 1226700.6562
23 | 2752001.4183 | 1226683.3655
24 | 2752022.3594 | 1226896.4193
25 | 2752036.6455 | 1226878.3141
26 | 2752029.5952 | 1226845.4049
27 | 2752072.1394 | 1226876.9643
28 | 2752020.1429 | 1226925.3228
29 | 2752028.8419 | 1226840.7327
30 | 2752121.3453 | 1226730.344
31 | 2752150.924 | 1226742.8675
32 | 2752166.7482 | 1226749.578
33 | 2752176.3415 | 1226755.4701
34 | 2752152.5773 | 1226768.3151
35 | 2752145.6212 | 1226777.5125
36 | 2752146.1089 | 1226776.8677
37 | 2752184.1611 | 1226759.635
38 | 2752204.1961 | 1226760.8015
39 | 2752203.3254 | 1226755.1185
40 | 2752211.3172 | 1226776.9546
41 | 2752214.5768 | 1226753.9816
42 | 2752213.1008 | 1226781.0004
43 | 2752237.9041 | 1226757.2713
44 | 2752219.1468 | 1226794.7148
45 | 2752226.7351 | 1226789.8323
46 | 2752223.8018 | 1226805.2812
47 | 2752242.598 | 1226783.0375
48 | 2752227.2884 | 1226813.1955
49 | 2752085.0697 | 1227142.8264
50 | 2752090.8026 | 1227129.2037
51 | 2752105.8095 | 1227093.5433
52 | 2752113.1665 | 1227076.0611
53 | 2752128.1704 | 1227087.0885
54 | 2752140.9797 | 1227042.19
55 | 2752149.0967 | 1227102.4687
56 | 2752167.0052 | 1227023.0672
57 | 2752156.5147 | 1227107.9207
58 | 2752172.0693 | 1227019.5213
59 | 2752162.5644 | 1227100.2358
60 | 2752168.6563 | 1227092.4974
61 | 2752176.0923 | 1227083.0515
62 | 2752209.2367 | 1227134.3197
63 | 2752228.1812 | 1227158.1766
64 | 2752232.5918 | 1227102.1169
65 | 2752185.2716 | 1227071.3911
66 | 2752189.3137 | 1227066.2564
67 | 2752197.3855 | 1227056.0029
68 | 2752199.0039 | 1227053.9471
69 | 2752189.941 | 1227006.8946
70 | 2752204.373 | 1227021.5756
71 | 2752217.8371 | 1226986.5451
72 | 2752236.8365 | 1227051.9868
73 | 2752231.3156 | 1226967.3678
74 | 2752254.1254 | 1227068.1029
75 | 2752233.1535 | 1226963.4438
76 | 2752285.7925 | 1227097.6218
77 | 2752278.6872 | 1227090.9985
78 | 2752291.0827 | 1227102.5531
79 | 2752270.5845 | 1227083.4455
80 | 2752307.486 | 1227117.5546
81 | 2752316.57 | 1227125.8346
82 | 2752324.1483 | 1227132.1717
83 | 2752182.1224 | 1226899.096
84 | 2752196.4414 | 1226898.4175
85 | 2752221.1132 | 1226936.8202
86 | 2752223.4 | 1226939.8159
87 | 2752237.4402 | 1226954.5397
88 | 2752248.5609 | 1226946.6948
89 | 2752254.3115 | 1226871.4135
90 | 2752246.9413 | 1226858.8996
91 | 2752277.6675 | 1226903.0887
92 | 2752243.3736 | 1226852.135
93 | 2752263.5726 | 1226921.5499
94 | 2752283.9068 | 1226897.0231
95 | 2752240.4602 | 1226845.195
96 | 2752289.2963 | 1226892.3054
97 | 2752254.0925 | 1226835.2037
98 | 2752238.7131 | 1226840.9506
99 | 2752259.2016 | 1226957.6075
100 | 2752305.5754 | 1226882.1452
101 | 2752269.3877 | 1226823.9936
102 | 2752232.9487 | 1226826.9467
103 | 2752263.5522 | 1226959.6913
104 | 2752291.1162 | 1226972.894
105 | 2752298.5057 | 1226976.4335
106 | 2752302.8229 | 1226978.5013
107 | 2752336.553 | 1226992.7
108 | 2752286.6986 | 1227017.4279
109 | 2752327.6744 | 1227010.2704
110 | 2752338.5184 | 1226993.2943
111 | 2752278.3916 | 1227031.0644
112 | 2752317.8998 | 1227029.6142
113 | 2752351.2189 | 1226997.1351
114 | 2752362.6251 | 1226973.665
115 | 2752371.8694 | 1227003.4133
116 | 2752382.3899 | 1226949.6343
117 | 2752378.0649 | 1227005.2968
118 | 2752308.1766 | 1227048.8562
119 | 2752333.2986 | 1226936.5209
120 | 2752306.7828 | 1227051.6146
121 | 2752304.302 | 1227056.5239
122 | 2752338.8074 | 1227143.1715
123 | 2752355.983 | 1227154.7676
124 | 2752378.2159 | 1227135.6743
125 | 2752319.1129 | 1226874.9308
126 | 2752326.5591 | 1226870.9626
127 | 2752329.6906 | 1226869.2938
128 | 2752347.2956 | 1226859.0531
129 | 2752287.3937 | 1226759.0396
130 | 2752252.2489 | 1226789.9574
131 | 2752189.941 | 1227006.8946

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97219 | -0.53789 | 0.00056219 | 0.0001409
1 | 0.97222 | -0.53725 | 0.00067303 | 0.00016868
2 | 0.97212 | -0.53925 | 0.0031708 | 0.00079467
3 | 0.97258 | -0.53011 | 0 | 0
4 | 0.97211 | -0.53951 | 0.00061667 | 0.00015455
5 | 0.97302 | -0.5215 | 0.0029587 | 0.00074152
6 | 0.97256 | -0.5305 | 0.0018254 | 0.0004575
7 | 0.97326 | -0.51669 | 0 | 0
8 | 0.97243 | -0.53316 | 0 | 0
9 | 0.97606 | -0.46168 | 0.0021459 | 0.00053782
10 | 0.97598 | -0.46327 | 0.0015505 | 0.00038859
11 | 0.9762 | -0.45902 | 0 | 0
12 | 0.97352 | -0.5115 | 0 | 0
13 | 0.97228 | -0.53617 | 0.002261 | 0.00056666
14 | 0.97633 | -0.45637 | 0.0010019 | 0.0002511
15 | 0.97739 | -0.43548 | 0.00106 | 0.00026566
16 | 0.97676 | -0.44789 | 0.0016557 | 0.00041496
17 | 0.97799 | -0.42369 | 0.0012246 | 0.00030693
18 | 0.97635 | -0.45601 | 0.0022534 | 0.00056475
19 | 0.97565 | -0.46965 | 0.0008585 | 0.00021516
20 | 0.97693 | -0.44438 | 0.0016488 | 0.00041323
21 | 0.97543 | -0.47385 | 0.00041939 | 0.00010511
22 | 0.97642 | -0.45461 | 0.0012982 | 0.00032537
23 | 0.97659 | -0.45133 | 0.00089908 | 0.00022533
24 | 0.97381 | -0.50581 | 0.0040487 | 0.0010147
25 | 0.97421 | -0.49802 | 0 | 0
26 | 0.97482 | -0.48586 | 0.00098787 | 0.00024758
27 | 0.97416 | -0.49894 | 0.0013229 | 0.00033154
28 | 0.97349 | -0.51227 | 0.0022389 | 0.00056112
29 | 0.97492 | -0.48406 | 0.0004938 | 0.00012376
30 | 0.97821 | -0.41945 | 0 | 0
31 | 0.97932 | -0.39765 | 0.0035699 | 0.00089471
32 | 0.97997 | -0.38492 | 0 | 0
33 | 0.98044 | -0.37576 | 0.0014075 | 0.00035275
34 | 0.97988 | -0.38667 | 0.0017293 | 0.0004334
35 | 0.97986 | -0.38715 | 0.0010421 | 0.00026119
36 | 0.97986 | -0.38713 | 0.0013247 | 0.000332
37 | 0.98082 | -0.36829 | 0.0013259 | 0.0003323
38 | 0.98175 | -0.35027 | 0 | 0
39 | 0.98174 | -0.35043 | 0 | 0
40 | 0.98255 | -0.3346 | 0.0034789 | 0.0008719
41 | 0.98173 | -0.35073 | 0.00075642 | 0.00018958
42 | 0.98277 | -0.3304 | 0.00079766 | 0.00019991
43 | 0.98171 | -0.35106 | 0.00030722 | 7.6998e-05
44 | 0.98351 | -0.31597 | 0 | 0
45 | 0.9835 | -0.31625 | 0.00057273 | 0.00014354
46 | 0.9841 | -0.30452 | 0.0035658 | 0.00089367
47 | 0.98348 | -0.31661 | 0.00050577 | 0.00012676
48 | 0.98457 | -0.29539 | 0.0036015 | 0.00090261
49 | 0.99258 | -0.14248 | 0.0039674 | 0.00099433
50 | 0.99263 | -0.14145 | 0.0056467 | 0.0014152
51 | 0.99297 | -0.13487 | 0.0015049 | 0.00037715
52 | 0.99316 | -0.13114 | 0 | 0
53 | 0.9928 | -0.13822 | 0.0015578 | 0.00039042
54 | 0.99448 | -0.1057 | 0.001434 | 0.0003594
55 | 0.99232 | -0.14739 | 0.0031414 | 0.0007873
56 | 0.99548 | -0.086329 | 0 | 0
57 | 0.99218 | -0.15013 | 0.0032872 | 0.00082384
58 | 0.99568 | -0.082626 | 0.0014966 | 0.00037509
59 | 0.99206 | -0.15247 | 0.0015375 | 0.00038533
60 | 0.99195 | -0.15456 | 0.0025967 | 0.0006508
61 | 0.99185 | -0.15656 | 0.0015571 | 0.00039025
62 | 0.98808 | -0.22926 | 0.011834 | 0.0029658
63 | 0.98754 | -0.2397 | 0.013645 | 0.0034197
64 | 0.98901 | -0.21118 | 0.007777 | 0.0019491
65 | 0.99174 | -0.15862 | 0.0016598 | 0.00041599
66 | 0.99171 | -0.15933 | 0.0016421 | 0.00041156
67 | 0.99165 | -0.16038 | 0.0028708 | 0.00071949
68 | 0.99165 | -0.16045 | 0.0016547 | 0.00041472
69 | 0.99639 | -0.068952 | 0 | 0
70 | 0.9949 | -0.097402 | 0.0031123 | 0.00078002
71 | 1 | 0 | -0.29132 | -0.073851
72 | 0.99182 | -0.15671 | 0.0024033 | 0.00060232
73 | 0.99813 | -0.03553 | 0.0014347 | 0.00035956
74 | 0.99024 | -0.18736 | 0.0021629 | 0.00054208
75 | 0.99779 | -0.042008 | 0.0010663 | 0.00026725
76 | 0.98881 | -0.21511 | 0.015514 | 0.0038881
77 | 0.98911 | -0.20934 | 0.0017151 | 0.00042984
78 | 0.98869 | -0.2174 | 0.0020183 | 0.00050583
79 | 0.98946 | -0.20242 | 0.0026055 | 0.000653
80 | 0.98837 | -0.22367 | 0.0020014 | 0.0005016
81 | 0.98821 | -0.22669 | 0.0023911 | 0.00059925
82 | 0.98811 | -0.2287 | 0.004356 | 0.0010917
83 | 0.99662 | -0.064272 | 0.0028684 | 0.00071889
84 | 0.99666 | -0.063545 | 0.0015962 | 0.00040005
85 | 0.99685 | -0.059928 | 0.0017036 | 0.00042696
86 | 0.99687 | -0.059521 | 0.0016757 | 0.00041996
87 | 0.99701 | -0.056715 | 0 | 0
88 | 0.99596 | -0.076792 | 0 | 0
89 | 0.98864 | -0.21691 | 0.0036403 | 0.00091234
90 | 0.9876 | -0.23688 | 0.0046668 | 0.0011696
91 | 0.99157 | -0.16058 | 0 | 0
92 | 0.98709 | -0.24676 | 0.0029305 | 0.00073445
93 | 0.99346 | -0.12451 | 0.0019023 | 0.00047677
94 | 0.99151 | -0.16169 | 0.0012246 | 0.00030691
95 | 0.98661 | -0.25609 | 0 | 0
96 | 0.99147 | -0.16246 | 0.0022396 | 0.00056129
97 | 0.98654 | -0.25743 | 0.0021401 | 0.00053636
98 | 0.98633 | -0.26142 | 0.00096475 | 0.00024179
99 | 0.99492 | -0.096878 | 0.0019685 | 0.00049336
100 | 0.99141 | -0.16374 | 0.0006834 | 0.00017128
101 | 0.9865 | -0.2582 | 0.0022826 | 0.00057208
102 | 0.98543 | -0.27877 | 0.0016237 | 0.00040694
103 | 0.9946 | -0.10285 | 0.0017512 | 0.00043889
104 | 0.99269 | -0.13986 | 0.0018007 | 0.00045129
105 | 0.99218 | -0.14954 | 0.0073564 | 0.0018437
106 | 0.99192 | -0.15458 | 0 | 0
107 | 0.99042 | -0.18369 | 0 | 0
108 | 0.99136 | -0.16547 | 0.0043721 | 0.0010957
109 | 0.99009 | -0.19005 | 0.0042435 | 0.0010635
110 | 0.99037 | -0.18466 | 0.0027376 | 0.0006861
111 | 0.99121 | -0.16834 | 0.010128 | 0.0025384
112 | 0.98982 | -0.19542 | 0.0025026 | 0.00062722
113 | 0.99008 | -0.19033 | 0.0032318 | 0.00080997
114 | 0.98984 | -0.195 | 0.0020682 | 0.00051833
115 | 0.98987 | -0.19447 | 0.0046601 | 0.0011679
116 | 0.98961 | -0.19938 | 0 | 0
117 | 0.98983 | -0.19518 | 0.0061437 | 0.0015398
118 | 0.98959 | -0.1998 | 0.0061429 | 0.0015396
119 | 0.98913 | -0.20872 | 0.0079048 | 0.0019811
120 | 0.98958 | -0.20009 | 0.00284 | 0.00071177
121 | 0.98956 | -0.20033 | 0.0024444 | 0.00061263
122 | 0.98799 | -0.23101 | 0.004422 | 0.0011083
123 | 0.98794 | -0.23198 | 0 | 0
124 | 0.98787 | -0.23335 | 0.0026215 | 0.00065702
125 | 0.99136 | -0.16457 | 0.0011192 | 0.0002805
126 | 0.99135 | -0.16486 | 0.00056066 | 0.00014052
127 | 0.99134 | -0.16495 | 0.0003813 | 9.5563e-05
128 | 0.99133 | -0.16532 | 0.0010085 | 0.00025274
129 | 0.98168 | -0.35155 | 0.00044206 | 0.00011079
130 | 0.98347 | -0.31673 | 0.00060499 | 0.00015162
131 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0043499 | -0.0010898 | 0.00435 | 0.0010897 | 1.3327e-07 | -1.4129e-08 | 0.0066577 | 0.0066577 | 0.0066577 | 0.97219 | -0.53789 | 0.97222 | -0.53725 | 1.829
1 | 0.0037877 | 0.00094885 | -0.0037874 | -0.00094894 | 2.4456e-07 | -8.4079e-08 | 0.0057972 | 0.0057973 | 0.0057973 | 0.97219 | -0.53789 | 0.97212 | -0.53925 | 1.5927
2 | -0.005023 | -0.0012584 | 0.0050247 | 0.0012586 | 1.7077e-06 | 1.3705e-07 | 0.0076877 | 0.0076874 | 0.0076877 | 0.97222 | -0.53725 | 0.97258 | -0.53011 | 2.112
3 | 0.00061668 | 0.00015427 | -0.00061667 | -0.00015455 | 7.8004e-09 | -2.8446e-07 | 0.00094385 | 0.00094395 | 0.00094395 | 0.97212 | -0.53925 | 0.97211 | -0.53951 | 0.25933
4 | -0.0091119 | -0.0022814 | 0.0091156 | 0.0022832 | 3.7342e-06 | 1.7537e-06 | 0.01394 | 0.01394 | 0.01394 | 0.97258 | -0.53011 | 0.97302 | -0.5215 | 3.8297
5 | 0.0040871 | 0.0010229 | -0.0040871 | -0.0010229 | 7.4989e-08 | -1.548e-08 | 0.0062526 | 0.0062527 | 0.0062527 | 0.97258 | -0.53011 | 0.97256 | -0.5305 | 1.7178
6 | -0.012074 | -0.0030247 | 0.012077 | 0.0030262 | 2.7661e-06 | 1.5015e-06 | 0.018465 | 0.018464 | 0.018465 | 0.97302 | -0.5215 | 0.97326 | -0.51669 | 5.0727
7 | 0.0022616 | 0.00056537 | -0.0022613 | -0.00056598 | 2.8647e-07 | -6.0846e-07 | 0.0034598 | 0.00346 | 0.00346 | 0.97256 | -0.5305 | 0.97243 | -0.53316 | 0.95056
8 | -0.012077 | -0.0030262 | 0.01208 | 0.0030278 | 2.9894e-06 | 1.6226e-06 | 0.018464 | 0.018464 | 0.018464 | 0.97326 | -0.51669 | 0.97352 | -0.5115 | 5.0726
9 | 0.0022613 | 0.00056598 | -0.002261 | -0.00056666 | 3.24e-07 | -6.8773e-07 | 0.00346 | 0.0034604 | 0.0034604 | 0.97243 | -0.53316 | 0.97228 | -0.53617 | 0.95065
10 | 0.0015506 | 0.00038797 | -0.0015505 | -0.00038859 | 1.168e-07 | -6.219e-07 | 0.0023637 | 0.0023639 | 0.0023639 | 0.97606 | -0.46168 | 0.97598 | -0.46327 | 0.64943
11 | -0.0036965 | -0.00092579 | 0.003697 | 0.0009256 | 4.6901e-07 | -1.9218e-07 | 0.0056352 | 0.005635 | 0.0056352 | 0.97606 | -0.46168 | 0.9762 | -0.45902 | 1.5481
12 | -0.003697 | -0.0009256 | 0.0036975 | 0.00092541 | 4.6557e-07 | -1.9093e-07 | 0.005635 | 0.0056348 | 0.005635 | 0.9762 | -0.45902 | 0.97633 | -0.45637 | 1.5481
13 | 0.002239 | 0.00056094 | -0.0022389 | -0.00056112 | 8.2712e-08 | -1.8122e-07 | 0.0034222 | 0.0034222 | 0.0034222 | 0.97352 | -0.5115 | 0.97349 | -0.51227 | 0.94017
14 | -0.014319 | -0.0035887 | 0.014323 | 0.003591 | 3.8831e-06 | 2.2163e-06 | 0.021886 | 0.021886 | 0.021886 | 0.97352 | -0.5115 | 0.97381 | -0.50581 | 6.0128
15 | -0.0046994 | -0.0011765 | 0.0046995 | 0.0011765 | 8.0313e-08 | -8.1757e-10 | 0.0071618 | 0.0071618 | 0.0071618 | 0.97633 | -0.45637 | 0.97635 | -0.45601 | 1.9675
16 | 0.010816 | 0.0027116 | -0.010809 | -0.0027083 | 6.3925e-06 | 3.3038e-06 | 0.016466 | 0.016467 | 0.016467 | 0.97739 | -0.43548 | 0.97676 | -0.44789 | 4.5238
17 | -0.011876 | -0.0029773 | 0.011882 | 0.0029809 | 6.674e-06 | 3.5886e-06 | 0.01808 | 0.01808 | 0.01808 | 0.97739 | -0.43548 | 0.97799 | -0.42369 | 4.9671
18 | 0.0091534 | 0.0022934 | -0.0091519 | -0.0022927 | 1.502e-06 | 7.0351e-07 | 0.013944 | 0.013944 | 0.013944 | 0.97676 | -0.44789 | 0.97659 | -0.45133 | 3.8309
19 | -0.013107 | -0.0032878 | 0.013109 | 0.0032893 | 2.6486e-06 | 1.4722e-06 | 0.019943 | 0.019943 | 0.019943 | 0.97799 | -0.42369 | 0.97821 | -0.41945 | 5.4789
20 | -0.0069528 | -0.0017413 | 0.0069533 | 0.0017414 | 4.6577e-07 | 1.5973e-07 | 0.010596 | 0.010596 | 0.010596 | 0.97635 | -0.45601 | 0.97642 | -0.45461 | 2.911
21 | -0.022489 | -0.0056493 | 0.022516 | 0.005666 | 2.7155e-05 | 1.661e-05 | 0.034304 | 0.034303 | 0.034304 | 0.97565 | -0.46965 | 0.97693 | -0.44438 | 9.4241
22 | 0.02163 | 0.0054342 | -0.021626 | -0.0054315 | 4.3372e-06 | 2.6432e-06 | 0.032994 | 0.032994 | 0.032994 | 0.97565 | -0.46965 | 0.97543 | -0.47385 | 9.0644
23 | -0.024165 | -0.0060792 | 0.024194 | 0.0060969 | 2.8815e-05 | 1.7731e-05 | 0.036815 | 0.036815 | 0.036815 | 0.97693 | -0.44438 | 0.97821 | -0.41945 | 10.114
24 | 0.021207 | 0.0053264 | -0.021196 | -0.0053202 | 1.0329e-05 | 6.282e-06 | 0.032355 | 0.032355 | 0.032355 | 0.97543 | -0.47385 | 0.97492 | -0.48406 | 8.8887
25 | -0.0082516 | -0.0020668 | 0.0082528 | 0.0020673 | 1.2863e-06 | 5.5184e-07 | 0.012575 | 0.012574 | 0.012575 | 0.97642 | -0.45461 | 0.97659 | -0.45133 | 3.4545
26 | -0.018372 | -0.0046057 | 0.018378 | 0.0046097 | 6.8187e-06 | 4.0768e-06 | 0.028073 | 0.028073 | 0.028073 | 0.97381 | -0.50581 | 0.97421 | -0.49802 | 7.7123
27 | -0.019701 | -0.0049408 | 0.019713 | 0.0049477 | 1.143e-05 | 6.8958e-06 | 0.030093 | 0.030093 | 0.030093 | 0.97421 | -0.49802 | 0.97482 | -0.48586 | 8.2674
28 | 0.0013229 | 0.00033111 | -0.0013229 | -0.00033154 | 5.7626e-08 | -4.3175e-07 | 0.0020205 | 0.0020207 | 0.0020207 | 0.97421 | -0.49802 | 0.97416 | -0.49894 | 0.55512
29 | -0.020701 | -0.0051953 | 0.020702 | 0.0051964 | 1.7723e-06 | 1.0752e-06 | 0.031601 | 0.031601 | 0.031601 | 0.97482 | -0.48586 | 0.97492 | -0.48406 | 8.6816
30 | -0.037303 | -0.0093862 | 0.037342 | 0.0094107 | 3.8897e-05 | 2.449e-05 | 0.056758 | 0.056757 | 0.056758 | 0.97821 | -0.41945 | 0.97932 | -0.39765 | 15.5928
31 | -0.040912 | -0.010305 | 0.040937 | 0.010321 | 2.4923e-05 | 1.5734e-05 | 0.062182 | 0.062182 | 0.062182 | 0.97932 | -0.39765 | 0.97997 | -0.38492 | 17.0829
32 | -0.045033 | -0.011348 | 0.045053 | 0.01136 | 1.9753e-05 | 1.25e-05 | 0.068402 | 0.068402 | 0.068402 | 0.97997 | -0.38492 | 0.98044 | -0.37576 | 18.7917
33 | 0.0040965 | 0.0010264 | -0.0040962 | -0.0010265 | 3.4085e-07 | -7.7809e-08 | 0.0062201 | 0.0062203 | 0.0062203 | 0.97997 | -0.38492 | 0.97988 | -0.38667 | 1.7089
34 | -0.046461 | -0.011713 | 0.046477 | 0.011723 | 1.6612e-05 | 1.0519e-05 | 0.070538 | 0.070538 | 0.070538 | 0.98044 | -0.37576 | 0.98082 | -0.36829 | 19.3785
35 | 0.0023669 | 0.00059308 | -0.0023668 | -0.00059318 | 5.1949e-08 | -1.0183e-07 | 0.0035942 | 0.0035943 | 0.0035943 | 0.97988 | -0.38667 | 0.97986 | -0.38713 | 0.98744
36 | -0.0010421 | -0.00026119 | 0.0010421 | 0.00026118 | 7.5939e-10 | -9.6977e-09 | 0.0015826 | 0.0015826 | 0.0015826 | 0.97986 | -0.38715 | 0.97986 | -0.38713 | 0.43478
37 | -0.047803 | -0.012056 | 0.047844 | 0.012082 | 4.1276e-05 | 2.6153e-05 | 0.072549 | 0.072549 | 0.072549 | 0.98082 | -0.36829 | 0.98175 | -0.35027 | 19.9312
38 | 0.0015058 | 0.0003761 | -0.0015057 | -0.00037617 | 1.1227e-08 | -6.5522e-08 | 0.0022818 | 0.0022818 | 0.0022818 | 0.98175 | -0.35027 | 0.98174 | -0.35043 | 0.62687
39 | -0.04935 | -0.012458 | 0.049387 | 0.012481 | 3.707e-05 | 2.3501e-05 | 0.074831 | 0.074831 | 0.074831 | 0.98175 | -0.35027 | 0.98255 | -0.3346 | 20.558
40 | 0.0015057 | 0.00037617 | -0.0015057 | -0.00037629 | 2.2081e-08 | -1.2886e-07 | 0.0022818 | 0.0022819 | 0.0022819 | 0.98174 | -0.35043 | 0.98173 | -0.35073 | 0.62689
41 | -0.052866 | -0.013353 | 0.052877 | 0.01336 | 1.0638e-05 | 6.7524e-06 | 0.0801 | 0.0801 | 0.0801 | 0.98255 | -0.3346 | 0.98277 | -0.3304 | 22.0054
42 | 0.0007493 | 0.00018672 | -0.00074929 | -0.00018701 | 1.1419e-08 | -2.9136e-07 | 0.0011353 | 0.0011355 | 0.0011355 | 0.98173 | -0.35073 | 0.98171 | -0.35106 | 0.31194
43 | -0.053674 | -0.01356 | 0.053712 | 0.013584 | 3.7156e-05 | 2.359e-05 | 0.081307 | 0.081307 | 0.081307 | 0.98277 | -0.3304 | 0.98351 | -0.31597 | 22.3372
44 | 0.00044207 | 0.00011001 | -0.00044206 | -0.00011079 | 1.0445e-08 | -7.7801e-07 | 0.00066978 | 0.00067006 | 0.00067006 | 0.98171 | -0.35106 | 0.98168 | -0.35155 | 0.18408
45 | 0.0016835 | 0.00042146 | -0.0016835 | -0.00042156 | 2.1951e-08 | -1.0046e-07 | 0.0025469 | 0.002547 | 0.002547 | 0.98351 | -0.31597 | 0.9835 | -0.31625 | 0.69972
46 | -0.055395 | -0.014005 | 0.055426 | 0.014024 | 3.0445e-05 | 1.9339e-05 | 0.083854 | 0.083854 | 0.083854 | 0.98351 | -0.31597 | 0.9841 | -0.30452 | 23.0369
47 | 0.0011108 | 0.00027802 | -0.0011108 | -0.00027823 | 1.9002e-08 | -2.1553e-07 | 0.0016805 | 0.0016805 | 0.0016805 | 0.9835 | -0.31625 | 0.98348 | -0.31661 | 0.46169
48 | -0.058991 | -0.014918 | 0.059017 | 0.014934 | 2.5831e-05 | 1.6422e-05 | 0.089246 | 0.089246 | 0.089246 | 0.9841 | -0.30452 | 0.98457 | -0.29539 | 24.5181
49 | 0.00060499 | 0.00015148 | -0.00060499 | -0.00015162 | 3.7311e-09 | -1.483e-07 | 0.00091531 | 0.00091536 | 0.00091536 | 0.98348 | -0.31661 | 0.98347 | -0.31673 | 0.25147
50 | -0.062619 | -0.015837 | 0.062669 | 0.015869 | 4.9998e-05 | 3.181e-05 | 0.094689 | 0.094689 | 0.094689 | 0.98457 | -0.29539 | 0.98543 | -0.27877 | 26.0134
51 | -0.0039674 | -0.00099433 | 0.0039676 | 0.00099426 | 1.9606e-07 | -6.5562e-08 | 0.0059477 | 0.0059477 | 0.0059477 | 0.99258 | -0.14248 | 0.99263 | -0.14145 | 1.634
52 | -0.0096143 | -0.0024095 | 0.0096173 | 0.0024109 | 3.0136e-06 | 1.4284e-06 | 0.014412 | 0.014412 | 0.014412 | 0.99263 | -0.14145 | 0.99297 | -0.13487 | 3.9594
53 | -0.011122 | -0.002788 | 0.011124 | 0.0027891 | 1.9759e-06 | 1.0192e-06 | 0.016667 | 0.016667 | 0.016667 | 0.99297 | -0.13487 | 0.99316 | -0.13114 | 4.5789
54 | 0.021528 | 0.0054028 | -0.021521 | -0.0053984 | 7.2658e-06 | 4.4092e-06 | 0.032257 | 0.032257 | 0.032257 | 0.99316 | -0.13114 | 0.9928 | -0.13822 | 8.8619
55 | -0.032652 | -0.0081919 | 0.032692 | 0.0082167 | 3.965e-05 | 2.4803e-05 | 0.048925 | 0.048924 | 0.048925 | 0.99316 | -0.13114 | 0.99448 | -0.1057 | 13.4408
56 | 0.019963 | 0.005008 | -0.019954 | -0.0050028 | 8.7199e-06 | 5.2451e-06 | 0.029923 | 0.029923 | 0.029923 | 0.9928 | -0.13822 | 0.99232 | -0.14739 | 8.2205
57 | -0.034126 | -0.0085761 | 0.034158 | 0.0085959 | 3.1596e-05 | 1.9802e-05 | 0.05107 | 0.05107 | 0.05107 | 0.99448 | -0.1057 | 0.99548 | -0.086329 | 14.0303
58 | 0.016813 | 0.0042155 | -0.016811 | -0.0042142 | 2.1944e-06 | 1.2855e-06 | 0.025212 | 0.025212 | 0.025212 | 0.99232 | -0.14739 | 0.99218 | -0.15013 | 6.9264
59 | -0.034158 | -0.0085959 | 0.034164 | 0.0085997 | 6.0465e-06 | 3.7893e-06 | 0.05107 | 0.05107 | 0.05107 | 0.99548 | -0.086329 | 0.99568 | -0.082626 | 14.0302
60 | 0.013524 | 0.0033903 | -0.013522 | -0.0033895 | 1.5088e-06 | 8.3932e-07 | 0.020282 | 0.020282 | 0.020282 | 0.99218 | -0.15013 | 0.99206 | -0.15247 | 5.5721
61 | -0.03566 | -0.0089748 | 0.035684 | 0.0089894 | 2.3321e-05 | 1.464e-05 | 0.053307 | 0.053307 | 0.053307 | 0.99568 | -0.082626 | 0.99639 | -0.068952 | 14.6447
62 | 0.011985 | 0.0030042 | -0.011983 | -0.0030035 | 1.1934e-06 | 6.3665e-07 | 0.017976 | 0.017976 | 0.017976 | 0.99206 | -0.15247 | 0.99195 | -0.15456 | 4.9385
63 | 0.0093867 | 0.0023527 | -0.0093858 | -0.0023523 | 8.9385e-07 | 4.1689e-07 | 0.014081 | 0.014081 | 0.014081 | 0.99195 | -0.15456 | 0.99185 | -0.15656 | 3.8684
64 | 0.0078287 | 0.0019621 | -0.0078279 | -0.0019618 | 7.6766e-07 | 2.998e-07 | 0.011745 | 0.011745 | 0.011745 | 0.99185 | -0.15656 | 0.99174 | -0.15862 | 3.2267
65 | 0.013652 | 0.0034235 | -0.013645 | -0.0034197 | 6.7907e-06 | 3.7976e-06 | 0.02056 | 0.02056 | 0.02056 | 0.98808 | -0.22926 | 0.98754 | -0.2397 | 5.6483
66 | -0.025485 | -0.0063893 | 0.025507 | 0.0064029 | 2.1975e-05 | 1.3554e-05 | 0.038381 | 0.038381 | 0.038381 | 0.98808 | -0.22926 | 0.98901 | -0.21118 | 10.5442
67 | -0.033284 | -0.008352 | 0.033322 | 0.0083757 | 3.7864e-05 | 2.3716e-05 | 0.050082 | 0.050081 | 0.050082 | 0.98901 | -0.21118 | 0.99024 | -0.18736 | 13.7587
68 | 0.0061681 | 0.0015458 | -0.0061679 | -0.0015457 | 2.0989e-07 | 5.0008e-08 | 0.0092546 | 0.0092547 | 0.0092547 | 0.99174 | -0.15862 | 0.99171 | -0.15933 | 2.5425
69 | 0.0045258 | 0.0011342 | -0.0045255 | -0.0011342 | 2.2566e-07 | -2.3939e-08 | 0.0067907 | 0.0067908 | 0.0067908 | 0.99171 | -0.15933 | 0.99165 | -0.16038 | 1.8656
70 | 0.0016547 | 0.00041469 | -0.0016547 | -0.00041472 | 6.0492e-09 | -2.9883e-08 | 0.002483 | 0.002483 | 0.002483 | 0.99165 | -0.16038 | 0.99165 | -0.16045 | 0.68215
71 | 0.079134 | 0.020045 | -0.079026 | -0.019976 | 0.00010797 | 6.8833e-05 | 0.11825 | 0.11826 | 0.11826 | 0.99639 | -0.068952 | 0.9949 | -0.097402 | 32.4877
72 | -0.11482 | -0.029034 | 0.1152 | 0.029277 | 0.00038112 | 0.00024347 | 0.17156 | 0.17156 | 0.17156 | 0.99639 | -0.068952 | 1 | 0 | 47.1323
73 | 0.075914 | 0.019196 | -0.075699 | -0.019058 | 0.00021527 | 0.0001372 | 0.1136 | 0.1136 | 0.1136 | 0.9949 | -0.097402 | 0.99182 | -0.15671 | 31.2089
74 | 0.17447 | 0.044573 | -0.17417 | -0.044383 | 0.00029917 | 0.00019085 | 0.25991 | 0.25991 | 0.25991 | 1 | 0 | 0.99813 | -0.03553 | 35.7019
75 | 0.073295 | 0.018456 | -0.073188 | -0.018388 | 0.00010724 | 6.8326e-05 | 0.10999 | 0.10999 | 0.10999 | 0.99182 | -0.15671 | 0.99024 | -0.18736 | 30.2184
76 | 0.17273 | 0.044023 | -0.17268 | -0.043989 | 5.3984e-05 | 3.4437e-05 | 0.25777 | 0.25777 | 0.25777 | 0.99813 | -0.03553 | 0.99779 | -0.042008 | 35.4081
77 | 0.037703 | 0.00947 | -0.037676 | -0.009453 | 2.7092e-05 | 1.705e-05 | 0.056663 | 0.056663 | 0.056663 | 0.99024 | -0.18736 | 0.98946 | -0.20242 | 15.5668
78 | 0.17161 | 0.043721 | -0.17149 | -0.043644 | 0.00012167 | 7.7612e-05 | 0.25618 | 0.25618 | 0.25618 | 0.99779 | -0.042008 | 0.99701 | -0.056715 | 35.1897
79 | -0.033335 | -0.0083571 | 0.033344 | 0.0083629 | 9.1666e-06 | 5.742e-06 | 0.050165 | 0.050165 | 0.050165 | 0.98881 | -0.21511 | 0.98911 | -0.20934 | 13.7816
80 | 0.017821 | 0.0044691 | -0.017819 | -0.0044679 | 1.9507e-06 | 1.1557e-06 | 0.026819 | 0.026819 | 0.026819 | 0.98881 | -0.21511 | 0.98869 | -0.2174 | 7.3679
81 | -0.035059 | -0.0087927 | 0.03507 | 0.0088 | 1.1556e-05 | 7.2538e-06 | 0.052745 | 0.052745 | 0.052745 | 0.98911 | -0.20934 | 0.98946 | -0.20242 | 14.4904
82 | 0.015801 | 0.0039621 | -0.015796 | -0.0039593 | 4.7145e-06 | 2.7323e-06 | 0.023782 | 0.023782 | 0.023782 | 0.98869 | -0.2174 | 0.98837 | -0.22367 | 6.5334
83 | 0.013795 | 0.0034577 | -0.013793 | -0.0034566 | 1.9881e-06 | 1.1149e-06 | 0.020769 | 0.020769 | 0.020769 | 0.98837 | -0.22367 | 0.98821 | -0.22669 | 5.7057
84 | 0.011402 | 0.0028574 | -0.011401 | -0.0028568 | 1.0922e-06 | 5.7242e-07 | 0.017168 | 0.017168 | 0.017168 | 0.98821 | -0.22669 | 0.98811 | -0.2287 | 4.7166
85 | 0.0070446 | 0.0017651 | -0.0070438 | -0.0017648 | 7.7374e-07 | 2.6038e-07 | 0.010608 | 0.010609 | 0.010609 | 0.98811 | -0.2287 | 0.98799 | -0.23101 | 2.9144
86 | -0.0028684 | -0.00071889 | 0.0028685 | 0.00071877 | 9.9348e-08 | -1.2465e-07 | 0.0042827 | 0.0042826 | 0.0042827 | 0.99662 | -0.064272 | 0.99666 | -0.063545 | 1.1766
87 | -0.0044647 | -0.0011188 | 0.0044655 | 0.0011187 | 7.6907e-07 | -1.0943e-07 | 0.0066658 | 0.0066656 | 0.0066658 | 0.99666 | -0.063545 | 0.99685 | -0.059928 | 1.8313
88 | -0.006169 | -0.0015457 | 0.0061692 | 0.0015457 | 1.1984e-07 | 2.7565e-08 | 0.0092085 | 0.0092085 | 0.0092085 | 0.99685 | -0.059928 | 0.99687 | -0.059521 | 2.5298
89 | -0.0078448 | -0.0019656 | 0.0078459 | 0.0019661 | 1.0485e-06 | 4.0517e-07 | 0.01171 | 0.01171 | 0.01171 | 0.99687 | -0.059521 | 0.99701 | -0.056715 | 3.217
90 | 0.16365 | 0.041678 | -0.16349 | -0.041577 | 0.00015831 | 0.00010095 | 0.24447 | 0.24447 | 0.24447 | 0.99701 | -0.056715 | 0.99596 | -0.076792 | 33.5812
91 | 0.072654 | 0.018343 | -0.072584 | -0.018298 | 6.9841e-05 | 4.4493e-05 | 0.1086 | 0.1086 | 0.1086 | 0.99596 | -0.076792 | 0.99492 | -0.096878 | 29.8342
92 | 0.090833 | 0.023234 | -0.090623 | -0.0231 | 0.00020924 | 0.00013352 | 0.13588 | 0.13588 | 0.13588 | 0.99596 | -0.076792 | 0.99346 | -0.12451 | 37.3284
93 | 0.077488 | 0.019664 | -0.077414 | -0.019616 | 7.437e-05 | 4.741e-05 | 0.11672 | 0.11672 | 0.11672 | 0.98864 | -0.21691 | 0.9876 | -0.23688 | 32.0648
94 | -0.081128 | -0.020576 | 0.081349 | 0.020717 | 0.00022036 | 0.00014053 | 0.12219 | 0.12219 | 0.12219 | 0.98864 | -0.21691 | 0.99157 | -0.16058 | 33.57
95 | 0.072747 | 0.018447 | -0.072712 | -0.018425 | 3.4503e-05 | 2.1984e-05 | 0.10968 | 0.10968 | 0.10968 | 0.9876 | -0.23688 | 0.98709 | -0.24676 | 30.133
96 | -0.088567 | -0.022525 | 0.088721 | 0.022624 | 0.00015422 | 9.8399e-05 | 0.13303 | 0.13303 | 0.13303 | 0.99157 | -0.16058 | 0.99346 | -0.12451 | 36.5457
97 | 0.0072182 | 0.0018084 | -0.0072178 | -0.0018082 | 3.8287e-07 | 1.328e-07 | 0.010832 | 0.010832 | 0.010832 | 0.99157 | -0.16058 | 0.99151 | -0.16169 | 2.9758
98 | 0.069782 | 0.01769 | -0.069751 | -0.017671 | 3.1286e-05 | 1.9927e-05 | 0.10527 | 0.10527 | 0.10527 | 0.98709 | -0.24676 | 0.98661 | -0.25609 | 28.9194
99 | 0.0059932 | 0.0015013 | -0.005993 | -0.0015013 | 2.1784e-07 | 4.6804e-08 | 0.0089941 | 0.0089942 | 0.0089942 | 0.99151 | -0.16169 | 0.99147 | -0.16246 | 2.4709
100 | 0.0044231 | 0.0011082 | -0.0044228 | -0.0011083 | 2.8205e-07 | -3.5307e-08 | 0.0066709 | 0.006671 | 0.006671 | 0.98661 | -0.25609 | 0.98654 | -0.25743 | 1.8327
101 | 0.065327 | 0.016562 | -0.065311 | -0.016552 | 1.6732e-05 | 1.065e-05 | 0.098596 | 0.098596 | 0.098596 | 0.98661 | -0.25609 | 0.98633 | -0.26142 | 27.0868
102 | 0.0037534 | 0.00093999 | -0.0037532 | -0.0009401 | 2.2864e-07 | -1.0146e-07 | 0.005633 | 0.0056331 | 0.0056331 | 0.99147 | -0.16246 | 0.99141 | -0.16374 | 1.5475
103 | 0.0022827 | 0.00057189 | -0.0022826 | -0.00057208 | 8.43e-08 | -1.8817e-07 | 0.003443 | 0.0034431 | 0.0034431 | 0.98654 | -0.25743 | 0.9865 | -0.2582 | 0.9459
104 | 0.064346 | 0.01631 | -0.064292 | -0.016276 | 5.3588e-05 | 3.4103e-05 | 0.09714 | 0.09714 | 0.09714 | 0.98633 | -0.26142 | 0.98543 | -0.27877 | 26.6869
105 | 0.070616 | 0.017805 | -0.070596 | -0.017792 | 2.0192e-05 | 1.286e-05 | 0.10565 | 0.10565 | 0.10565 | 0.99492 | -0.096878 | 0.9946 | -0.10285 | 29.0254
106 | 0.0030698 | 0.00076882 | -0.0030697 | -0.00076894 | 1.2211e-07 | -1.1964e-07 | 0.0046073 | 0.0046074 | 0.0046074 | 0.99141 | -0.16374 | 0.99136 | -0.16457 | 1.2658
107 | 0.068844 | 0.017353 | -0.068723 | -0.017276 | 0.00012167 | 7.7471e-05 | 0.10303 | 0.10303 | 0.10303 | 0.9946 | -0.10285 | 0.99269 | -0.13986 | 28.3056
108 | 0.066922 | 0.016825 | -0.066891 | -0.016805 | 3.093e-05 | 1.969e-05 | 0.10033 | 0.10033 | 0.10033 | 0.99269 | -0.13986 | 0.99218 | -0.14954 | 27.5641
109 | 0.059535 | 0.014961 | -0.05952 | -0.014952 | 1.4315e-05 | 9.0999e-06 | 0.089301 | 0.089301 | 0.089301 | 0.99218 | -0.14954 | 0.99192 | -0.15458 | 24.5332
110 | 0.045011 | 0.011313 | -0.044949 | -0.011273 | 6.2449e-05 | 3.9497e-05 | 0.067534 | 0.067534 | 0.067534 | 0.99192 | -0.15458 | 0.99042 | -0.18369 | 18.5533
111 | 0.014509 | 0.0036391 | -0.014502 | -0.0036349 | 7.5246e-06 | 4.2694e-06 | 0.021767 | 0.021767 | 0.021767 | 0.99192 | -0.15458 | 0.99136 | -0.16547 | 5.98
112 | 0.018185 | 0.0045612 | -0.01818 | -0.0045579 | 5.5111e-06 | 3.2739e-06 | 0.027323 | 0.027323 | 0.027323 | 0.99042 | -0.18369 | 0.99009 | -0.19005 | 7.5062
113 | 0.026764 | 0.0067122 | -0.026762 | -0.0067115 | 1.245e-06 | 7.7041e-07 | 0.040211 | 0.040211 | 0.040211 | 0.99042 | -0.18369 | 0.99037 | -0.18466 | 11.0471
114 | 0.01013 | 0.0025391 | -0.010128 | -0.0025384 | 1.388e-06 | 6.8194e-07 | 0.015205 | 0.015205 | 0.015205 | 0.99136 | -0.16547 | 0.99121 | -0.16834 | 4.1772
115 | 0.013936 | 0.0034944 | -0.013932 | -0.0034924 | 3.5655e-06 | 2.0033e-06 | 0.020945 | 0.020945 | 0.020945 | 0.99009 | -0.19005 | 0.98982 | -0.19542 | 5.7542
116 | 0.024025 | 0.0060254 | -0.024018 | -0.0060214 | 6.4838e-06 | 3.9789e-06 | 0.036098 | 0.036098 | 0.036098 | 0.99037 | -0.18466 | 0.99008 | -0.19033 | 9.9171
117 | 0.01143 | 0.0028652 | -0.011427 | -0.0028639 | 2.387e-06 | 1.2506e-06 | 0.017183 | 0.017183 | 0.017183 | 0.98982 | -0.19542 | 0.98959 | -0.1998 | 4.7206
118 | 0.0099803 | 0.0025026 | -0.0099781 | -0.0025015 | 2.223e-06 | 1.084e-06 | 0.015 | 0.015 | 0.015 | 0.99008 | -0.19033 | 0.98984 | -0.195 | 4.121
119 | 0.010806 | 0.0027088 | -0.010804 | -0.0027077 | 2.135e-06 | 1.0889e-06 | 0.016241 | 0.016241 | 0.016241 | 0.99008 | -0.19033 | 0.98987 | -0.19447 | 4.4618
120 | 0.0079099 | 0.0019832 | -0.0079083 | -0.0019825 | 1.6499e-06 | 6.5607e-07 | 0.011891 | 0.011891 | 0.011891 | 0.98984 | -0.195 | 0.98961 | -0.19938 | 3.2669
121 | 0.0061439 | 0.0015398 | -0.0061437 | -0.0015398 | 2.0714e-07 | 4.933e-08 | 0.0092359 | 0.0092359 | 0.0092359 | 0.98987 | -0.19447 | 0.98983 | -0.19518 | 2.5373
122 | 0.0079083 | 0.0019825 | -0.0079048 | -0.0019811 | 3.5193e-06 | 1.4001e-06 | 0.011891 | 0.011892 | 0.011892 | 0.98961 | -0.19938 | 0.98913 | -0.20872 | 3.2669
123 | 0.0052845 | 0.0013244 | -0.0052845 | -0.0013244 | 7.3178e-08 | 7.1285e-09 | 0.0079462 | 0.0079462 | 0.0079462 | 0.98959 | -0.1998 | 0.98958 | -0.20009 | 2.183
124 | 0.0024444 | 0.00061258 | -0.0024444 | -0.00061263 | 2.7868e-08 | -5.283e-08 | 0.0036757 | 0.0036757 | 0.0036757 | 0.98958 | -0.20009 | 0.98956 | -0.20033 | 1.0098
125 | 0.0026218 | 0.00065657 | -0.0026217 | -0.00065675 | 1.2119e-07 | -1.8786e-07 | 0.0039486 | 0.0039487 | 0.0039487 | 0.98799 | -0.23101 | 0.98794 | -0.23198 | 1.0848
126 | 0.0026217 | 0.00065675 | -0.0026215 | -0.00065702 | 1.7147e-07 | -2.6574e-07 | 0.0039487 | 0.0039488 | 0.0039488 | 0.98794 | -0.23198 | 0.98787 | -0.23335 | 1.0848
127 | 0.0019505 | 0.00048844 | -0.0019504 | -0.00048853 | 2.7117e-08 | -9.1435e-08 | 0.0029275 | 0.0029275 | 0.0029275 | 0.99136 | -0.16457 | 0.99135 | -0.16486 | 0.80426
128 | 0.0013898 | 0.00034801 | -0.0013898 | -0.00034806 | 5.7901e-09 | -4.2046e-08 | 0.002086 | 0.002086 | 0.002086 | 0.99135 | -0.16486 | 0.99134 | -0.16495 | 0.57307
129 | 0.0010085 | 0.00025249 | -0.0010085 | -0.00025274 | 1.7503e-08 | -2.5144e-07 | 0.0015136 | 0.0015137 | 0.0015137 | 0.99134 | -0.16495 | 0.99133 | -0.16532 | 0.41586

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29506 | 0.074789

## res_load
| p_mw | q_mvar
0 | 0.00056219 | 0.0001409
1 | 0.00067303 | 0.00016868
2 | 0.0031708 | 0.00079467
3 | 0.00061667 | 0.00015455
4 | 0.0029587 | 0.00074152
5 | 0.0018254 | 0.0004575
6 | 0.0021459 | 0.00053782
7 | 0.0015505 | 0.00038859
8 | 0.002261 | 0.00056666
9 | 0.0010019 | 0.0002511
10 | 0.00106 | 0.00026566
11 | 0.0016557 | 0.00041496
12 | 0.0012246 | 0.00030693
13 | 0.0022534 | 0.00056475
14 | 0.0008585 | 0.00021516
15 | 0.0016488 | 0.00041323
16 | 0.00041939 | 0.00010511
17 | 0.0012982 | 0.00032537
18 | 0.00089908 | 0.00022533
19 | 0.0040487 | 0.0010147
20 | 0.00098787 | 0.00024758
21 | 0.0013229 | 0.00033154
22 | 0.0022389 | 0.00056112
23 | 0.0004938 | 0.00012376
24 | 0.0035699 | 0.00089471
25 | 0.0014075 | 0.00035275
26 | 0.0017293 | 0.0004334
27 | 0.0010421 | 0.00026119
28 | 0.0013247 | 0.000332
29 | 0.0013259 | 0.0003323
30 | 0.0034789 | 0.0008719
31 | 0.00075642 | 0.00018958
32 | 0.00079766 | 0.00019991
33 | 0.00030722 | 7.6998e-05
34 | 0.00057273 | 0.00014354
35 | 0.0035658 | 0.00089367
36 | 0.00050577 | 0.00012676
37 | 0.0036015 | 0.00090261
38 | 0.0039674 | 0.00099433
39 | 0.0056467 | 0.0014152
40 | 0.0015049 | 0.00037715
41 | 0.0015578 | 0.00039042
42 | 0.001434 | 0.0003594
43 | 0.0031414 | 0.0007873
44 | 0.0032872 | 0.00082384
45 | 0.0014966 | 0.00037509
46 | 0.0015375 | 0.00038533
47 | 0.0025967 | 0.0006508
48 | 0.0015571 | 0.00039025
49 | 0.011834 | 0.0029658
50 | 0.013645 | 0.0034197
51 | 0.007777 | 0.0019491
52 | 0.0016598 | 0.00041599
53 | 0.0016421 | 0.00041156
54 | 0.0028708 | 0.00071949
55 | 0.0016547 | 0.00041472
56 | 0.0031123 | 0.00078002
57 | 0.0037439 | 0.0009383
58 | 0.0024033 | 0.00060232
59 | 0.0014347 | 0.00035956
60 | 0.0021629 | 0.00054208
61 | 0.0010663 | 0.00026725
62 | 0.015514 | 0.0038881
63 | 0.0017151 | 0.00042984
64 | 0.0020183 | 0.00050583
65 | 0.0026055 | 0.000653
66 | 0.0020014 | 0.0005016
67 | 0.0023911 | 0.00059925
68 | 0.004356 | 0.0010917
69 | 0.0028684 | 0.00071889
70 | 0.0015962 | 0.00040005
71 | 0.0017036 | 0.00042696
72 | 0.0016757 | 0.00041996
73 | 0.0036403 | 0.00091234
74 | 0.0046668 | 0.0011696
75 | 0.0029305 | 0.00073445
76 | 0.0019023 | 0.00047677
77 | 0.0012246 | 0.00030691
78 | 0.0022396 | 0.00056129
79 | 0.0021401 | 0.00053636
80 | 0.00096475 | 0.00024179
81 | 0.0019685 | 0.00049336
82 | 0.0006834 | 0.00017128
83 | 0.0022826 | 0.00057208
84 | 0.0016237 | 0.00040694
85 | 0.0017512 | 0.00043889
86 | 0.0018007 | 0.00045129
87 | 0.0073564 | 0.0018437
88 | 0.0043721 | 0.0010957
89 | 0.0042435 | 0.0010635
90 | 0.0027376 | 0.0006861
91 | 0.010128 | 0.0025384
92 | 0.0025026 | 0.00062722
93 | 0.0032318 | 0.00080997
94 | 0.0020682 | 0.00051833
95 | 0.0046601 | 0.0011679
96 | 0.0061437 | 0.0015398
97 | 0.0061429 | 0.0015396
98 | 0.0079048 | 0.0019811
99 | 0.00284 | 0.00071177
100 | 0.0024444 | 0.00061263
101 | 0.004422 | 0.0011083
102 | 0.0026215 | 0.00065702
103 | 0.0011192 | 0.0002805
104 | 0.00056066 | 0.00014052
105 | 0.0003813 | 9.5563e-05
106 | 0.0010085 | 0.00025274
107 | 0.00044206 | 0.00011079
108 | 0.00060499 | 0.00015162

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1