## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3273-1_1_4_node_13 | 0.4 | n |  | TRUE
1 | bus_LV_3273-1_1_4_node_14 | 0.4 | n |  | TRUE
2 | bus_LV_3273-1_1_4_node_16 | 0.4 | n |  | TRUE
3 | bus_LV_3273-1_1_4_node_238 | 0.4 | n |  | TRUE
4 | bus_LV_3273-1_1_4_node_239 | 0.4 | n |  | TRUE
5 | bus_LV_3273-1_1_4_node_17 | 0.4 | n |  | TRUE
6 | bus_LV_3273-1_1_4_node_237 | 0.4 | n |  | TRUE
7 | bus_LV_3273-1_1_4_node_204 | 0.4 | n |  | TRUE
8 | bus_LV_3273-1_1_4_node_203 | 0.4 | n |  | TRUE
9 | bus_LV_3273-1_1_4_node_117 | 0.4 | n |  | TRUE
10 | bus_LV_3273-1_1_4_node_118 | 0.4 | n |  | TRUE
11 | bus_LV_3273-1_1_4_node_129 | 0.4 | n |  | TRUE
12 | bus_LV_3273-1_1_4_node_120 | 0.4 | n |  | TRUE
13 | bus_LV_3273-1_1_4_node_125 | 0.4 | n |  | TRUE
14 | bus_LV_3273-1_1_4_node_137 | 0.4 | n |  | TRUE
15 | bus_LV_3273-1_1_4_node_145 | 0.4 | n |  | TRUE
16 | bus_LV_3273-1_1_4_node_146 | 0.4 | n |  | TRUE
17 | bus_LV_3273-1_1_4_node_144 | 0.4 | n |  | TRUE
18 | bus_LV_3273-1_1_4_node_138 | 0.4 | n |  | TRUE
19 | bus_LV_3273-1_1_4_node_130 | 0.4 | n |  | TRUE
20 | bus_LV_3273-1_1_4_node_131 | 0.4 | n |  | TRUE
21 | bus_LV_3273-1_1_4_node_132 | 0.4 | n |  | TRUE
22 | bus_LV_3273-1_1_4_node_133 | 0.4 | n |  | TRUE
23 | bus_LV_3273-1_1_4_node_134 | 0.4 | n |  | TRUE
24 | bus_LV_3273-1_1_4_node_135 | 0.4 | n |  | TRUE
25 | bus_LV_3273-1_1_4_node_136 | 0.4 | n |  | TRUE
26 | bus_LV_3273-1_1_4_node_225 | 0.4 | n |  | TRUE
27 | bus_LV_3273-1_1_4_node_220 | 0.4 | n |  | TRUE
28 | bus_LV_3273-1_1_4_node_221 | 0.4 | n |  | TRUE
29 | bus_LV_3273-1_1_4_node_231 | 0.4 | n |  | TRUE
30 | bus_LV_3273-1_1_4_node_218 | 0.4 | n |  | TRUE
31 | bus_LV_3273-1_1_4_node_141 | 0.4 | n |  | TRUE
32 | bus_LV_3273-1_1_4_node_139 | 0.4 | n |  | TRUE
33 | bus_LV_3273-1_1_4_node_140 | 0.4 | n |  | TRUE
34 | bus_LV_3273-1_1_4_node_142 | 0.4 | n |  | TRUE
35 | bus_LV_3273-1_1_4_node_222 | 0.4 | n |  | TRUE
36 | bus_LV_3273-1_1_4_node_224 | 0.4 | n |  | TRUE
37 | bus_LV_3273-1_1_4_node_143 | 0.4 | n |  | TRUE
38 | bus_LV_3273-1_1_4_node_147 | 0.4 | n |  | TRUE
39 | bus_LV_3273-1_1_4_node_148 | 0.4 | n |  | TRUE
40 | bus_LV_3273-1_1_4_node_149 | 0.4 | n |  | TRUE
41 | bus_LV_3273-1_1_4_node_150 | 0.4 | n |  | TRUE
42 | bus_LV_3273-1_1_4_node_151 | 0.4 | n |  | TRUE
43 | bus_LV_3273-1_1_4_node_152 | 0.4 | n |  | TRUE
44 | bus_LV_3273-1_1_4_node_153 | 0.4 | n |  | TRUE
45 | bus_LV_3273-1_1_4_node_155 | 0.4 | n |  | TRUE
46 | bus_LV_3273-1_1_4_node_154 | 0.4 | n |  | TRUE
47 | bus_LV_3273-1_1_4_node_156 | 0.4 | n |  | TRUE
48 | bus_LV_3273-1_1_4_node_174 | 0.4 | n |  | TRUE
49 | bus_LV_3273-1_1_4_node_173 | 0.4 | n |  | TRUE
50 | bus_LV_3273-1_1_4_node_160 | 0.4 | n |  | TRUE
51 | bus_LV_3273-1_1_4_node_157 | 0.4 | n |  | TRUE
52 | bus_LV_3273-1_1_4_node_158 | 0.4 | n |  | TRUE
53 | bus_LV_3273-1_1_4_node_159 | 0.4 | n |  | TRUE
54 | bus_LV_3273-1_1_4_node_161 | 0.4 | n |  | TRUE
55 | bus_LV_3273-1_1_4_node_162 | 0.4 | n |  | TRUE
56 | bus_LV_3273-1_1_4_node_164 | 0.4 | n |  | TRUE
57 | bus_LV_3273-1_1_4_node_165 | 0.4 | n |  | TRUE
58 | bus_LV_3273-1_1_4_node_166 | 0.4 | n |  | TRUE
59 | bus_LV_3273-1_1_4_node_167 | 0.4 | n |  | TRUE
60 | bus_LV_3273-1_1_4_node_243 | 0.4 | n |  | TRUE
61 | bus_LV_3273-1_1_4_node_168 | 0.4 | n |  | TRUE
62 | bus_LV_3273-1_1_4_node_169 | 0.4 | n |  | TRUE
63 | bus_LV_3273-1_1_4_node_185 | 0.4 | n |  | TRUE
64 | bus_LV_3273-1_1_4_node_184 | 0.4 | n |  | TRUE
65 | bus_LV_3273-1_1_4_node_170 | 0.4 | n |  | TRUE
66 | bus_LV_3273-1_1_4_node_186 | 0.4 | n |  | TRUE
67 | bus_LV_3273-1_1_4_node_182 | 0.4 | n |  | TRUE
68 | bus_LV_3273-1_1_4_node_171 | 0.4 | n |  | TRUE
69 | bus_LV_3273-1_1_4_node_172 | 0.4 | n |  | TRUE
70 | bus_LV_3273-1_1_4_node_175 | 0.4 | n |  | TRUE
71 | bus_LV_3273-1_1_4_node_176 | 0.4 | n |  | TRUE
72 | bus_LV_3273-1_1_4_node_177 | 0.4 | n |  | TRUE
73 | bus_LV_3273-1_1_4_node_178 | 0.4 | n |  | TRUE
74 | bus_LV_3273-1_1_4_node_179 | 0.4 | n |  | TRUE
75 | bus_LV_3273-1_1_4_node_180 | 0.4 | n |  | TRUE
76 | bus_LV_3273-1_1_4_node_189 | 0.4 | n |  | TRUE
77 | bus_LV_3273-1_1_4_node_183 | 0.4 | n |  | TRUE
78 | bus_LV_3273-1_1_4_node_190 | 0.4 | n |  | TRUE
79 | bus_LV_3273-1_1_4_node_181 | 0.4 | n |  | TRUE
80 | bus_LV_3273-1_1_4_node_187 | 0.4 | n |  | TRUE
81 | bus_LV_3273-1_1_4_node_188 | 0.4 | n |  | TRUE
82 | bus_LV_3273-1_1_4_node_199 | 0.4 | n |  | TRUE
83 | bus_LV_3273-1_1_4_node_201 | 0.4 | n |  | TRUE
84 | bus_LV_3273-1_1_4_node_198 | 0.4 | n |  | TRUE
85 | bus_LV_3273-1_1_4_node_202 | 0.4 | n |  | TRUE
86 | bus_LV_3273-1_1_4_node_191 | 0.4 | n |  | TRUE
87 | bus_LV_3273-1_1_4_node_192 | 0.4 | n |  | TRUE
88 | bus_LV_3273-1_1_4_node_193 | 0.4 | n |  | TRUE
89 | bus_LV_3273-1_1_4_node_194 | 0.4 | n |  | TRUE
90 | bus_LV_3273-1_1_4_node_195 | 0.4 | n |  | TRUE
91 | bus_LV_3273-1_1_4_node_196 | 0.4 | n |  | TRUE
92 | bus_LV_3273-1_1_4_node_207 | 0.4 | n |  | TRUE
93 | bus_LV_3273-1_1_4_node_197 | 0.4 | n |  | TRUE
94 | bus_LV_3273-1_1_4_node_215 | 0.4 | n |  | TRUE
95 | bus_LV_3273-1_1_4_node_200 | 0.4 | n |  | TRUE
96 | bus_LV_3273-1_1_4_node_205 | 0.4 | n |  | TRUE
97 | bus_LV_3273-1_1_4_node_206 | 0.4 | n |  | TRUE
98 | bus_LV_3273-1_1_4_node_212 | 0.4 | n |  | TRUE
99 | bus_LV_3273-1_1_4_node_213 | 0.4 | n |  | TRUE
100 | bus_LV_3273-1_1_4_node_210 | 0.4 | n |  | TRUE
101 | bus_LV_3273-1_1_4_node_240 | 0.4 | n |  | TRUE
102 | bus_LV_3273-1_1_4_node_216 | 0.4 | n |  | TRUE
103 | bus_LV_3273-1_1_4_node_208 | 0.4 | n |  | TRUE
104 | bus_LV_3273-1_1_4_node_209 | 0.4 | n |  | TRUE
105 | bus_LV_3273-1_1_4_node_211 | 0.4 | n |  | TRUE
106 | bus_LV_3273-1_1_4_node_214 | 0.4 | n |  | TRUE
107 | bus_LV_3273-1_1_4_node_219 | 0.4 | n |  | TRUE
108 | bus_LV_3273-1_1_4_node_217 | 0.4 | n |  | TRUE
109 | bus_LV_3273-1_1_4_node_223 | 0.4 | n |  | TRUE
110 | bus_LV_3273-1_1_4_node_232 | 0.4 | n |  | TRUE
111 | bus_LV_3273-1_1_4_node_226 | 0.4 | n |  | TRUE
112 | bus_LV_3273-1_1_4_node_227 | 0.4 | n |  | TRUE
113 | bus_LV_3273-1_1_4_node_228 | 0.4 | n |  | TRUE
114 | bus_LV_3273-1_1_4_node_229 | 0.4 | n |  | TRUE
115 | bus_LV_3273-1_1_4_node_230 | 0.4 | n |  | TRUE
116 | bus_LV_3273-1_1_4_node_234 | 0.4 | n |  | TRUE
117 | bus_LV_3273-1_1_4_node_235 | 0.4 | n |  | TRUE
118 | bus_LV_3273-1_1_4_node_236 | 0.4 | n |  | TRUE
119 | bus_MV_237_0_node_133 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3273-1_1_4_load_13 | 0 | 0.00097005 | 0.00024312 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3273-1_1_4_load_14 | 1 | 0.00042271 | 0.00010594 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3273-1_1_4_load_16 | 2 | 0.00082412 | 0.00020654 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3273-1_1_4_load_239 | 4 | 0.0017774 | 0.00044546 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3273-1_1_4_load_237 | 6 | 0.002063 | 0.00051703 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3273-1_1_4_load_204 | 7 | 0.00044242 | 0.00011088 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3273-1_1_4_load_203 | 8 | 0.0004424 | 0.00011088 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3273-1_1_4_load_117 | 9 | 0.018526 | 0.004643 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3273-1_1_4_load_118 | 10 | 0.0044106 | 0.0011054 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3273-1_1_4_load_129 | 11 | 0.0036388 | 0.00091196 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3273-1_1_4_load_120 | 12 | 0.0032523 | 0.0008151 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3273-1_1_4_load_125 | 13 | 0.018682 | 0.0046822 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3273-1_1_4_load_137 | 14 | 0.012952 | 0.003246 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3273-1_1_4_load_146 | 16 | 0.0022868 | 0.00057314 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3273-1_1_4_load_144 | 17 | 0.0095258 | 0.0023874 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3273-1_1_4_load_138 | 18 | 0.00088855 | 0.00022269 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3273-1_1_4_load_130 | 19 | 0.0026361 | 0.00066066 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3273-1_1_4_load_131 | 20 | 0.0023946 | 0.00060014 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3273-1_1_4_load_132 | 21 | 0.00093162 | 0.00023349 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3273-1_1_4_load_133 | 22 | 0.0036812 | 0.00092259 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3273-1_1_4_load_134 | 23 | 0.0012535 | 0.00031415 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3273-1_1_4_load_135 | 24 | 0.0010153 | 0.00025447 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3273-1_1_4_load_136 | 25 | 0.0012049 | 0.00030197 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3273-1_1_4_load_225 | 26 | 0.0028286 | 0.00070892 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3273-1_1_4_load_220 | 27 | 0.0013458 | 0.00033728 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3273-1_1_4_load_221 | 28 | 0.0010653 | 0.00026699 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3273-1_1_4_load_218 | 30 | 0.001415 | 0.00035464 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3273-1_1_4_load_140 | 33 | 0.0017093 | 0.00042839 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3273-1_1_4_load_142 | 34 | 0.0034475 | 0.00086402 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3273-1_1_4_load_222 | 35 | 0.0019407 | 0.00048638 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3273-1_1_4_load_224 | 36 | 0.0018871 | 0.00047294 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3273-1_1_4_load_143 | 37 | 0.0086627 | 0.0021711 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3273-1_1_4_load_147 | 38 | 0.0049723 | 0.0012462 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3273-1_1_4_load_148 | 39 | 0.018708 | 0.0046886 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3273-1_1_4_load_149 | 40 | 0.022934 | 0.0057479 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3273-1_1_4_load_151 | 42 | 0.012524 | 0.0031389 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3273-1_1_4_load_152 | 43 | 0.010574 | 0.0026501 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3273-1_1_4_load_153 | 44 | 0.001901 | 0.00047645 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3273-1_1_4_load_154 | 46 | 0.0035559 | 0.0008912 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3273-1_1_4_load_174 | 48 | 0.0023624 | 0.00059208 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3273-1_1_4_load_173 | 49 | 0.0019232 | 0.000482 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3273-1_1_4_load_160 | 50 | 0.016391 | 0.0041079 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3273-1_1_4_load_157 | 51 | 0.015341 | 0.0038449 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3273-1_1_4_load_158 | 52 | 0.016437 | 0.0041195 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3273-1_1_4_load_161 | 54 | 0.0048753 | 0.0012219 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3273-1_1_4_load_162 | 55 | 0.005401 | 0.0013536 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3273-1_1_4_load_164 | 56 | 0.002785 | 0.00069799 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3273-1_1_4_load_165 | 57 | 0.001747 | 0.00043783 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3273-1_1_4_load_167 | 59 | 0.0014614 | 0.00036627 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3273-1_1_4_load_243 | 60 | 0.0010131 | 0.00025392 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3273-1_1_4_load_169 | 62 | 0.0014327 | 0.00035906 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3273-1_1_4_load_185 | 63 | 0.0029911 | 0.00074963 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3273-1_1_4_load_184 | 64 | 0.0020433 | 0.00051211 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3273-1_1_4_load_170 | 65 | 0.0016074 | 0.00040285 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3273-1_1_4_load_182 | 67 | 0.00095421 | 0.00023915 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3273-1_1_4_load_171 | 68 | 0.0021106 | 0.00052896 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3273-1_1_4_load_172 | 69 | 0.0034538 | 0.0008656 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3273-1_1_4_load_175 | 70 | 0.0014473 | 0.00036273 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3273-1_1_4_load_176 | 71 | 0.00227 | 0.00056892 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3273-1_1_4_load_177 | 72 | 0.001493 | 0.00037419 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3273-1_1_4_load_178 | 73 | 0.0015097 | 0.00037837 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3273-1_1_4_load_179 | 74 | 0.0014584 | 0.00036552 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3273-1_1_4_load_180 | 75 | 0.001467 | 0.00036767 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3273-1_1_4_load_189 | 76 | 0.0015951 | 0.00039976 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3273-1_1_4_load_183 | 77 | 0.0032546 | 0.00081568 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3273-1_1_4_load_190 | 78 | 0.00082841 | 0.00020762 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3273-1_1_4_load_181 | 79 | 0.0031878 | 0.00079894 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3273-1_1_4_load_187 | 80 | 0.0014866 | 0.00037258 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3273-1_1_4_load_188 | 81 | 0.001471 | 0.00036867 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3273-1_1_4_load_199 | 82 | 0.0023021 | 0.00057696 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3273-1_1_4_load_201 | 83 | 0.00044832 | 0.00011236 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3273-1_1_4_load_202 | 85 | 0.00050629 | 0.00012689 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3273-1_1_4_load_191 | 86 | 0.0029346 | 0.00073547 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3273-1_1_4_load_192 | 87 | 0.0016775 | 0.00042043 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3273-1_1_4_load_193 | 88 | 0.0034893 | 0.0008745 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3273-1_1_4_load_194 | 89 | 0.001987 | 0.00049799 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3273-1_1_4_load_195 | 90 | 0.0029267 | 0.00073349 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3273-1_1_4_load_196 | 91 | 0.0017784 | 0.00044571 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3273-1_1_4_load_207 | 92 | 0.0024653 | 0.00061787 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3273-1_1_4_load_197 | 93 | 0.0015701 | 0.0003935 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3273-1_1_4_load_215 | 94 | 0.001908 | 0.00047818 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3273-1_1_4_load_200 | 95 | 0.0017066 | 0.00042771 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3273-1_1_4_load_205 | 96 | 0.0020078 | 0.00050319 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3273-1_1_4_load_212 | 98 | 0.0017902 | 0.00044866 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3273-1_1_4_load_213 | 99 | 0.0014472 | 0.0003627 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3273-1_1_4_load_210 | 100 | 0.0010584 | 0.00026527 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3273-1_1_4_load_240 | 101 | 0.0011841 | 0.00029677 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3273-1_1_4_load_216 | 102 | 0.0017572 | 0.00044038 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3273-1_1_4_load_208 | 103 | 0.0015919 | 0.00039897 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3273-1_1_4_load_209 | 104 | 0.0021774 | 0.0005457 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3273-1_1_4_load_211 | 105 | 0.001106 | 0.0002772 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3273-1_1_4_load_214 | 106 | 0.0010935 | 0.00027404 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3273-1_1_4_load_219 | 107 | 0.0016012 | 0.0004013 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3273-1_1_4_load_217 | 108 | 0.0037865 | 0.00094899 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3273-1_1_4_load_223 | 109 | 0.0035346 | 0.00088585 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3273-1_1_4_load_232 | 110 | 0.0024819 | 0.00062204 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3273-1_1_4_load_226 | 111 | 0.0015517 | 0.00038889 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3273-1_1_4_load_227 | 112 | 0.00051612 | 0.00012935 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3273-1_1_4_load_228 | 113 | 0.0017458 | 0.00043753 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3273-1_1_4_load_229 | 114 | 0.0017524 | 0.00043918 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3273-1_1_4_load_230 | 115 | 0.0015272 | 0.00038276 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3273-1_1_4_load_234 | 116 | 0.0014728 | 0.00036912 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3273-1_1_4_load_235 | 117 | 0.0015741 | 0.00039451 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 78 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3273-1_1_4_line_0 |  | 0 | 1 | 0.031553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3273-1_1_4_line_1 |  | 1 | 2 | 0.0056079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3273-1_1_4_line_2 |  | 2 | 5 | 0.0589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3273-1_1_4_line_3 |  | 3 | 4 | 0.035937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3273-1_1_4_line_4 |  | 3 | 5 | 0.097819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3273-1_1_4_line_5 |  | 3 | 6 | 0.018319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3273-1_1_4_line_6 |  | 4 | 101 | 0.028509 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3273-1_1_4_line_7 |  | 6 | 118 | 0.041039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3273-1_1_4_line_8 |  | 7 | 8 | 0.020229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3273-1_1_4_line_9 |  | 8 | 85 | 0.019272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3273-1_1_4_line_10 |  | 9 | 10 | 0.0099824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3273-1_1_4_line_11 |  | 9 | 11 | 0.059981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3273-1_1_4_line_12 |  | 10 | 12 | 0.014708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3273-1_1_4_line_13 |  | 11 | 19 | 0.003365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3273-1_1_4_line_14 |  | 12 | 13 | 0.0034208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3273-1_1_4_line_15 |  | 13 | 14 | 0.029624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3273-1_1_4_line_16 |  | 14 | 18 | 0.0025321 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3273-1_1_4_line_17 |  | 15 | 16 | 0.0071886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3273-1_1_4_line_18 |  | 15 | 17 | 0.014505 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3273-1_1_4_line_19 |  | 16 | 38 | 0.019994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3273-1_1_4_line_20 |  | 17 | 37 | 0.0045333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3273-1_1_4_line_21 |  | 18 | 32 | 0.02664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3273-1_1_4_line_22 |  | 20 | 21 | 0.021955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3273-1_1_4_line_23 |  | 20 | 22 | 0.0048364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3273-1_1_4_line_24 |  | 21 | 23 | 0.019701 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3273-1_1_4_line_25 |  | 22 | 24 | 0.017477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
26 | LV_3273-1_1_4_line_26 |  | 22 | 25 | 0.022437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
27 | LV_3273-1_1_4_line_27 |  | 23 | 26 | 0.026521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3273-1_1_4_line_28 |  | 24 | 27 | 0.019965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
29 | LV_3273-1_1_4_line_29 |  | 25 | 28 | 0.027142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_3273-1_1_4_line_30 |  | 26 | 29 | 0.020375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3273-1_1_4_line_31 |  | 27 | 30 | 0.0095186 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
32 | LV_3273-1_1_4_line_32 |  | 28 | 31 | 0.018299 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3273-1_1_4_line_33 |  | 29 | 110 | 0.019436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3273-1_1_4_line_34 |  | 30 | 108 | 0.022473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
35 | LV_3273-1_1_4_line_35 |  | 31 | 35 | 0.020743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3273-1_1_4_line_36 |  | 31 | 32 | 0.004825 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3273-1_1_4_line_37 |  | 32 | 33 | 0.014267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3273-1_1_4_line_38 |  | 33 | 34 | 0.024402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3273-1_1_4_line_39 |  | 35 | 36 | 0.012827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3273-1_1_4_line_40 |  | 36 | 109 | 0.0077758 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3273-1_1_4_line_41 |  | 38 | 39 | 0.0041078 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3273-1_1_4_line_42 |  | 39 | 40 | 0.024287 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3273-1_1_4_line_43 |  | 40 | 41 | 0.014795 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3273-1_1_4_line_44 |  | 41 | 42 | 0.039594 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_3273-1_1_4_line_45 |  | 41 | 43 | 0.014341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3273-1_1_4_line_46 |  | 42 | 44 | 0.04254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_3273-1_1_4_line_47 |  | 43 | 45 | 0.010018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3273-1_1_4_line_48 |  | 44 | 46 | 0.0056896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_3273-1_1_4_line_49 |  | 45 | 47 | 0.045908 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3273-1_1_4_line_50 |  | 46 | 48 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_3273-1_1_4_line_51 |  | 47 | 50 | 0.007525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3273-1_1_4_line_52 |  | 47 | 51 | 0.022824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3273-1_1_4_line_53 |  | 48 | 49 | 0.0073221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_3273-1_1_4_line_54 |  | 49 | 69 | 0.025561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_3273-1_1_4_line_55 |  | 51 | 52 | 0.023232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3273-1_1_4_line_56 |  | 52 | 53 | 0.036818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3273-1_1_4_line_57 |  | 53 | 54 | 0.010399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3273-1_1_4_line_58 |  | 53 | 55 | 0.017291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3273-1_1_4_line_59 |  | 56 | 57 | 0.00082715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
60 | LV_3273-1_1_4_line_60 |  | 56 | 58 | 0.021805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_3273-1_1_4_line_61 |  | 57 | 59 | 0.024316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_3273-1_1_4_line_62 |  | 57 | 60 | 0.057133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3273-1_1_4_line_63 |  | 58 | 61 | 0.057379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
64 | LV_3273-1_1_4_line_64 |  | 59 | 62 | 0.0082498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
65 | LV_3273-1_1_4_line_65 |  | 61 | 63 | 0.035841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
66 | LV_3273-1_1_4_line_66 |  | 61 | 64 | 0.024065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
67 | LV_3273-1_1_4_line_67 |  | 62 | 65 | 0.014014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
68 | LV_3273-1_1_4_line_68 |  | 63 | 66 | 0.0088588 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
69 | LV_3273-1_1_4_line_69 |  | 64 | 67 | 0.0006712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
70 | LV_3273-1_1_4_line_70 |  | 65 | 68 | 0.021344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
71 | LV_3273-1_1_4_line_71 |  | 66 | 80 | 0.015885 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
72 | LV_3273-1_1_4_line_72 |  | 66 | 81 | 0.03337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3273-1_1_4_line_73 |  | 67 | 79 | 0.029975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
74 | LV_3273-1_1_4_line_74 |  | 68 | 69 | 0.0025793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
75 | LV_3273-1_1_4_line_75 |  | 70 | 71 | 0.025096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
76 | LV_3273-1_1_4_line_76 |  | 70 | 72 | 0.0013177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
77 | LV_3273-1_1_4_line_77 |  | 71 | 73 | 0.0020205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
78 | LV_3273-1_1_4_line_78 |  | 72 | 74 | 0.00014381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
79 | LV_3273-1_1_4_line_79 |  | 73 | 75 | 0.00057148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_3273-1_1_4_line_80 |  | 74 | 76 | 0.0017117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_3273-1_1_4_line_81 |  | 75 | 77 | 0.023995 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_3273-1_1_4_line_82 |  | 76 | 78 | 0.0012298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_3273-1_1_4_line_83 |  | 77 | 79 | 0.0012872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_3273-1_1_4_line_84 |  | 80 | 82 | 0.0045507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
85 | LV_3273-1_1_4_line_85 |  | 81 | 83 | 0.020651 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3273-1_1_4_line_86 |  | 82 | 84 | 0.021666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
87 | LV_3273-1_1_4_line_87 |  | 83 | 85 | 0.021844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3273-1_1_4_line_88 |  | 84 | 95 | 0.021598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
89 | LV_3273-1_1_4_line_89 |  | 86 | 87 | 0.010948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3273-1_1_4_line_90 |  | 86 | 88 | 0.010182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3273-1_1_4_line_91 |  | 87 | 89 | 0.010646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3273-1_1_4_line_92 |  | 88 | 90 | 0.011324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3273-1_1_4_line_93 |  | 89 | 91 | 0.015185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3273-1_1_4_line_94 |  | 90 | 92 | 0.020239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3273-1_1_4_line_95 |  | 91 | 93 | 0.0058334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3273-1_1_4_line_96 |  | 92 | 94 | 0.0018202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3273-1_1_4_line_97 |  | 94 | 102 | 0.019146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_3273-1_1_4_line_98 |  | 95 | 96 | 0.026513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
99 | LV_3273-1_1_4_line_99 |  | 96 | 97 | 0.029511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
100 | LV_3273-1_1_4_line_100 |  | 97 | 98 | 0.019131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
101 | LV_3273-1_1_4_line_101 |  | 97 | 99 | 0.019293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_3273-1_1_4_line_102 |  | 98 | 100 | 0.024634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
103 | LV_3273-1_1_4_line_103 |  | 99 | 101 | 0.02015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3273-1_1_4_line_104 |  | 100 | 103 | 0.0081554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
105 | LV_3273-1_1_4_line_105 |  | 102 | 109 | 0.0046616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3273-1_1_4_line_106 |  | 103 | 104 | 0.00092474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
107 | LV_3273-1_1_4_line_107 |  | 104 | 105 | 0.0061133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
108 | LV_3273-1_1_4_line_108 |  | 105 | 106 | 0.016048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
109 | LV_3273-1_1_4_line_109 |  | 106 | 107 | 0.026781 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
110 | LV_3273-1_1_4_line_110 |  | 107 | 108 | 0.0017306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
111 | LV_3273-1_1_4_line_111 |  | 111 | 112 | 0.0025488 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3273-1_1_4_line_112 |  | 111 | 113 | 0.0095337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3273-1_1_4_line_113 |  | 112 | 114 | 0.015145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3273-1_1_4_line_114 |  | 113 | 115 | 0.0074139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3273-1_1_4_line_115 |  | 115 | 116 | 0.0084167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3273-1_1_4_line_116 |  | 116 | 117 | 0.010886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3273-1_1_4_line_117 |  | 117 | 118 | 0.016799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3273-1_1_4_trafo_190 | 0.63 MVA 20/0.4 kV | 119 | 78 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2752638.0206 | 1226090.2346 | 2752634.7117 | 1226094.5432 | 2752630.5366 | 1226102.0763 | 2752626.178 | 1226109.9606 | 2752622.0584 | 1226117.3941
1 | 2752619.3402 | 1226122.2991 | 2752622.0584 | 1226117.3941
2 | 2752589.6834 | 1226172.5707 | 2752607.2439 | 1226150.2896 | 2752616.2849 | 1226127.8121 | 2752619.3402 | 1226122.2991
3 | 2752544.2011 | 1226259.1726 | 2752576.5669 | 1226274.7915
4 | 2752544.2011 | 1226259.1726 | 2752589.6834 | 1226172.5707
5 | 2752544.2011 | 1226259.1726 | 2752533.3922 | 1226273.9625
6 | 2752576.5669 | 1226274.7915 | 2752602.2422 | 1226287.1818
7 | 2752509.1771 | 1226307.0963 | 2752533.3922 | 1226273.9625
8 | 2752778.1084 | 1226256.0872 | 2752784.5168 | 1226236.9005
9 | 2752772.0031 | 1226274.3662 | 2752778.1084 | 1226256.0872
10 | 2752547.7905 | 1226560.0274 | 2752554.548 | 1226552.68
11 | 2752547.7905 | 1226560.0274 | 2752488.3416 | 1226552.0581
12 | 2752554.548 | 1226552.68 | 2752564.5041 | 1226541.8546
13 | 2752488.3416 | 1226552.0581 | 2752485.8659 | 1226549.7789
14 | 2752566.8197 | 1226539.3368 | 2752564.5041 | 1226541.8546
15 | 2752566.8197 | 1226539.3368 | 2752571.732 | 1226533.9957 | 2752587.0211 | 1226517.6689
16 | 2752587.0211 | 1226517.6689 | 2752588.7519 | 1226515.8207
17 | 2752712.8567 | 1226592.8027 | 2752719.0476 | 1226589.149
18 | 2752712.8567 | 1226592.8027 | 2752702.1316 | 1226583.0365
19 | 2752719.0476 | 1226589.149 | 2752733.3707 | 1226580.6959 | 2752736.523 | 1226579.5266
20 | 2752702.1316 | 1226583.0365 | 2752698.7797 | 1226579.9844
21 | 2752606.961 | 1226496.3758 | 2752588.7519 | 1226515.8207
22 | 2752525.6281 | 1226439.0949 | 2752543.7192 | 1226451.5335
23 | 2752547.7046 | 1226454.2736 | 2752543.7192 | 1226451.5335
24 | 2752525.6281 | 1226439.0949 | 2752511.0759 | 1226429.0896 | 2752509.6499 | 1226427.6287
25 | 2752547.7046 | 1226454.2736 | 2752556.6894 | 1226439.2833
26 | 2752547.7046 | 1226454.2736 | 2752566.0778 | 1226467.1522
27 | 2752509.6499 | 1226427.6287 | 2752491.1238 | 1226408.6506
28 | 2752566.9534 | 1226422.159 | 2752556.6894 | 1226439.2833
29 | 2752566.0778 | 1226467.1522 | 2752588.3031 | 1226482.7309
30 | 2752476.891 | 1226394.0705 | 2752491.1238 | 1226408.6506
31 | 2752566.9534 | 1226422.159 | 2752571.8469 | 1226413.9946
32 | 2752603.2877 | 1226493.2343 | 2752588.3031 | 1226482.7309
33 | 2752476.891 | 1226394.0705 | 2752466.6242 | 1226383.9427 | 2752463.7641 | 1226379.824
34 | 2752583.4002 | 1226394.7193 | 2752571.8469 | 1226413.9946
35 | 2752603.2877 | 1226493.2343 | 2752614.6473 | 1226475.8786
36 | 2752603.2877 | 1226493.2343 | 2752606.961 | 1226496.3758
37 | 2752606.961 | 1226496.3758 | 2752617.5101 | 1226505.9816
38 | 2752617.5101 | 1226505.9816 | 2752635.5527 | 1226522.4109
39 | 2752614.6473 | 1226475.8786 | 2752621.6717 | 1226465.1463
40 | 2752625.93 | 1226458.6402 | 2752621.6717 | 1226465.1463
41 | 2752740.3744 | 1226578.098 | 2752736.523 | 1226579.5266
42 | 2752740.3744 | 1226578.098 | 2752743.8297 | 1226576.8164 | 2752753.7363 | 1226574.3684 | 2752764.1314 | 1226574.5811
43 | 2752778.8018 | 1226576.3804 | 2752766.4854 | 1226574.6293 | 2752764.1314 | 1226574.5811
44 | 2752778.8018 | 1226576.3804 | 2752796.2746 | 1226540.8506
45 | 2752778.8018 | 1226576.3804 | 2752791.8593 | 1226582.3094
46 | 2752796.2746 | 1226540.8506 | 2752802.4795 | 1226528.2333 | 2752801.9107 | 1226522.0352 | 2752790.6159 | 1226516.5291 | 2752790.0675 | 1226508.6522 | 2752790.9399 | 1226507.0848
47 | 2752800.9513 | 1226586.5139 | 2752797.9097 | 1226585.0567 | 2752791.8593 | 1226582.3094
48 | 2752790.9399 | 1226507.0848 | 2752793.7069 | 1226502.1134
49 | 2752800.9513 | 1226586.5139 | 2752821.6544 | 1226545.5192
50 | 2752800.9646 | 1226489.0733 | 2752793.7069 | 1226502.1134
51 | 2752825.0502 | 1226538.8003 | 2752821.6544 | 1226545.5192
52 | 2752821.6544 | 1226545.5192 | 2752842.2332 | 1226555.3901
53 | 2752800.9646 | 1226489.0733 | 2752804.5255 | 1226482.6754
54 | 2752814.7587 | 1226459.7402 | 2752814.6361 | 1226464.5094 | 2752804.5255 | 1226482.6754
55 | 2752842.2332 | 1226555.3901 | 2752842.2332 | 1226555.3901 | 2752852.1995 | 1226534.4049
56 | 2752867.9945 | 1226501.1467 | 2752852.1995 | 1226534.4049
57 | 2752867.9945 | 1226501.1467 | 2752858.3835 | 1226497.1072
58 | 2752867.9945 | 1226501.1467 | 2752883.4719 | 1226508.8565
59 | 2752837.0761 | 1226392.826 | 2752836.7146 | 1226393.57
60 | 2752846.6057 | 1226373.2138 | 2752837.0761 | 1226392.826
61 | 2752836.7146 | 1226393.57 | 2752826.0876 | 1226415.4409
62 | 2752836.7146 | 1226393.57 | 2752884.9357 | 1226424.2116
63 | 2752846.6057 | 1226373.2138 | 2752791.0176 | 1226358.3616
64 | 2752822.8248 | 1226422.9974 | 2752823.5759 | 1226420.61 | 2752826.0876 | 1226415.4409
65 | 2752791.0176 | 1226358.3616 | 2752756.5007 | 1226348.7091
66 | 2752791.0176 | 1226358.3616 | 2752780.6039 | 1226380.0572
67 | 2752822.8248 | 1226422.9974 | 2752818.6192 | 1226436.3658
68 | 2752747.9692 | 1226346.3233 | 2752756.5007 | 1226348.7091
69 | 2752780.3134 | 1226380.6623 | 2752780.6039 | 1226380.0572
70 | 2752814.8249 | 1226457.1617 | 2752815.0694 | 1226447.6496 | 2752818.6192 | 1226436.3658
71 | 2752747.9692 | 1226346.3233 | 2752742.1986 | 1226345.9971 | 2752732.6153 | 1226342.7913
72 | 2752747.9692 | 1226346.3233 | 2752758.5408 | 1226314.6722
73 | 2752767.3425 | 1226407.6856 | 2752780.3134 | 1226380.6623
74 | 2752814.8249 | 1226457.1617 | 2752814.7587 | 1226459.7402
75 | 2752744.421 | 1226455.4393 | 2752755.2805 | 1226432.815
76 | 2752744.421 | 1226455.4393 | 2752743.8508 | 1226456.6273
77 | 2752755.2805 | 1226432.815 | 2752756.1549 | 1226430.9935
78 | 2752743.7886 | 1226456.757 | 2752743.8508 | 1226456.6273
79 | 2752756.1549 | 1226430.9935 | 2752756.4021 | 1226430.4783
80 | 2752743.0479 | 1226458.3001 | 2752743.7886 | 1226456.757
81 | 2752766.7855 | 1226408.846 | 2752756.4021 | 1226430.4783
82 | 2752742.5157 | 1226459.4088 | 2752743.0479 | 1226458.3001
83 | 2752767.3425 | 1226407.6856 | 2752766.7855 | 1226408.846
84 | 2752728.2996 | 1226341.3476 | 2752732.6153 | 1226342.7913
85 | 2752758.5408 | 1226314.6722 | 2752765.0831 | 1226295.0846
86 | 2752707.3534 | 1226337.8954 | 2752712.9578 | 1226337.0162 | 2752717.0989 | 1226337.6008 | 2752728.2996 | 1226341.3476
87 | 2752765.0831 | 1226295.0846 | 2752772.0031 | 1226274.3662
88 | 2752707.3534 | 1226337.8954 | 2752687.6718 | 1226329.001
89 | 2752663.1571 | 1226402.4894 | 2752669.3396 | 1226393.4535
90 | 2752663.1571 | 1226402.4894 | 2752657.4072 | 1226410.893
91 | 2752675.3515 | 1226384.6671 | 2752669.3396 | 1226393.4535
92 | 2752657.4072 | 1226410.893 | 2752652.2034 | 1226418.4985 | 2752651.0486 | 1226420.2628
93 | 2752675.3515 | 1226384.6671 | 2752683.9263 | 1226372.1347
94 | 2752639.9647 | 1226437.1974 | 2752651.0486 | 1226420.2628
95 | 2752687.2204 | 1226367.3203 | 2752683.9263 | 1226372.1347
96 | 2752639.9647 | 1226437.1974 | 2752638.9678 | 1226438.7204
97 | 2752628.4829 | 1226454.7398 | 2752638.9678 | 1226438.7204
98 | 2752687.6718 | 1226329.001 | 2752663.5115 | 1226318.0825
99 | 2752636.6189 | 1226305.9293 | 2752663.5115 | 1226318.0825
100 | 2752636.6189 | 1226305.9293 | 2752626.7837 | 1226322.3384
101 | 2752636.6189 | 1226305.9293 | 2752632.531 | 1226301.7985 | 2752620.3899 | 1226295.9395
102 | 2752626.7837 | 1226322.3384 | 2752614.1195 | 1226343.4673
103 | 2752602.2422 | 1226287.1818 | 2752620.3899 | 1226295.9395
104 | 2752609.9268 | 1226350.4624 | 2752614.1195 | 1226343.4673
105 | 2752625.93 | 1226458.6402 | 2752628.4829 | 1226454.7398
106 | 2752609.4514 | 1226351.2556 | 2752609.9268 | 1226350.4624
107 | 2752609.4514 | 1226351.2556 | 2752606.3085 | 1226356.4991
108 | 2752598.0581 | 1226370.264 | 2752606.3085 | 1226356.4991
109 | 2752584.2898 | 1226393.2349 | 2752598.0581 | 1226370.264
110 | 2752583.4002 | 1226394.7193 | 2752584.2898 | 1226393.2349
111 | 2752521.5733 | 1226347.1506 | 2752520.0557 | 1226349.1984
112 | 2752521.5733 | 1226347.1506 | 2752521.5733 | 1226347.1506 | 2752526.5306 | 1226339.0071
113 | 2752520.0557 | 1226349.1984 | 2752511.0387 | 1226361.366
114 | 2752526.5306 | 1226339.0071 | 2752530.3857 | 1226332.6743
115 | 2752530.7076 | 1226324.2638 | 2752530.7076 | 1226324.2638 | 2752530.3857 | 1226332.6743 | 2752530.3857 | 1226332.6743
116 | 2752523.015 | 1226316.6216 | 2752524.7676 | 1226317.8279 | 2752530.7076 | 1226324.2638
117 | 2752509.1771 | 1226307.0963 | 2752523.015 | 1226316.6216

## bus_geodata
| x | y | coords
0 | 2752638.0206 | 1226090.2346
1 | 2752622.0584 | 1226117.3941
2 | 2752619.3402 | 1226122.2991
3 | 2752544.2011 | 1226259.1726
4 | 2752576.5669 | 1226274.7915
5 | 2752589.6834 | 1226172.5707
6 | 2752533.3922 | 1226273.9625
7 | 2752784.5168 | 1226236.9005
8 | 2752778.1084 | 1226256.0872
9 | 2752547.7905 | 1226560.0274
10 | 2752554.548 | 1226552.68
11 | 2752488.3416 | 1226552.0581
12 | 2752564.5041 | 1226541.8546
13 | 2752566.8197 | 1226539.3368
14 | 2752587.0211 | 1226517.6689
15 | 2752712.8567 | 1226592.8027
16 | 2752719.0476 | 1226589.149
17 | 2752702.1316 | 1226583.0365
18 | 2752588.7519 | 1226515.8207
19 | 2752485.8659 | 1226549.7789
20 | 2752543.7192 | 1226451.5335
21 | 2752525.6281 | 1226439.0949
22 | 2752547.7046 | 1226454.2736
23 | 2752509.6499 | 1226427.6287
24 | 2752556.6894 | 1226439.2833
25 | 2752566.0778 | 1226467.1522
26 | 2752491.1238 | 1226408.6506
27 | 2752566.9534 | 1226422.159
28 | 2752588.3031 | 1226482.7309
29 | 2752476.891 | 1226394.0705
30 | 2752571.8469 | 1226413.9946
31 | 2752603.2877 | 1226493.2343
32 | 2752606.961 | 1226496.3758
33 | 2752617.5101 | 1226505.9816
34 | 2752635.5527 | 1226522.4109
35 | 2752614.6473 | 1226475.8786
36 | 2752621.6717 | 1226465.1463
37 | 2752698.7797 | 1226579.9844
38 | 2752736.523 | 1226579.5266
39 | 2752740.3744 | 1226578.098
40 | 2752764.1314 | 1226574.5811
41 | 2752778.8018 | 1226576.3804
42 | 2752796.2746 | 1226540.8506
43 | 2752791.8593 | 1226582.3094
44 | 2752790.9399 | 1226507.0848
45 | 2752800.9513 | 1226586.5139
46 | 2752793.7069 | 1226502.1134
47 | 2752821.6544 | 1226545.5192
48 | 2752800.9646 | 1226489.0733
49 | 2752804.5255 | 1226482.6754
50 | 2752825.0502 | 1226538.8003
51 | 2752842.2332 | 1226555.3901
52 | 2752852.1995 | 1226534.4049
53 | 2752867.9945 | 1226501.1467
54 | 2752858.3835 | 1226497.1072
55 | 2752883.4719 | 1226508.8565
56 | 2752837.0761 | 1226392.826
57 | 2752836.7146 | 1226393.57
58 | 2752846.6057 | 1226373.2138
59 | 2752826.0876 | 1226415.4409
60 | 2752884.9357 | 1226424.2116
61 | 2752791.0176 | 1226358.3616
62 | 2752822.8248 | 1226422.9974
63 | 2752756.5007 | 1226348.7091
64 | 2752780.6039 | 1226380.0572
65 | 2752818.6192 | 1226436.3658
66 | 2752747.9692 | 1226346.3233
67 | 2752780.3134 | 1226380.6623
68 | 2752814.8249 | 1226457.1617
69 | 2752814.7587 | 1226459.7402
70 | 2752744.421 | 1226455.4393
71 | 2752755.2806 | 1226432.815
72 | 2752743.8508 | 1226456.6273
73 | 2752756.1549 | 1226430.9935
74 | 2752743.7886 | 1226456.757
75 | 2752756.4021 | 1226430.4783
76 | 2752743.0479 | 1226458.3001
77 | 2752766.7855 | 1226408.846
78 | 2752742.5157 | 1226459.4088
79 | 2752767.3425 | 1226407.6856
80 | 2752732.6153 | 1226342.7913
81 | 2752758.5408 | 1226314.6722
82 | 2752728.2996 | 1226341.3476
83 | 2752765.0831 | 1226295.0846
84 | 2752707.3534 | 1226337.8954
85 | 2752772.0031 | 1226274.3662
86 | 2752663.1571 | 1226402.4894
87 | 2752669.3396 | 1226393.4535
88 | 2752657.4072 | 1226410.893
89 | 2752675.3515 | 1226384.6671
90 | 2752651.0486 | 1226420.2628
91 | 2752683.9263 | 1226372.1347
92 | 2752639.9647 | 1226437.1974
93 | 2752687.2204 | 1226367.3203
94 | 2752638.9678 | 1226438.7204
95 | 2752687.6718 | 1226329.001
96 | 2752663.5115 | 1226318.0825
97 | 2752636.6189 | 1226305.9293
98 | 2752626.7837 | 1226322.3384
99 | 2752620.3899 | 1226295.9395
100 | 2752614.1195 | 1226343.4673
101 | 2752602.2422 | 1226287.1818
102 | 2752628.4829 | 1226454.7398
103 | 2752609.9268 | 1226350.4624
104 | 2752609.4514 | 1226351.2556
105 | 2752606.3085 | 1226356.4991
106 | 2752598.0581 | 1226370.264
107 | 2752584.2898 | 1226393.2349
108 | 2752583.4002 | 1226394.7193
109 | 2752625.93 | 1226458.6402
110 | 2752463.7641 | 1226379.824
111 | 2752521.5733 | 1226347.1506
112 | 2752520.0557 | 1226349.1984
113 | 2752526.5306 | 1226339.0071
114 | 2752511.0387 | 1226361.366
115 | 2752530.3857 | 1226332.6743
116 | 2752530.7076 | 1226324.2638
117 | 2752523.015 | 1226316.6216
118 | 2752509.1771 | 1226307.0963
119 | 2752791.0176 | 1226358.3616

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98298 | -0.32523 | 0.00097005 | 0.00024312
1 | 0.983 | -0.32468 | 0.00042271 | 0.00010594
2 | 0.98301 | -0.32453 | 0.00082412 | 0.00020654
3 | 0.98333 | -0.31826 | 0 | 0
4 | 0.98381 | -0.30892 | 0.0017774 | 0.00044546
5 | 0.98313 | -0.32218 | 0 | 0
6 | 0.98313 | -0.32229 | 0.002063 | 0.00051703
7 | 0.98904 | -0.20803 | 0.00044242 | 0.00011088
8 | 0.98904 | -0.20787 | 0.0004424 | 0.00011088
9 | 0.97214 | -0.53708 | 0.018526 | 0.004643
10 | 0.97237 | -0.53251 | 0.0044106 | 0.0011054
11 | 0.97179 | -0.54402 | 0.0036388 | 0.00091196
12 | 0.97277 | -0.5246 | 0.0032523 | 0.0008151
13 | 0.97287 | -0.52255 | 0.018682 | 0.0046822
14 | 0.97429 | -0.49469 | 0.012952 | 0.003246
15 | 0.97508 | -0.47918 | 0 | 0
16 | 0.9752 | -0.47678 | 0.0022868 | 0.00057314
17 | 0.97483 | -0.48401 | 0.0095258 | 0.0023874
18 | 0.97444 | -0.49171 | 0.00088855 | 0.00022269
19 | 0.97178 | -0.54419 | 0.0026361 | 0.00066066
20 | 0.97984 | -0.38588 | 0.0023946 | 0.00060014
21 | 0.97969 | -0.38887 | 0.00093162 | 0.00023349
22 | 0.97988 | -0.38501 | 0.0036812 | 0.00092259
23 | 0.97957 | -0.39122 | 0.0012535 | 0.00031415
24 | 0.98035 | -0.37582 | 0.0010153 | 0.00025447
25 | 0.97935 | -0.39543 | 0.0012049 | 0.00030197
26 | 0.97944 | -0.39378 | 0.0028286 | 0.00070892
27 | 0.9809 | -0.36525 | 0.0013458 | 0.00033728
28 | 0.97807 | -0.42039 | 0.0010653 | 0.00026699
29 | 0.97939 | -0.39469 | 0 | 0
30 | 0.98116 | -0.36015 | 0.001415 | 0.00035464
31 | 0.97637 | -0.45379 | 0 | 0
32 | 0.97605 | -0.45998 | 0 | 0
33 | 0.97598 | -0.46133 | 0.0017093 | 0.00042839
34 | 0.9759 | -0.46287 | 0.0034475 | 0.00086402
35 | 0.97579 | -0.46512 | 0.0019407 | 0.00048638
36 | 0.97546 | -0.47168 | 0.0018871 | 0.00047294
37 | 0.9748 | -0.48473 | 0.0086627 | 0.0021711
38 | 0.97558 | -0.46928 | 0.0049723 | 0.0012462
39 | 0.97568 | -0.46737 | 0.018708 | 0.0046886
40 | 0.97667 | -0.44775 | 0.022934 | 0.0057479
41 | 0.9776 | -0.42963 | 0 | 0
42 | 0.9801 | -0.38061 | 0.012524 | 0.0031389
43 | 0.97667 | -0.4477 | 0.010574 | 0.0026501
44 | 0.98305 | -0.32342 | 0.001901 | 0.00047645
45 | 0.97613 | -0.4584 | 0 | 0
46 | 0.98324 | -0.31955 | 0.0035559 | 0.0008912
47 | 0.97363 | -0.50761 | 0 | 0
48 | 0.98378 | -0.30919 | 0.0023624 | 0.00059208
49 | 0.98405 | -0.30404 | 0.0019232 | 0.000482
50 | 0.97351 | -0.50988 | 0.016391 | 0.0041079
51 | 0.97273 | -0.52528 | 0.015341 | 0.0038449
52 | 0.97215 | -0.53672 | 0.016437 | 0.0041195
53 | 0.9718 | -0.5437 | 0 | 0
54 | 0.97175 | -0.54464 | 0.0048753 | 0.0012219
55 | 0.97171 | -0.54542 | 0.005401 | 0.0013536
56 | 0.98774 | -0.23275 | 0.002785 | 0.00069799
57 | 0.98771 | -0.23338 | 0.001747 | 0.00043783
58 | 0.98862 | -0.21582 | 0 | 0
59 | 0.98676 | -0.2517 | 0.0014614 | 0.00036627
60 | 0.98766 | -0.23442 | 0.0010131 | 0.00025392
61 | 0.99095 | -0.1714 | 0 | 0
62 | 0.98644 | -0.25786 | 0.0014327 | 0.00035906
63 | 0.98956 | -0.19793 | 0.0029911 | 0.00074963
64 | 0.99285 | -0.13511 | 0.0020433 | 0.00051211
65 | 0.9859 | -0.26826 | 0.0016074 | 0.00040285
66 | 0.98922 | -0.20438 | 0 | 0
67 | 0.9929 | -0.13409 | 0.00095421 | 0.00023915
68 | 0.98508 | -0.28396 | 0.0021106 | 0.00052896
69 | 0.98499 | -0.28584 | 0.0034538 | 0.0008656
70 | 0.99963 | -0.0068936 | 0.0014473 | 0.00036273
71 | 0.99756 | -0.045851 | 0.00227 | 0.00056892
72 | 0.99974 | -0.0048441 | 0.001493 | 0.00037419
73 | 0.9974 | -0.048975 | 0.0015097 | 0.00037837
74 | 0.99975 | -0.0046195 | 0.0014584 | 0.00036552
75 | 0.99735 | -0.049855 | 0.001467 | 0.00036767
76 | 0.9999 | -0.001936 | 0.0015951 | 0.00039976
77 | 0.9954 | -0.086718 | 0.0032546 | 0.00081568
78 | 1 | 0 | -0.37021 | -0.095209
79 | 0.9953 | -0.088681 | 0.0031878 | 0.00079894
80 | 0.98863 | -0.21572 | 0.0014866 | 0.00037258
81 | 0.98912 | -0.20635 | 0.001471 | 0.00036867
82 | 0.98846 | -0.21894 | 0.0023021 | 0.00057696
83 | 0.98909 | -0.20702 | 0.00044832 | 0.00011236
84 | 0.98768 | -0.23406 | 0 | 0
85 | 0.98906 | -0.20757 | 0.00050629 | 0.00012689
86 | 0.97423 | -0.49595 | 0.0029346 | 0.00073547
87 | 0.97415 | -0.49736 | 0.0016775 | 0.00042043
88 | 0.97432 | -0.49409 | 0.0034893 | 0.0008745
89 | 0.9741 | -0.4984 | 0.001987 | 0.00049799
90 | 0.97446 | -0.4913 | 0.0029267 | 0.00073349
91 | 0.97405 | -0.49934 | 0.0017784 | 0.00044571
92 | 0.97477 | -0.48522 | 0.0024653 | 0.00061787
93 | 0.97405 | -0.49951 | 0.0015701 | 0.0003935
94 | 0.9748 | -0.48459 | 0.001908 | 0.00047818
95 | 0.98689 | -0.24917 | 0.0017066 | 0.00042771
96 | 0.98594 | -0.26754 | 0.0020078 | 0.00050319
97 | 0.98489 | -0.28776 | 0 | 0
98 | 0.9843 | -0.29927 | 0.0017902 | 0.00044866
99 | 0.98456 | -0.29429 | 0.0014472 | 0.0003627
100 | 0.98354 | -0.31391 | 0.0010584 | 0.00026527
101 | 0.98424 | -0.3006 | 0.0011841 | 0.00029677
102 | 0.97517 | -0.47731 | 0.0017572 | 0.00044038
103 | 0.98329 | -0.31873 | 0.0015919 | 0.00039897
104 | 0.98327 | -0.31927 | 0.0021774 | 0.0005457
105 | 0.98308 | -0.32277 | 0.001106 | 0.0002772
106 | 0.98261 | -0.3319 | 0.0010935 | 0.00027404
107 | 0.98183 | -0.34703 | 0.0016012 | 0.0004013
108 | 0.98179 | -0.34799 | 0.0037865 | 0.00094899
109 | 0.97527 | -0.47539 | 0.0035346 | 0.00088585
110 | 0.97935 | -0.39557 | 0.0024819 | 0.00062204
111 | 0.98237 | -0.33704 | 0.0015517 | 0.00038889
112 | 0.98237 | -0.33715 | 0.00051612 | 0.00012935
113 | 0.9824 | -0.33638 | 0.0017458 | 0.00043753
114 | 0.98234 | -0.33762 | 0.0017524 | 0.00043918
115 | 0.98244 | -0.33564 | 0.0015272 | 0.00038276
116 | 0.9825 | -0.33456 | 0.0014728 | 0.00036912
117 | 0.98258 | -0.33288 | 0.0015741 | 0.00039451
118 | 0.98274 | -0.3298 | 0 | 0
119 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.00097005 | -0.00024312 | 0.00097008 | 0.00024273 | 2.5512e-08 | -3.8366e-07 | 0.0014685 | 0.0014683 | 0.0014685 | 0.98298 | -0.32523 | 0.983 | -0.32468 | 0.40342
1 | -0.0013928 | -0.00034867 | 0.0013928 | 0.00034861 | 9.3463e-09 | -6.511e-08 | 0.0021082 | 0.0021082 | 0.0021082 | 0.983 | -0.32468 | 0.98301 | -0.32453 | 0.57917
2 | -0.0022169 | -0.00055515 | 0.0022172 | 0.00055457 | 2.4869e-07 | -5.8762e-07 | 0.0033556 | 0.0033554 | 0.0033556 | 0.98301 | -0.32453 | 0.98313 | -0.32218 | 0.92188
3 | -0.01443 | -0.003616 | 0.014436 | 0.0036197 | 6.4252e-06 | 3.656e-06 | 0.021835 | 0.021835 | 0.021835 | 0.98333 | -0.31826 | 0.98381 | -0.30892 | 5.9987
4 | 0.0022176 | 0.00055359 | -0.0022172 | -0.00055457 | 4.1293e-07 | -9.7636e-07 | 0.0033549 | 0.0033554 | 0.0033554 | 0.98333 | -0.31826 | 0.98313 | -0.32218 | 0.92181
5 | 0.012212 | 0.0030624 | -0.01221 | -0.0030611 | 2.3461e-06 | 1.2692e-06 | 0.01848 | 0.01848 | 0.01848 | 0.98333 | -0.31826 | 0.98313 | -0.32229 | 5.077
6 | -0.016213 | -0.0040651 | 0.01622 | 0.0040689 | 6.4294e-06 | 3.7526e-06 | 0.024523 | 0.024523 | 0.024523 | 0.98381 | -0.30892 | 0.98424 | -0.3006 | 6.7372
7 | 0.010147 | 0.0025441 | -0.010143 | -0.0025423 | 3.63e-06 | 1.803e-06 | 0.015358 | 0.015358 | 0.015358 | 0.98313 | -0.32229 | 0.98274 | -0.3298 | 4.2193
8 | -0.00044242 | -0.00011088 | 0.00044242 | 0.00011062 | 3.3605e-09 | -2.5745e-07 | 0.00066563 | 0.00066553 | 0.00066563 | 0.98904 | -0.20803 | 0.98904 | -0.20787 | 0.18286
9 | -0.00088482 | -0.0002215 | 0.00088483 | 0.00022126 | 1.2804e-08 | -2.3913e-07 | 0.0013311 | 0.001331 | 0.0013311 | 0.98904 | -0.20787 | 0.98906 | -0.20757 | 0.36569
10 | -0.024803 | -0.0062162 | 0.024808 | 0.0062195 | 5.3954e-06 | 3.3293e-06 | 0.037965 | 0.037965 | 0.037965 | 0.97214 | -0.53708 | 0.97237 | -0.53251 | 10.4298
11 | 0.0062769 | 0.0015732 | -0.0062748 | -0.0015726 | 2.0764e-06 | 5.8549e-07 | 0.0096079 | 0.0096081 | 0.0096081 | 0.97214 | -0.53708 | 0.97179 | -0.54402 | 2.6396
12 | -0.029219 | -0.0073249 | 0.02923 | 0.0073318 | 1.1027e-05 | 6.8748e-06 | 0.044714 | 0.044714 | 0.044714 | 0.97237 | -0.53251 | 0.97277 | -0.5246 | 12.2841
13 | 0.0026361 | 0.00066063 | -0.0026361 | -0.00066066 | 2.056e-08 | -2.8533e-08 | 0.0040364 | 0.0040364 | 0.0040364 | 0.97179 | -0.54402 | 0.97178 | -0.54419 | 1.1089
14 | -0.032482 | -0.0081469 | 0.032485 | 0.0081489 | 3.1672e-06 | 1.9845e-06 | 0.049689 | 0.049689 | 0.049689 | 0.97277 | -0.5246 | 0.97287 | -0.52255 | 13.6508
15 | -0.051167 | -0.012831 | 0.051236 | 0.012874 | 6.8046e-05 | 4.3181e-05 | 0.078264 | 0.078264 | 0.078264 | 0.97287 | -0.52255 | 0.97429 | -0.49469 | 21.501
16 | -0.064187 | -0.01612 | 0.064196 | 0.016126 | 9.1278e-06 | 5.8103e-06 | 0.098045 | 0.098045 | 0.098045 | 0.97429 | -0.49469 | 0.97444 | -0.49171 | 26.9353
17 | -0.018193 | -0.0045611 | 0.018195 | 0.0045623 | 2.078e-06 | 1.2402e-06 | 0.027764 | 0.027764 | 0.027764 | 0.97508 | -0.47918 | 0.9752 | -0.47678 | 7.6274
18 | 0.018193 | 0.0045611 | -0.018189 | -0.0045586 | 4.193e-06 | 2.5026e-06 | 0.027764 | 0.027764 | 0.027764 | 0.97508 | -0.47918 | 0.97483 | -0.48401 | 7.6275
19 | -0.020482 | -0.0051355 | 0.020489 | 0.0051399 | 7.3234e-06 | 4.4374e-06 | 0.031253 | 0.031253 | 0.031253 | 0.9752 | -0.47678 | 0.97558 | -0.46928 | 8.5861
20 | 0.008663 | 0.0021712 | -0.0086627 | -0.0021711 | 2.9726e-07 | 1.3373e-07 | 0.013223 | 0.013223 | 0.013223 | 0.97483 | -0.48401 | 0.9748 | -0.48473 | 3.6328
21 | -0.065085 | -0.016349 | 0.065184 | 0.016412 | 9.8707e-05 | 6.284e-05 | 0.099401 | 0.099401 | 0.099401 | 0.97444 | -0.49171 | 0.97605 | -0.45998 | 27.3081
22 | 0.0074984 | 0.0018789 | -0.0074973 | -0.0018785 | 1.0676e-06 | 4.0675e-07 | 0.011387 | 0.011387 | 0.011387 | 0.97984 | -0.38588 | 0.97969 | -0.38887 | 3.1284
23 | -0.0098929 | -0.0024791 | 0.0098934 | 0.0024793 | 4.0936e-07 | 2.0107e-07 | 0.015024 | 0.015024 | 0.015024 | 0.97984 | -0.38588 | 0.97988 | -0.38501 | 4.1274
24 | 0.0065657 | 0.001645 | -0.0065649 | -0.0016448 | 7.3471e-07 | 2.2217e-07 | 0.0099722 | 0.0099723 | 0.0099723 | 0.97969 | -0.38887 | 0.97957 | -0.39122 | 2.7396
25 | -0.11644 | -0.02941 | 0.11649 | 0.029442 | 5.1278e-05 | 3.1937e-05 | 0.17691 | 0.17691 | 0.17691 | 0.97988 | -0.38501 | 0.98035 | -0.37582 | 12.1503
26 | 0.10287 | 0.026009 | -0.10282 | -0.025977 | 5.1385e-05 | 3.1756e-05 | 0.1563 | 0.1563 | 0.1563 | 0.97988 | -0.38501 | 0.97935 | -0.39543 | 10.7346
27 | 0.0053114 | 0.0013307 | -0.0053108 | -0.0013306 | 6.4742e-07 | 8.0525e-08 | 0.0080682 | 0.0080683 | 0.0080683 | 0.97957 | -0.39122 | 0.97944 | -0.39378 | 2.2166
28 | -0.11751 | -0.029697 | 0.11757 | 0.029734 | 5.9603e-05 | 3.7138e-05 | 0.17845 | 0.17845 | 0.17845 | 0.98035 | -0.37582 | 0.9809 | -0.36525 | 12.2562
29 | 0.10161 | 0.025675 | -0.10149 | -0.025598 | 0.00012142 | 7.7028e-05 | 0.15446 | 0.15447 | 0.15447 | 0.97935 | -0.39543 | 0.97807 | -0.42039 | 21.2177
30 | 0.0024822 | 0.00062167 | -0.0024821 | -0.00062186 | 1.0865e-07 | -1.8688e-07 | 0.0037709 | 0.003771 | 0.003771 | 0.97944 | -0.39378 | 0.97939 | -0.39469 | 1.036
31 | -0.11892 | -0.030071 | 0.11894 | 0.030089 | 2.9071e-05 | 1.8124e-05 | 0.18049 | 0.18049 | 0.18049 | 0.9809 | -0.36525 | 0.98116 | -0.36015 | 12.3963
32 | 0.10043 | 0.025331 | -0.10027 | -0.025229 | 0.00016031 | 0.00010237 | 0.15284 | 0.15284 | 0.15284 | 0.97807 | -0.42039 | 0.97637 | -0.45379 | 41.9902
33 | 0.0024821 | 0.00062186 | -0.0024819 | -0.00062204 | 1.0365e-07 | -1.7824e-07 | 0.003771 | 0.0037711 | 0.0037711 | 0.97939 | -0.39469 | 0.97935 | -0.39557 | 1.036
34 | -0.12036 | -0.030444 | 0.12043 | 0.030488 | 7.0275e-05 | 4.384e-05 | 0.18264 | 0.18264 | 0.18264 | 0.98116 | -0.36015 | 0.98179 | -0.34799 | 12.5437
35 | 0.029904 | 0.0075113 | -0.029888 | -0.0075012 | 1.6161e-05 | 1.0084e-05 | 0.045581 | 0.045581 | 0.045581 | 0.97637 | -0.45379 | 0.97579 | -0.46512 | 12.5222
36 | 0.070362 | 0.017717 | -0.070341 | -0.017704 | 2.0818e-05 | 1.3263e-05 | 0.10726 | 0.10726 | 0.10726 | 0.97637 | -0.45379 | 0.97605 | -0.45998 | 29.4681
37 | 0.0051574 | 0.0012923 | -0.005157 | -0.0012923 | 3.3074e-07 | 3.3369e-08 | 0.0078624 | 0.0078625 | 0.0078625 | 0.97605 | -0.45998 | 0.97598 | -0.46133 | 2.16
38 | 0.0034477 | 0.00086388 | -0.0034475 | -0.00086402 | 2.5284e-07 | -1.431e-07 | 0.0052565 | 0.0052566 | 0.0052566 | 0.97598 | -0.46133 | 0.9759 | -0.46287 | 1.4441
39 | 0.027947 | 0.0070148 | -0.027938 | -0.0070094 | 8.7378e-06 | 5.432e-06 | 0.042621 | 0.042621 | 0.042621 | 0.97579 | -0.46512 | 0.97546 | -0.47168 | 11.7092
40 | 0.026051 | 0.0065365 | -0.026047 | -0.0065336 | 4.6057e-06 | 2.8506e-06 | 0.039743 | 0.039743 | 0.039743 | 0.97546 | -0.47168 | 0.97527 | -0.47539 | 10.9184
41 | -0.025462 | -0.0063861 | 0.025464 | 0.0063875 | 2.3235e-06 | 1.4357e-06 | 0.038837 | 0.038837 | 0.038837 | 0.97558 | -0.46928 | 0.97568 | -0.46737 | 10.6696
42 | -0.044172 | -0.011076 | 0.044213 | 0.011102 | 4.1336e-05 | 2.6151e-05 | 0.067369 | 0.067369 | 0.067369 | 0.97568 | -0.46737 | 0.97667 | -0.44775 | 18.5079
43 | -0.067147 | -0.01685 | 0.067206 | 0.016887 | 5.8074e-05 | 3.6982e-05 | 0.10231 | 0.10231 | 0.10231 | 0.97667 | -0.44775 | 0.9776 | -0.42963 | 28.1073
44 | -0.13651 | -0.034364 | 0.13683 | 0.034568 | 0.00032068 | 0.00020424 | 0.20784 | 0.20784 | 0.20784 | 0.9776 | -0.42963 | 0.9801 | -0.38061 | 28.5489
45 | 0.069303 | 0.017477 | -0.069243 | -0.017439 | 5.9885e-05 | 3.8146e-05 | 0.10553 | 0.10553 | 0.10553 | 0.9776 | -0.42963 | 0.97667 | -0.4477 | 28.9906
46 | -0.14935 | -0.037707 | 0.14976 | 0.037969 | 0.00041046 | 0.00026162 | 0.22685 | 0.22685 | 0.22685 | 0.9801 | -0.38061 | 0.98305 | -0.32342 | 31.1608
47 | 0.058669 | 0.014789 | -0.058639 | -0.01477 | 3.0034e-05 | 1.9097e-05 | 0.089416 | 0.089416 | 0.089416 | 0.97667 | -0.4477 | 0.97613 | -0.4584 | 24.5647
48 | -0.15166 | -0.038445 | 0.15169 | 0.038463 | 2.815e-05 | 1.7727e-05 | 0.22973 | 0.22973 | 0.22973 | 0.98305 | -0.32342 | 0.98324 | -0.31955 | 15.778
49 | 0.058639 | 0.01477 | -0.058501 | -0.014682 | 0.00013764 | 8.7518e-05 | 0.089416 | 0.089416 | 0.089416 | 0.97613 | -0.4584 | 0.97363 | -0.50761 | 24.5648
50 | -0.15525 | -0.039354 | 0.15533 | 0.039403 | 7.7337e-05 | 4.8738e-05 | 0.23511 | 0.23511 | 0.23511 | 0.98324 | -0.31955 | 0.98378 | -0.30919 | 16.1476
51 | 0.016392 | 0.0041089 | -0.016391 | -0.0041079 | 1.7712e-06 | 1.04e-06 | 0.025053 | 0.025053 | 0.025053 | 0.97363 | -0.50761 | 0.97351 | -0.50988 | 6.8827
52 | 0.042109 | 0.010573 | -0.042073 | -0.010551 | 3.5456e-05 | 2.2408e-05 | 0.064363 | 0.064363 | 0.064363 | 0.97363 | -0.50761 | 0.97273 | -0.52528 | 17.6821
53 | -0.15769 | -0.039995 | 0.15773 | 0.04002 | 3.9106e-05 | 2.4656e-05 | 0.23868 | 0.23868 | 0.23868 | 0.98378 | -0.30919 | 0.98405 | -0.30404 | 16.393
54 | -0.15965 | -0.040502 | 0.15979 | 0.04059 | 0.00013986 | 8.8212e-05 | 0.24159 | 0.24159 | 0.24159 | 0.98405 | -0.30404 | 0.98499 | -0.28584 | 16.5927
55 | 0.026732 | 0.0067058 | -0.026717 | -0.0066968 | 1.457e-05 | 9.0364e-06 | 0.040895 | 0.040895 | 0.040895 | 0.97273 | -0.52528 | 0.97215 | -0.53672 | 11.2349
56 | 0.01028 | 0.0025773 | -0.010277 | -0.0025756 | 3.4189e-06 | 1.7317e-06 | 0.015736 | 0.015736 | 0.015736 | 0.97215 | -0.53672 | 0.9718 | -0.5437 | 4.3231
57 | 0.0048755 | 0.0012219 | -0.0048753 | -0.0012219 | 2.1733e-07 | 1.0259e-08 | 0.0074654 | 0.0074654 | 0.0074654 | 0.9718 | -0.5437 | 0.97175 | -0.54464 | 2.0509
58 | 0.0054014 | 0.0013537 | -0.005401 | -0.0013536 | 4.4355e-07 | 6.9657e-08 | 0.0082707 | 0.0082707 | 0.0082707 | 0.9718 | -0.5437 | 0.97171 | -0.54542 | 2.2722
59 | 0.17305 | 0.044075 | -0.17304 | -0.044071 | 5.2802e-06 | 3.337e-06 | 0.26094 | 0.26094 | 0.26094 | 0.98774 | -0.23275 | 0.98771 | -0.23338 | 17.9219
60 | -0.17583 | -0.044773 | 0.17597 | 0.044864 | 0.0001437 | 9.0853e-05 | 0.26514 | 0.26514 | 0.26514 | 0.98774 | -0.23275 | 0.98862 | -0.21582 | 18.2101
61 | 0.17028 | 0.04338 | -0.17013 | -0.043285 | 0.00015032 | 9.4958e-05 | 0.25678 | 0.25679 | 0.25679 | 0.98771 | -0.23338 | 0.98676 | -0.2517 | 17.6364
62 | 0.0010132 | 0.00025322 | -0.0010131 | -0.00025392 | 4.991e-08 | -6.9925e-07 | 0.0015262 | 0.0015264 | 0.0015264 | 0.98771 | -0.23338 | 0.98766 | -0.23442 | 0.41935
63 | -0.17597 | -0.044864 | 0.17635 | 0.045103 | 0.00037815 | 0.00023907 | 0.26514 | 0.26514 | 0.26514 | 0.98862 | -0.21582 | 0.99095 | -0.1714 | 18.21
64 | 0.16867 | 0.042919 | -0.16862 | -0.042887 | 5.0127e-05 | 3.166e-05 | 0.25458 | 0.25458 | 0.25458 | 0.98676 | -0.2517 | 0.98644 | -0.25786 | 17.485
65 | 0.16858 | 0.043044 | -0.16836 | -0.042908 | 0.0002158 | 0.00013627 | 0.25342 | 0.25342 | 0.25342 | 0.99095 | -0.1714 | 0.98956 | -0.19793 | 17.4055
66 | -0.34493 | -0.088147 | 0.34554 | 0.088534 | 0.00060668 | 0.00038704 | 0.51856 | 0.51856 | 0.51856 | 0.99095 | -0.1714 | 0.99285 | -0.13511 | 35.6154
67 | 0.16719 | 0.042528 | -0.1671 | -0.042476 | 8.3713e-05 | 5.2861e-05 | 0.25242 | 0.25242 | 0.25242 | 0.98644 | -0.25786 | 0.9859 | -0.26826 | 17.3366
68 | 0.16537 | 0.042158 | -0.16532 | -0.042126 | 5.1462e-05 | 3.2481e-05 | 0.24893 | 0.24893 | 0.24893 | 0.98956 | -0.19793 | 0.98922 | -0.20438 | 17.0966
69 | -0.34758 | -0.089046 | 0.3476 | 0.089057 | 1.7121e-05 | 1.0923e-05 | 0.52162 | 0.52162 | 0.52162 | 0.99285 | -0.13511 | 0.9929 | -0.13409 | 35.8257
70 | 0.16549 | 0.042073 | -0.16537 | -0.041994 | 0.00012506 | 7.895e-05 | 0.24999 | 0.25 | 0.25 | 0.9859 | -0.26826 | 0.98508 | -0.28396 | 17.17
71 | 0.16201 | 0.041297 | -0.16192 | -0.041242 | 8.8624e-05 | 5.5904e-05 | 0.24395 | 0.24395 | 0.24395 | 0.98922 | -0.20438 | 0.98863 | -0.21572 | 16.7546
72 | 0.0033109 | 0.00082847 | -0.0033106 | -0.0008287 | 3.1033e-07 | -2.2975e-07 | 0.0049798 | 0.00498 | 0.00498 | 0.98922 | -0.20438 | 0.98912 | -0.20635 | 1.3681
73 | -0.34855 | -0.089296 | 0.34932 | 0.089787 | 0.00076881 | 0.00049048 | 0.52305 | 0.52305 | 0.52305 | 0.9929 | -0.13409 | 0.9953 | -0.088681 | 35.9239
74 | 0.16326 | 0.041465 | -0.16324 | -0.041456 | 1.4729e-05 | 9.2954e-06 | 0.24681 | 0.24681 | 0.24681 | 0.98508 | -0.28396 | 0.98499 | -0.28584 | 16.951
75 | 0.36244 | 0.093628 | -0.36175 | -0.09319 | 0.00068734 | 0.00043859 | 0.54051 | 0.54051 | 0.54051 | 0.99963 | -0.0068936 | 0.99756 | -0.045851 | 37.1229
76 | -0.36389 | -0.093991 | 0.36392 | 0.094014 | 3.638e-05 | 2.3214e-05 | 0.54266 | 0.54266 | 0.54266 | 0.99963 | -0.0068936 | 0.99974 | -0.0048441 | 37.2708
77 | 0.35948 | 0.092621 | -0.35943 | -0.092586 | 5.4647e-05 | 3.4869e-05 | 0.53712 | 0.53712 | 0.53712 | 0.99756 | -0.045851 | 0.9974 | -0.048975 | 36.8903
78 | -0.36542 | -0.094388 | 0.36542 | 0.094391 | 4.003e-06 | 2.5544e-06 | 0.54488 | 0.54488 | 0.54488 | 0.99974 | -0.0048441 | 0.99975 | -0.0046195 | 37.4234
79 | 0.35792 | 0.092207 | -0.3579 | -0.092198 | 1.5327e-05 | 9.7797e-06 | 0.53487 | 0.53487 | 0.53487 | 0.9974 | -0.048975 | 0.99735 | -0.049855 | 36.7356
80 | -0.36688 | -0.094756 | 0.36693 | 0.094787 | 4.8024e-05 | 3.0646e-05 | 0.54706 | 0.54706 | 0.54706 | 0.99975 | -0.0046195 | 0.9999 | -0.001936 | 37.5725
81 | 0.35644 | 0.09183 | -0.3558 | -0.091423 | 0.00063831 | 0.00040727 | 0.53268 | 0.53268 | 0.53268 | 0.99735 | -0.049855 | 0.9954 | -0.086718 | 36.5853
82 | -0.36852 | -0.095187 | 0.36856 | 0.095209 | 3.4803e-05 | 2.2209e-05 | 0.54943 | 0.54943 | 0.54943 | 0.9999 | -0.001936 | 1 | 0 | 37.7355
83 | 0.35254 | 0.090607 | -0.35251 | -0.090586 | 3.3619e-05 | 2.1449e-05 | 0.52782 | 0.52782 | 0.52782 | 0.9954 | -0.086718 | 0.9953 | -0.088681 | 36.2512
84 | 0.16043 | 0.040869 | -0.16041 | -0.040853 | 2.4925e-05 | 1.5719e-05 | 0.24171 | 0.24171 | 0.24171 | 0.98863 | -0.21572 | 0.98846 | -0.21894 | 16.6009
85 | 0.0018395 | 0.00046002 | -0.0018395 | -0.00046025 | 5.9294e-08 | -2.2711e-07 | 0.002767 | 0.0027671 | 0.0027671 | 0.98912 | -0.20635 | 0.98909 | -0.20702 | 0.76019
86 | 0.15811 | 0.040276 | -0.15799 | -0.040204 | 0.00011529 | 7.2675e-05 | 0.23824 | 0.23824 | 0.23824 | 0.98846 | -0.21894 | 0.98768 | -0.23406 | 16.3629
87 | 0.0013912 | 0.00034789 | -0.0013911 | -0.00034815 | 3.5872e-08 | -2.5739e-07 | 0.0020926 | 0.0020927 | 0.0020927 | 0.98909 | -0.20702 | 0.98906 | -0.20757 | 0.57493
88 | 0.15799 | 0.040204 | -0.15788 | -0.040131 | 0.00011493 | 7.245e-05 | 0.23824 | 0.23824 | 0.23824 | 0.98768 | -0.23406 | 0.98689 | -0.24917 | 16.3629
89 | 0.0070139 | 0.0017577 | -0.0070135 | -0.0017575 | 4.712e-07 | 1.6525e-07 | 0.010713 | 0.010713 | 0.010713 | 0.97423 | -0.49595 | 0.97415 | -0.49736 | 2.9431
90 | -0.0099485 | -0.0024932 | 0.0099494 | 0.0024936 | 8.8164e-07 | 4.3745e-07 | 0.015195 | 0.015195 | 0.015195 | 0.97423 | -0.49595 | 0.97432 | -0.49409 | 4.1745
91 | 0.0053359 | 0.0013371 | -0.0053357 | -0.001337 | 2.6522e-07 | 3.7201e-08 | 0.0081505 | 0.0081506 | 0.0081506 | 0.97415 | -0.49736 | 0.9741 | -0.4984 | 2.2392
92 | -0.013439 | -0.0033681 | 0.01344 | 0.0033691 | 1.7888e-06 | 1.0038e-06 | 0.020524 | 0.020524 | 0.020524 | 0.97432 | -0.49409 | 0.97446 | -0.4913 | 5.6385
93 | 0.0033486 | 0.00083905 | -0.0033485 | -0.00083914 | 1.49e-07 | -9.3664e-08 | 0.0051152 | 0.0051153 | 0.0051153 | 0.9741 | -0.4984 | 0.97405 | -0.49934 | 1.4053
94 | -0.016367 | -0.0041026 | 0.016372 | 0.0041054 | 4.7409e-06 | 2.782e-06 | 0.024993 | 0.024993 | 0.024993 | 0.97446 | -0.4913 | 0.97477 | -0.48522 | 6.8662
95 | 0.0015701 | 0.00039344 | -0.0015701 | -0.0003935 | 1.2585e-08 | -6.4555e-08 | 0.0023985 | 0.0023986 | 0.0023986 | 0.97405 | -0.49934 | 0.97405 | -0.49951 | 0.65895
96 | -0.018837 | -0.0047232 | 0.018838 | 0.0047236 | 5.6445e-07 | 3.3856e-07 | 0.028756 | 0.028756 | 0.028756 | 0.97477 | -0.48522 | 0.9748 | -0.48459 | 7.9001
97 | -0.020746 | -0.0052018 | 0.020753 | 0.0052061 | 7.2005e-06 | 4.3695e-06 | 0.031669 | 0.031669 | 0.031669 | 0.9748 | -0.48459 | 0.97517 | -0.47731 | 8.7002
98 | 0.15617 | 0.039703 | -0.15603 | -0.039616 | 0.00013805 | 8.6999e-05 | 0.23567 | 0.23567 | 0.23567 | 0.98689 | -0.24917 | 0.98594 | -0.26754 | 16.1862
99 | 0.15402 | 0.039113 | -0.15387 | -0.039019 | 0.00014974 | 9.4329e-05 | 0.23264 | 0.23264 | 0.23264 | 0.98594 | -0.26754 | 0.98489 | -0.28776 | 15.9782
100 | 0.13501 | 0.034284 | -0.13494 | -0.034237 | 7.4743e-05 | 4.6862e-05 | 0.20414 | 0.20414 | 0.20414 | 0.98489 | -0.28776 | 0.9843 | -0.29927 | 14.0207
101 | 0.018862 | 0.004735 | -0.018856 | -0.0047314 | 5.8766e-06 | 3.5156e-06 | 0.028501 | 0.028501 | 0.028501 | 0.98489 | -0.28776 | 0.98456 | -0.29429 | 7.8299
102 | 0.13315 | 0.033788 | -0.13305 | -0.03373 | 9.3707e-05 | 5.8721e-05 | 0.20144 | 0.20144 | 0.20144 | 0.9843 | -0.29927 | 0.98354 | -0.31391 | 13.8349
103 | 0.017409 | 0.0043687 | -0.017404 | -0.0043656 | 5.232e-06 | 3.0923e-06 | 0.026313 | 0.026314 | 0.026314 | 0.98456 | -0.29429 | 0.98424 | -0.3006 | 7.229
104 | 0.13199 | 0.033464 | -0.13196 | -0.033445 | 3.0532e-05 | 1.9127e-05 | 0.19983 | 0.19983 | 0.19983 | 0.98354 | -0.31391 | 0.98329 | -0.31873 | 13.7249
105 | -0.02251 | -0.0056465 | 0.022512 | 0.0056478 | 2.0626e-06 | 1.2619e-06 | 0.03435 | 0.03435 | 0.03435 | 0.97517 | -0.47731 | 0.97527 | -0.47539 | 9.4368
106 | 0.13037 | 0.033046 | -0.13037 | -0.033044 | 3.3791e-06 | 2.1157e-06 | 0.19743 | 0.19743 | 0.19743 | 0.98329 | -0.31873 | 0.98327 | -0.31927 | 13.5595
107 | 0.12819 | 0.032499 | -0.12817 | -0.032485 | 2.1599e-05 | 1.3513e-05 | 0.19413 | 0.19413 | 0.19413 | 0.98327 | -0.31927 | 0.98308 | -0.32277 | 13.3332
108 | 0.12706 | 0.032208 | -0.12701 | -0.032173 | 5.5726e-05 | 3.4851e-05 | 0.19246 | 0.19246 | 0.19246 | 0.98308 | -0.32277 | 0.98261 | -0.3319 | 13.2182
109 | 0.12591 | 0.031899 | -0.12582 | -0.031842 | 9.1404e-05 | 5.7143e-05 | 0.1908 | 0.1908 | 0.1908 | 0.98261 | -0.3319 | 0.98183 | -0.34703 | 13.1045
110 | 0.12422 | 0.031441 | -0.12422 | -0.031437 | 5.7571e-06 | 3.597e-06 | 0.18838 | 0.18838 | 0.18838 | 0.98183 | -0.34703 | 0.98179 | -0.34799 | 12.9379
111 | 0.0022685 | 0.00056834 | -0.0022685 | -0.00056837 | 1.1285e-08 | -2.5048e-08 | 0.0034361 | 0.0034361 | 0.0034361 | 0.98237 | -0.33704 | 0.98237 | -0.33715 | 0.94399
112 | -0.0038202 | -0.00095724 | 0.0038204 | 0.00095719 | 1.1971e-07 | -4.4096e-08 | 0.0057865 | 0.0057865 | 0.0057865 | 0.98237 | -0.33704 | 0.9824 | -0.33638 | 1.5897
113 | 0.0017524 | 0.00043902 | -0.0017524 | -0.00043918 | 4.0014e-08 | -1.6613e-07 | 0.0026543 | 0.0026544 | 0.0026544 | 0.98237 | -0.33715 | 0.98234 | -0.33762 | 0.72923
114 | -0.0055661 | -0.0013947 | 0.0055663 | 0.0013948 | 1.9761e-07 | 3.2593e-08 | 0.0084307 | 0.0084307 | 0.0084307 | 0.9824 | -0.33638 | 0.98244 | -0.33564 | 2.3161
115 | -0.0070935 | -0.0017775 | 0.0070939 | 0.0017776 | 3.6432e-07 | 1.2658e-07 | 0.010744 | 0.010744 | 0.010744 | 0.98244 | -0.33564 | 0.9825 | -0.33456 | 2.9516
116 | -0.0085667 | -0.0021468 | 0.0085674 | 0.0021471 | 6.8717e-07 | 3.0192e-07 | 0.012974 | 0.012974 | 0.012974 | 0.9825 | -0.33456 | 0.98258 | -0.33288 | 3.5644
117 | -0.010142 | -0.0025416 | 0.010143 | 0.0025423 | 1.4859e-06 | 7.3818e-07 | 0.015358 | 0.015358 | 0.015358 | 0.98258 | -0.33288 | 0.98274 | -0.3298 | 4.2193

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.37103 | 0.095417

## res_load
| p_mw | q_mvar
0 | 0.00097005 | 0.00024312
1 | 0.00042271 | 0.00010594
2 | 0.00082412 | 0.00020654
3 | 0.0017774 | 0.00044546
4 | 0.002063 | 0.00051703
5 | 0.00044242 | 0.00011088
6 | 0.0004424 | 0.00011088
7 | 0.018526 | 0.004643
8 | 0.0044106 | 0.0011054
9 | 0.0036388 | 0.00091196
10 | 0.0032523 | 0.0008151
11 | 0.018682 | 0.0046822
12 | 0.012952 | 0.003246
13 | 0.0022868 | 0.00057314
14 | 0.0095258 | 0.0023874
15 | 0.00088855 | 0.00022269
16 | 0.0026361 | 0.00066066
17 | 0.0023946 | 0.00060014
18 | 0.00093162 | 0.00023349
19 | 0.0036812 | 0.00092259
20 | 0.0012535 | 0.00031415
21 | 0.0010153 | 0.00025447
22 | 0.0012049 | 0.00030197
23 | 0.0028286 | 0.00070892
24 | 0.0013458 | 0.00033728
25 | 0.0010653 | 0.00026699
26 | 0.001415 | 0.00035464
27 | 0.0017093 | 0.00042839
28 | 0.0034475 | 0.00086402
29 | 0.0019407 | 0.00048638
30 | 0.0018871 | 0.00047294
31 | 0.0086627 | 0.0021711
32 | 0.0049723 | 0.0012462
33 | 0.018708 | 0.0046886
34 | 0.022934 | 0.0057479
35 | 0.012524 | 0.0031389
36 | 0.010574 | 0.0026501
37 | 0.001901 | 0.00047645
38 | 0.0035559 | 0.0008912
39 | 0.0023624 | 0.00059208
40 | 0.0019232 | 0.000482
41 | 0.016391 | 0.0041079
42 | 0.015341 | 0.0038449
43 | 0.016437 | 0.0041195
44 | 0.0048753 | 0.0012219
45 | 0.005401 | 0.0013536
46 | 0.002785 | 0.00069799
47 | 0.001747 | 0.00043783
48 | 0.0014614 | 0.00036627
49 | 0.0010131 | 0.00025392
50 | 0.0014327 | 0.00035906
51 | 0.0029911 | 0.00074963
52 | 0.0020433 | 0.00051211
53 | 0.0016074 | 0.00040285
54 | 0.00095421 | 0.00023915
55 | 0.0021106 | 0.00052896
56 | 0.0034538 | 0.0008656
57 | 0.0014473 | 0.00036273
58 | 0.00227 | 0.00056892
59 | 0.001493 | 0.00037419
60 | 0.0015097 | 0.00037837
61 | 0.0014584 | 0.00036552
62 | 0.001467 | 0.00036767
63 | 0.0015951 | 0.00039976
64 | 0.0032546 | 0.00081568
65 | 0.00082841 | 0.00020762
66 | 0.0031878 | 0.00079894
67 | 0.0014866 | 0.00037258
68 | 0.001471 | 0.00036867
69 | 0.0023021 | 0.00057696
70 | 0.00044832 | 0.00011236
71 | 0.00050629 | 0.00012689
72 | 0.0029346 | 0.00073547
73 | 0.0016775 | 0.00042043
74 | 0.0034893 | 0.0008745
75 | 0.001987 | 0.00049799
76 | 0.0029267 | 0.00073349
77 | 0.0017784 | 0.00044571
78 | 0.0024653 | 0.00061787
79 | 0.0015701 | 0.0003935
80 | 0.001908 | 0.00047818
81 | 0.0017066 | 0.00042771
82 | 0.0020078 | 0.00050319
83 | 0.0017902 | 0.00044866
84 | 0.0014472 | 0.0003627
85 | 0.0010584 | 0.00026527
86 | 0.0011841 | 0.00029677
87 | 0.0017572 | 0.00044038
88 | 0.0015919 | 0.00039897
89 | 0.0021774 | 0.0005457
90 | 0.001106 | 0.0002772
91 | 0.0010935 | 0.00027404
92 | 0.0016012 | 0.0004013
93 | 0.0037865 | 0.00094899
94 | 0.0035346 | 0.00088585
95 | 0.0024819 | 0.00062204
96 | 0.0015517 | 0.00038889
97 | 0.00051612 | 0.00012935
98 | 0.0017458 | 0.00043753
99 | 0.0017524 | 0.00043918
100 | 0.0015272 | 0.00038276
101 | 0.0014728 | 0.00036912
102 | 0.0015741 | 0.00039451

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1