## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3273-3_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3273-3_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3273-3_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3273-3_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3273-3_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3273-3_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3273-3_0_4_node_7 | 0.4 | n |  | TRUE
7 | bus_LV_3273-3_0_4_node_126 | 0.4 | n |  | TRUE
8 | bus_LV_3273-3_0_4_node_125 | 0.4 | n |  | TRUE
9 | bus_LV_3273-3_0_4_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_3273-3_0_4_node_50 | 0.4 | n |  | TRUE
11 | bus_LV_3273-3_0_4_node_137 | 0.4 | n |  | TRUE
12 | bus_LV_3273-3_0_4_node_127 | 0.4 | n |  | TRUE
13 | bus_LV_3273-3_0_4_node_46 | 0.4 | n |  | TRUE
14 | bus_LV_3273-3_0_4_node_45 | 0.4 | n |  | TRUE
15 | bus_LV_3273-3_0_4_node_119 | 0.4 | n |  | TRUE
16 | bus_LV_3273-3_0_4_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_3273-3_0_4_node_44 | 0.4 | n |  | TRUE
18 | bus_LV_3273-3_0_4_node_124 | 0.4 | n |  | TRUE
19 | bus_LV_3273-3_0_4_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_3273-3_0_4_node_49 | 0.4 | n |  | TRUE
21 | bus_LV_3273-3_0_4_node_147 | 0.4 | n |  | TRUE
22 | bus_LV_3273-3_0_4_node_121 | 0.4 | n |  | TRUE
23 | bus_LV_3273-3_0_4_node_120 | 0.4 | n |  | TRUE
24 | bus_LV_3273-3_0_4_node_40 | 0.4 | n |  | TRUE
25 | bus_LV_3273-3_0_4_node_42 | 0.4 | n |  | TRUE
26 | bus_LV_3273-3_0_4_node_47 | 0.4 | n |  | TRUE
27 | bus_LV_3273-3_0_4_node_73 | 0.4 | n |  | TRUE
28 | bus_LV_3273-3_0_4_node_43 | 0.4 | n |  | TRUE
29 | bus_LV_3273-3_0_4_node_102 | 0.4 | n |  | TRUE
30 | bus_LV_3273-3_0_4_node_78 | 0.4 | n |  | TRUE
31 | bus_LV_3273-3_0_4_node_75 | 0.4 | n |  | TRUE
32 | bus_LV_3273-3_0_4_node_138 | 0.4 | n |  | TRUE
33 | bus_LV_3273-3_0_4_node_8 | 0.4 | n |  | TRUE
34 | bus_LV_3273-3_0_4_node_9 | 0.4 | n |  | TRUE
35 | bus_LV_3273-3_0_4_node_10 | 0.4 | n |  | TRUE
36 | bus_LV_3273-3_0_4_node_11 | 0.4 | n |  | TRUE
37 | bus_LV_3273-3_0_4_node_12 | 0.4 | n |  | TRUE
38 | bus_LV_3273-3_0_4_node_15 | 0.4 | n |  | TRUE
39 | bus_LV_3273-3_0_4_node_13 | 0.4 | n |  | TRUE
40 | bus_LV_3273-3_0_4_node_21 | 0.4 | n |  | TRUE
41 | bus_LV_3273-3_0_4_node_18 | 0.4 | n |  | TRUE
42 | bus_LV_3273-3_0_4_node_20 | 0.4 | n |  | TRUE
43 | bus_LV_3273-3_0_4_node_16 | 0.4 | n |  | TRUE
44 | bus_LV_3273-3_0_4_node_71 | 0.4 | n |  | TRUE
45 | bus_LV_3273-3_0_4_node_19 | 0.4 | n |  | TRUE
46 | bus_LV_3273-3_0_4_node_17 | 0.4 | n |  | TRUE
47 | bus_LV_3273-3_0_4_node_69 | 0.4 | n |  | TRUE
48 | bus_LV_3273-3_0_4_node_63 | 0.4 | n |  | TRUE
49 | bus_LV_3273-3_0_4_node_128 | 0.4 | n |  | TRUE
50 | bus_LV_3273-3_0_4_node_22 | 0.4 | n |  | TRUE
51 | bus_LV_3273-3_0_4_node_23 | 0.4 | n |  | TRUE
52 | bus_LV_3273-3_0_4_node_24 | 0.4 | n |  | TRUE
53 | bus_LV_3273-3_0_4_node_25 | 0.4 | n |  | TRUE
54 | bus_LV_3273-3_0_4_node_26 | 0.4 | n |  | TRUE
55 | bus_LV_3273-3_0_4_node_27 | 0.4 | n |  | TRUE
56 | bus_LV_3273-3_0_4_node_28 | 0.4 | n |  | TRUE
57 | bus_LV_3273-3_0_4_node_29 | 0.4 | n |  | TRUE
58 | bus_LV_3273-3_0_4_node_30 | 0.4 | n |  | TRUE
59 | bus_LV_3273-3_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_3273-3_0_4_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_3273-3_0_4_node_53 | 0.4 | n |  | TRUE
62 | bus_LV_3273-3_0_4_node_34 | 0.4 | n |  | TRUE
63 | bus_LV_3273-3_0_4_node_32 | 0.4 | n |  | TRUE
64 | bus_LV_3273-3_0_4_node_38 | 0.4 | n |  | TRUE
65 | bus_LV_3273-3_0_4_node_37 | 0.4 | n |  | TRUE
66 | bus_LV_3273-3_0_4_node_33 | 0.4 | n |  | TRUE
67 | bus_LV_3273-3_0_4_node_35 | 0.4 | n |  | TRUE
68 | bus_LV_3273-3_0_4_node_39 | 0.4 | n |  | TRUE
69 | bus_LV_3273-3_0_4_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_3273-3_0_4_node_72 | 0.4 | n |  | TRUE
71 | bus_LV_3273-3_0_4_node_100 | 0.4 | n |  | TRUE
72 | bus_LV_3273-3_0_4_node_66 | 0.4 | n |  | TRUE
73 | bus_LV_3273-3_0_4_node_67 | 0.4 | n |  | TRUE
74 | bus_LV_3273-3_0_4_node_60 | 0.4 | n |  | TRUE
75 | bus_LV_3273-3_0_4_node_74 | 0.4 | n |  | TRUE
76 | bus_LV_3273-3_0_4_node_101 | 0.4 | n |  | TRUE
77 | bus_LV_3273-3_0_4_node_123 | 0.4 | n |  | TRUE
78 | bus_LV_3273-3_0_4_node_80 | 0.4 | n |  | TRUE
79 | bus_LV_3273-3_0_4_node_81 | 0.4 | n |  | TRUE
80 | bus_LV_3273-3_0_4_node_76 | 0.4 | n |  | TRUE
81 | bus_LV_3273-3_0_4_node_122 | 0.4 | n |  | TRUE
82 | bus_LV_3273-3_0_4_node_51 | 0.4 | n |  | TRUE
83 | bus_LV_3273-3_0_4_node_52 | 0.4 | n |  | TRUE
84 | bus_LV_3273-3_0_4_node_54 | 0.4 | n |  | TRUE
85 | bus_LV_3273-3_0_4_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_3273-3_0_4_node_57 | 0.4 | n |  | TRUE
87 | bus_LV_3273-3_0_4_node_58 | 0.4 | n |  | TRUE
88 | bus_LV_3273-3_0_4_node_59 | 0.4 | n |  | TRUE
89 | bus_LV_3273-3_0_4_node_64 | 0.4 | n |  | TRUE
90 | bus_LV_3273-3_0_4_node_65 | 0.4 | n |  | TRUE
91 | bus_LV_3273-3_0_4_node_129 | 0.4 | n |  | TRUE
92 | bus_LV_3273-3_0_4_node_70 | 0.4 | n |  | TRUE
93 | bus_LV_3273-3_0_4_node_68 | 0.4 | n |  | TRUE
94 | bus_LV_3273-3_0_4_node_77 | 0.4 | n |  | TRUE
95 | bus_LV_3273-3_0_4_node_79 | 0.4 | n |  | TRUE
96 | bus_LV_3273-3_0_4_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_3273-3_0_4_node_116 | 0.4 | n |  | TRUE
98 | bus_LV_3273-3_0_4_node_91 | 0.4 | n |  | TRUE
99 | bus_LV_3273-3_0_4_node_146 | 0.4 | n |  | TRUE
100 | bus_LV_3273-3_0_4_node_118 | 0.4 | n |  | TRUE
101 | bus_LV_3273-3_0_4_node_104 | 0.4 | n |  | TRUE
102 | bus_LV_3273-3_0_4_node_106 | 0.4 | n |  | TRUE
103 | bus_LV_3273-3_0_4_node_103 | 0.4 | n |  | TRUE
104 | bus_LV_3273-3_0_4_node_108 | 0.4 | n |  | TRUE
105 | bus_LV_3273-3_0_4_node_115 | 0.4 | n |  | TRUE
106 | bus_LV_3273-3_0_4_node_111 | 0.4 | n |  | TRUE
107 | bus_LV_3273-3_0_4_node_113 | 0.4 | n |  | TRUE
108 | bus_LV_3273-3_0_4_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_3273-3_0_4_node_82 | 0.4 | n |  | TRUE
110 | bus_LV_3273-3_0_4_node_83 | 0.4 | n |  | TRUE
111 | bus_LV_3273-3_0_4_node_84 | 0.4 | n |  | TRUE
112 | bus_LV_3273-3_0_4_node_85 | 0.4 | n |  | TRUE
113 | bus_LV_3273-3_0_4_node_86 | 0.4 | n |  | TRUE
114 | bus_LV_3273-3_0_4_node_87 | 0.4 | n |  | TRUE
115 | bus_LV_3273-3_0_4_node_88 | 0.4 | n |  | TRUE
116 | bus_LV_3273-3_0_4_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_3273-3_0_4_node_144 | 0.4 | n |  | TRUE
118 | bus_LV_3273-3_0_4_node_89 | 0.4 | n |  | TRUE
119 | bus_LV_3273-3_0_4_node_145 | 0.4 | n |  | TRUE
120 | bus_LV_3273-3_0_4_node_92 | 0.4 | n |  | TRUE
121 | bus_LV_3273-3_0_4_node_142 | 0.4 | n |  | TRUE
122 | bus_LV_3273-3_0_4_node_143 | 0.4 | n |  | TRUE
123 | bus_LV_3273-3_0_4_node_94 | 0.4 | n |  | TRUE
124 | bus_LV_3273-3_0_4_node_95 | 0.4 | n |  | TRUE
125 | bus_LV_3273-3_0_4_node_96 | 0.4 | n |  | TRUE
126 | bus_LV_3273-3_0_4_node_97 | 0.4 | n |  | TRUE
127 | bus_LV_3273-3_0_4_node_98 | 0.4 | n |  | TRUE
128 | bus_LV_3273-3_0_4_node_99 | 0.4 | n |  | TRUE
129 | bus_LV_3273-3_0_4_node_130 | 0.4 | n |  | TRUE
130 | bus_LV_3273-3_0_4_node_131 | 0.4 | n |  | TRUE
131 | bus_LV_3273-3_0_4_node_107 | 0.4 | n |  | TRUE
132 | bus_LV_3273-3_0_4_node_112 | 0.4 | n |  | TRUE
133 | bus_LV_3273-3_0_4_node_109 | 0.4 | n |  | TRUE
134 | bus_LV_3273-3_0_4_node_114 | 0.4 | n |  | TRUE
135 | bus_LV_3273-3_0_4_node_117 | 0.4 | n |  | TRUE
136 | bus_LV_3273-3_0_4_node_133 | 0.4 | n |  | TRUE
137 | bus_LV_3273-3_0_4_node_134 | 0.4 | n |  | TRUE
138 | bus_LV_3273-3_0_4_node_135 | 0.4 | n |  | TRUE
139 | bus_LV_3273-3_0_4_node_136 | 0.4 | n |  | TRUE
140 | bus_LV_3273-3_0_4_node_139 | 0.4 | n |  | TRUE
141 | bus_LV_3273-3_0_4_node_141 | 0.4 | n |  | TRUE
142 | bus_MV_237_0_node_128 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3273-3_0_4_load_0 | 0 | 0.022019 | 0.0055185 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3273-3_0_4_load_1 | 1 | 0.022954 | 0.0057527 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3273-3_0_4_load_4 | 4 | 0.0010064 | 0.00025224 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3273-3_0_4_load_7 | 6 | 0.0024343 | 0.00061008 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3273-3_0_4_load_126 | 7 | 0.0025444 | 0.0006377 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3273-3_0_4_load_125 | 8 | 0.0033772 | 0.0008464 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3273-3_0_4_load_137 | 11 | 0.0021338 | 0.00053479 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3273-3_0_4_load_127 | 12 | 0.0021726 | 0.00054449 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3273-3_0_4_load_119 | 15 | 0.007124 | 0.0017854 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3273-3_0_4_load_124 | 18 | 0.0057613 | 0.0014439 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3273-3_0_4_load_147 | 21 | 0.0028914 | 0.00072466 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3273-3_0_4_load_121 | 22 | 0.0044926 | 0.0011259 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3273-3_0_4_load_120 | 23 | 0.0036857 | 0.00092372 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3273-3_0_4_load_40 | 24 | 0.0076413 | 0.0019151 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3273-3_0_4_load_73 | 27 | 0.0033774 | 0.00084645 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3273-3_0_4_load_102 | 29 | 0.003458 | 0.00086666 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3273-3_0_4_load_75 | 31 | 0.0042889 | 0.0010749 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3273-3_0_4_load_138 | 32 | 0.001608 | 0.00040301 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3273-3_0_4_load_8 | 33 | 0.022591 | 0.0056618 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3273-3_0_4_load_9 | 34 | 0.002675 | 0.00067041 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3273-3_0_4_load_11 | 36 | 0.0034195 | 0.00085702 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3273-3_0_4_load_12 | 37 | 0.0031829 | 0.00079771 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3273-3_0_4_load_15 | 38 | 0.0044903 | 0.0011254 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3273-3_0_4_load_21 | 40 | 0.0020098 | 0.00050371 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3273-3_0_4_load_18 | 41 | 0.0044677 | 0.0011197 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3273-3_0_4_load_16 | 43 | 0.0053377 | 0.0013378 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3273-3_0_4_load_71 | 44 | 0.0037406 | 0.00093748 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3273-3_0_4_load_19 | 45 | 0.0059437 | 0.0014896 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3273-3_0_4_load_17 | 46 | 0.0033986 | 0.00085176 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3273-3_0_4_load_69 | 47 | 0.0020803 | 0.00052137 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3273-3_0_4_load_63 | 48 | 0.0031225 | 0.00078256 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3273-3_0_4_load_22 | 50 | 0.0039339 | 0.00098592 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3273-3_0_4_load_23 | 51 | 0.0018861 | 0.00047269 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3273-3_0_4_load_25 | 53 | 0.003565 | 0.00089348 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3273-3_0_4_load_26 | 54 | 0.0012991 | 0.00032559 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3273-3_0_4_load_27 | 55 | 0.002799 | 0.0007015 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3273-3_0_4_load_28 | 56 | 0.0043564 | 0.0010918 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3273-3_0_4_load_29 | 57 | 0.0021228 | 0.00053204 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3273-3_0_4_load_30 | 58 | 0.0015936 | 0.0003994 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3273-3_0_4_load_55 | 59 | 0.0052565 | 0.0013174 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3273-3_0_4_load_36 | 60 | 0.0017831 | 0.00044689 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3273-3_0_4_load_34 | 62 | 0.0021082 | 0.00052837 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3273-3_0_4_load_32 | 63 | 0.0037381 | 0.00093687 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3273-3_0_4_load_38 | 64 | 0.0024432 | 0.00061233 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3273-3_0_4_load_33 | 66 | 0.0024946 | 0.00062521 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3273-3_0_4_load_35 | 67 | 0.0033402 | 0.00083714 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3273-3_0_4_load_39 | 68 | 0.0030891 | 0.00077421 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3273-3_0_4_load_61 | 69 | 0.0021161 | 0.00053035 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3273-3_0_4_load_72 | 70 | 0.00026932 | 6.7497e-05 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3273-3_0_4_load_100 | 71 | 0.0083483 | 0.0020923 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3273-3_0_4_load_60 | 74 | 0.0058577 | 0.0014681 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3273-3_0_4_load_74 | 75 | 0.011853 | 0.0029707 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3273-3_0_4_load_101 | 76 | 0.0091485 | 0.0022928 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3273-3_0_4_load_123 | 77 | 0.0024022 | 0.00060205 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3273-3_0_4_load_80 | 78 | 0.0086611 | 0.0021707 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3273-3_0_4_load_81 | 79 | 0.0039516 | 0.00099035 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3273-3_0_4_load_76 | 80 | 0.0043764 | 0.0010968 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3273-3_0_4_load_122 | 81 | 0.0032796 | 0.00082195 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3273-3_0_4_load_51 | 82 | 0.0046369 | 0.0011621 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3273-3_0_4_load_52 | 83 | 0.0047715 | 0.0011959 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3273-3_0_4_load_54 | 84 | 0.0034319 | 0.00086011 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3273-3_0_4_load_56 | 85 | 0.0050876 | 0.0012751 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3273-3_0_4_load_57 | 86 | 0.007394 | 0.0018531 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3273-3_0_4_load_58 | 87 | 0.0030015 | 0.00075225 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3273-3_0_4_load_59 | 88 | 0.0032847 | 0.00082322 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3273-3_0_4_load_64 | 89 | 0.0028227 | 0.00070743 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3273-3_0_4_load_65 | 90 | 0.0017336 | 0.00043447 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3273-3_0_4_load_70 | 92 | 0.0032308 | 0.00080971 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3273-3_0_4_load_68 | 93 | 0.0024233 | 0.00060734 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3273-3_0_4_load_77 | 94 | 0.0015954 | 0.00039984 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3273-3_0_4_load_79 | 95 | 0.0021887 | 0.00054853 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3273-3_0_4_load_90 | 96 | 0.0037146 | 0.00093096 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3273-3_0_4_load_116 | 97 | 0.0057132 | 0.0014319 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3273-3_0_4_load_91 | 98 | 0.0020009 | 0.00050147 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3273-3_0_4_load_118 | 100 | 0.007139 | 0.0017892 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3273-3_0_4_load_104 | 101 | 0.0040417 | 0.0010129 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3273-3_0_4_load_103 | 103 | 0.001842 | 0.00046166 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3273-3_0_4_load_108 | 104 | 0.0092631 | 0.0023216 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3273-3_0_4_load_115 | 105 | 0.0042599 | 0.0010676 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3273-3_0_4_load_111 | 106 | 0.0099464 | 0.0024928 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3273-3_0_4_load_113 | 107 | 0.0038287 | 0.00095956 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3273-3_0_4_load_110 | 108 | 0.0054474 | 0.0013653 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3273-3_0_4_load_82 | 109 | 0.0020881 | 0.00052333 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3273-3_0_4_load_83 | 110 | 0.0024165 | 0.00060564 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3273-3_0_4_load_84 | 111 | 0.004162 | 0.0010431 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3273-3_0_4_load_86 | 113 | 0.0035173 | 0.00088152 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3273-3_0_4_load_87 | 114 | 0.0022485 | 0.00056353 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3273-3_0_4_load_88 | 115 | 0.0021288 | 0.00053354 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3273-3_0_4_load_93 | 116 | 0.0030123 | 0.00075494 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3273-3_0_4_load_89 | 118 | 0.0031325 | 0.00078507 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3273-3_0_4_load_145 | 119 | 0.0023826 | 0.00059715 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3273-3_0_4_load_142 | 121 | 0.0028078 | 0.00070371 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3273-3_0_4_load_143 | 122 | 0.0032528 | 0.00081524 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3273-3_0_4_load_94 | 123 | 0.0010517 | 0.00026359 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3273-3_0_4_load_95 | 124 | 0.018679 | 0.0046813 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3273-3_0_4_load_96 | 125 | 0.0038065 | 0.00095399 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3273-3_0_4_load_97 | 126 | 0.0046563 | 0.001167 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3273-3_0_4_load_98 | 127 | 0.0038691 | 0.00096968 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3273-3_0_4_load_130 | 129 | 0.0014373 | 0.00036021 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3273-3_0_4_load_131 | 130 | 0.0013557 | 0.00033978 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_3273-3_0_4_load_112 | 132 | 0.0037281 | 0.00093434 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_3273-3_0_4_load_109 | 133 | 0.0032725 | 0.00082017 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_3273-3_0_4_load_117 | 135 | 0.0035225 | 0.00088282 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_3273-3_0_4_load_133 | 136 | 0.0022066 | 0.00055303 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_3273-3_0_4_load_135 | 138 | 0.0012037 | 0.00030168 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_3273-3_0_4_load_139 | 140 | 0.0015119 | 0.00037891 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_3273-3_0_4_load_141 | 141 | 0.0019815 | 0.00049661 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 9 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3273-3_0_4_line_0 |  | 0 | 1 | 0.030652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3273-3_0_4_line_1 |  | 0 | 2 | 0.028084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3273-3_0_4_line_2 |  | 2 | 3 | 0.010961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_3273-3_0_4_line_3 |  | 2 | 4 | 0.038593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_3273-3_0_4_line_4 |  | 3 | 5 | 0.014737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_3273-3_0_4_line_5 |  | 4 | 6 | 0.0015595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
6 | LV_3273-3_0_4_line_6 |  | 5 | 7 | 0.011275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3273-3_0_4_line_7 |  | 5 | 8 | 0.0043109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_3273-3_0_4_line_8 |  | 6 | 11 | 0.021914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
9 | LV_3273-3_0_4_line_9 |  | 7 | 12 | 0.037732 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3273-3_0_4_line_10 |  | 8 | 13 | 0.020523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_3273-3_0_4_line_11 |  | 9 | 10 | 0.022323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_3273-3_0_4_line_12 |  | 10 | 22 | 0.0029409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_3273-3_0_4_line_13 |  | 10 | 23 | 0.018842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_3273-3_0_4_line_14 |  | 11 | 32 | 0.0048478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
15 | LV_3273-3_0_4_line_15 |  | 12 | 128 | 0.011579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3273-3_0_4_line_16 |  | 13 | 18 | 0.0079856 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
17 | LV_3273-3_0_4_line_17 |  | 14 | 15 | 0.005869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_3273-3_0_4_line_18 |  | 14 | 16 | 0.010769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3273-3_0_4_line_19 |  | 14 | 17 | 0.020541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
20 | LV_3273-3_0_4_line_20 |  | 15 | 23 | 0.013494 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
21 | LV_3273-3_0_4_line_21 |  | 16 | 24 | 0.012523 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3273-3_0_4_line_22 |  | 17 | 27 | 0.0029591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
23 | LV_3273-3_0_4_line_23 |  | 17 | 28 | 0.014314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3273-3_0_4_line_24 |  | 18 | 77 | 0.0052101 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
25 | LV_3273-3_0_4_line_25 |  | 19 | 20 | 0.032989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3273-3_0_4_line_26 |  | 19 | 21 | 0.016303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3273-3_0_4_line_27 |  | 20 | 30 | 0.020858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3273-3_0_4_line_28 |  | 20 | 31 | 0.013688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3273-3_0_4_line_29 |  | 22 | 81 | 0.0082875 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
30 | LV_3273-3_0_4_line_30 |  | 24 | 25 | 0.027041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3273-3_0_4_line_31 |  | 25 | 26 | 0.012402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3273-3_0_4_line_32 |  | 26 | 29 | 0.0051953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3273-3_0_4_line_33 |  | 27 | 75 | 0.016292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
34 | LV_3273-3_0_4_line_34 |  | 28 | 71 | 0.021006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3273-3_0_4_line_35 |  | 30 | 78 | 0.022837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3273-3_0_4_line_36 |  | 30 | 79 | 0.031994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3273-3_0_4_line_37 |  | 31 | 80 | 0.0051215 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3273-3_0_4_line_38 |  | 32 | 123 | 0.00034515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_3273-3_0_4_line_39 |  | 33 | 34 | 0.0056667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3273-3_0_4_line_40 |  | 33 | 35 | 0.024785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3273-3_0_4_line_41 |  | 34 | 36 | 0.011544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3273-3_0_4_line_42 |  | 35 | 37 | 0.0092142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3273-3_0_4_line_43 |  | 36 | 38 | 0.10627 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3273-3_0_4_line_44 |  | 38 | 42 | 0.014197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3273-3_0_4_line_45 |  | 39 | 40 | 0.048759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3273-3_0_4_line_46 |  | 39 | 41 | 0.014823 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3273-3_0_4_line_47 |  | 41 | 43 | 0.021771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3273-3_0_4_line_48 |  | 42 | 44 | 0.0070111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3273-3_0_4_line_49 |  | 42 | 45 | 0.0030121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3273-3_0_4_line_50 |  | 43 | 46 | 0.0064422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3273-3_0_4_line_51 |  | 44 | 47 | 0.0082162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3273-3_0_4_line_52 |  | 45 | 46 | 0.014039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3273-3_0_4_line_53 |  | 47 | 93 | 0.0043334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3273-3_0_4_line_54 |  | 48 | 49 | 0.04039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3273-3_0_4_line_55 |  | 49 | 91 | 0.013432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3273-3_0_4_line_56 |  | 50 | 51 | 0.0066556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3273-3_0_4_line_57 |  | 50 | 52 | 0.0027895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3273-3_0_4_line_58 |  | 51 | 53 | 0.0077536 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3273-3_0_4_line_59 |  | 52 | 54 | 0.0067596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3273-3_0_4_line_60 |  | 52 | 55 | 0.0055861 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3273-3_0_4_line_61 |  | 53 | 56 | 0.0033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3273-3_0_4_line_62 |  | 54 | 57 | 0.0008247 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3273-3_0_4_line_63 |  | 55 | 58 | 0.0072946 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3273-3_0_4_line_64 |  | 56 | 59 | 0.0050221 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3273-3_0_4_line_65 |  | 58 | 60 | 0.0066632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3273-3_0_4_line_66 |  | 59 | 61 | 0.0097098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3273-3_0_4_line_67 |  | 60 | 62 | 0.00035897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3273-3_0_4_line_68 |  | 61 | 85 | 0.0096043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3273-3_0_4_line_69 |  | 61 | 82 | 0.0040163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3273-3_0_4_line_70 |  | 62 | 66 | 0.0068239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3273-3_0_4_line_71 |  | 63 | 64 | 0.0069745 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3273-3_0_4_line_72 |  | 64 | 65 | 0.0135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3273-3_0_4_line_73 |  | 65 | 68 | 0.01527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3273-3_0_4_line_74 |  | 65 | 67 | 0.0095729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3273-3_0_4_line_75 |  | 66 | 67 | 0.0036176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3273-3_0_4_line_76 |  | 68 | 69 | 0.00044684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3273-3_0_4_line_77 |  | 69 | 70 | 0.17084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3273-3_0_4_line_78 |  | 71 | 76 | 0.016727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3273-3_0_4_line_79 |  | 72 | 73 | 0.037248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
80 | LV_3273-3_0_4_line_80 |  | 72 | 74 | 0.01199 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
81 | LV_3273-3_0_4_line_81 |  | 73 | 75 | 0.015941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
82 | LV_3273-3_0_4_line_82 |  | 74 | 88 | 0.0074702 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
83 | LV_3273-3_0_4_line_83 |  | 77 | 81 | 0.018045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
84 | LV_3273-3_0_4_line_84 |  | 78 | 97 | 0.032217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3273-3_0_4_line_85 |  | 80 | 94 | 0.014934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3273-3_0_4_line_86 |  | 82 | 83 | 0.006919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3273-3_0_4_line_87 |  | 83 | 84 | 0.00091933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3273-3_0_4_line_88 |  | 84 | 86 | 0.0097952 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
89 | LV_3273-3_0_4_line_89 |  | 85 | 87 | 0.004864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3273-3_0_4_line_90 |  | 86 | 88 | 0.00033365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
91 | LV_3273-3_0_4_line_91 |  | 87 | 89 | 0.0039453 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3273-3_0_4_line_92 |  | 89 | 90 | 0.0021218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3273-3_0_4_line_93 |  | 90 | 92 | 0.0050389 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3273-3_0_4_line_94 |  | 91 | 130 | 0.02222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3273-3_0_4_line_95 |  | 92 | 93 | 0.0033591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3273-3_0_4_line_96 |  | 94 | 95 | 0.0040724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3273-3_0_4_line_97 |  | 95 | 96 | 0.011376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_3273-3_0_4_line_98 |  | 96 | 98 | 0.015743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_3273-3_0_4_line_99 |  | 97 | 99 | 0.018804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_3273-3_0_4_line_100 |  | 97 | 100 | 0.033607 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3273-3_0_4_line_101 |  | 98 | 120 | 0.037095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
102 | LV_3273-3_0_4_line_102 |  | 99 | 119 | 0.037542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3273-3_0_4_line_103 |  | 100 | 135 | 0.0265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3273-3_0_4_line_104 |  | 101 | 102 | 0.014182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3273-3_0_4_line_105 |  | 101 | 103 | 0.028334 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3273-3_0_4_line_106 |  | 102 | 104 | 0.017846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3273-3_0_4_line_107 |  | 104 | 105 | 0.002412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3273-3_0_4_line_108 |  | 105 | 107 | 0.014229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3273-3_0_4_line_109 |  | 106 | 107 | 0.017459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3273-3_0_4_line_110 |  | 106 | 108 | 0.026746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_3273-3_0_4_line_111 |  | 108 | 133 | 0.025736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3273-3_0_4_line_112 |  | 109 | 110 | 0.012838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3273-3_0_4_line_113 |  | 109 | 111 | 0.033668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3273-3_0_4_line_114 |  | 110 | 112 | 0.01204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3273-3_0_4_line_115 |  | 111 | 113 | 0.00183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3273-3_0_4_line_116 |  | 112 | 114 | 0.0048826 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3273-3_0_4_line_117 |  | 112 | 115 | 0.03211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_3273-3_0_4_line_118 |  | 114 | 116 | 0.0051127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_3273-3_0_4_line_119 |  | 115 | 117 | 0.014983 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_3273-3_0_4_line_120 |  | 116 | 120 | 0.014689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_3273-3_0_4_line_121 |  | 117 | 121 | 0.018624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_3273-3_0_4_line_122 |  | 117 | 122 | 0.025455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_3273-3_0_4_line_123 |  | 118 | 119 | 0.021579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_3273-3_0_4_line_124 |  | 120 | 123 | 0.0097777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
125 | LV_3273-3_0_4_line_125 |  | 122 | 141 | 0.010713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_3273-3_0_4_line_126 |  | 124 | 125 | 0.0075249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_3273-3_0_4_line_127 |  | 124 | 126 | 0.010308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_3273-3_0_4_line_128 |  | 125 | 127 | 0.005659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_3273-3_0_4_line_129 |  | 127 | 128 | 0.020929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_3273-3_0_4_line_130 |  | 128 | 129 | 0.0017613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_3273-3_0_4_line_131 |  | 129 | 130 | 0.046798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_3273-3_0_4_line_132 |  | 131 | 132 | 0.015529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_3273-3_0_4_line_133 |  | 131 | 133 | 0.0090568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_3273-3_0_4_line_134 |  | 132 | 134 | 0.013363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_3273-3_0_4_line_135 |  | 134 | 135 | 0.01187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_3273-3_0_4_line_136 |  | 136 | 137 | 0.012709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_3273-3_0_4_line_137 |  | 137 | 138 | 0.013976 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_3273-3_0_4_line_138 |  | 138 | 139 | 0.036454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_3273-3_0_4_line_139 |  | 139 | 140 | 0.013785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_3273-3_0_4_line_140 |  | 140 | 141 | 0.016779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3273-3_0_4_trafo_6 | 0.63 MVA 20/0.4 kV | 142 | 9 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13
0 | 2753438.3492 | 1226274.0638 | 2753456.2074 | 1226273.8892 | 2753461.8046 | 1226269.7742 | 2753467.5306 | 1226268.5985
1 | 2753410.2663 | 1226274.3384 | 2753438.3492 | 1226274.0638
2 | 2753407.262 | 1226263.7958 | 2753410.2663 | 1226274.3384
3 | 2753410.2663 | 1226274.3384 | 2753420.8395 | 1226311.4544
4 | 2753403.2212 | 1226249.6231 | 2753404.6885 | 1226254.7767 | 2753407.262 | 1226263.7958
5 | 2753420.8395 | 1226311.4544 | 2753421.2668 | 1226312.9543
6 | 2753403.2212 | 1226249.6231 | 2753391.9458 | 1226249.6506
7 | 2753403.2212 | 1226249.6231 | 2753407.532 | 1226249.661
8 | 2753427.2707 | 1226334.0303 | 2753421.2668 | 1226312.9543
9 | 2753391.9458 | 1226249.6506 | 2753364.6306 | 1226249.7174 | 2753354.2415 | 1226250.4765
10 | 2753428.0538 | 1226249.8412 | 2753407.532 | 1226249.661
11 | 2753462.346 | 1226231.7533 | 2753464.4002 | 1226238.557 | 2753465.0079 | 1226240.5745 | 2753465.5459 | 1226242.3567 | 2753466.0693 | 1226244.1162 | 2753466.2677 | 1226245.834 | 2753466.5728 | 1226248.4109 | 2753466.8519 | 1226250.8203 | 2753467.1628 | 1226253.4641
12 | 2753462.346 | 1226231.7533 | 2753459.774 | 1226233.1793
13 | 2753462.346 | 1226231.7533 | 2753475.3956 | 1226223.0486 | 2753477.9836 | 1226221.2432
14 | 2753427.2707 | 1226334.0303 | 2753428.5988 | 1226338.6926
15 | 2753342.6937 | 1226251.3203 | 2753354.2415 | 1226250.4765
16 | 2753428.0538 | 1226249.8412 | 2753429.7266 | 1226242.0328
17 | 2753492.9791 | 1226214.6944 | 2753490.5527 | 1226213.4974 | 2753487.7144 | 1226212.1007
18 | 2753492.9791 | 1226214.6944 | 2753495.0985 | 1226215.7389 | 2753496.3642 | 1226216.361 | 2753497.5557 | 1226216.6253 | 2753499.7045 | 1226217.1145 | 2753501.7251 | 1226217.5782 | 2753503.188 | 1226217.9051
19 | 2753492.9791 | 1226214.6944 | 2753500.1057 | 1226206.5708 | 2753503.4437 | 1226197.4263
20 | 2753487.7144 | 1226212.1007 | 2753487.7144 | 1226212.1007 | 2753483.5282 | 1226217.3753 | 2753477.9836 | 1226221.2432
21 | 2753503.188 | 1226217.9051 | 2753504.7591 | 1226223.1504 | 2753506.3983 | 1226230.0044
22 | 2753503.4437 | 1226197.4263 | 2753504.4554 | 1226194.6455
23 | 2753503.4437 | 1226197.4263 | 2753507.8241 | 1226198.7294 | 2753517.1644 | 1226201.5062
24 | 2753434.8585 | 1226241.1334 | 2753429.7266 | 1226242.0328 | 2753429.7266 | 1226242.0328
25 | 2753527.9623 | 1226323.4742 | 2753524.1416 | 1226308.1394 | 2753534.0734 | 1226306.5052 | 2753538.1229 | 1226300.6488
26 | 2753538.1229 | 1226300.6488 | 2753537.1467 | 1226297.0425 | 2753539.2221 | 1226290.39 | 2753541.3613 | 1226285.2167
27 | 2753527.9623 | 1226323.4742 | 2753533.1362 | 1226343.6818
28 | 2753527.9623 | 1226323.4742 | 2753514.3123 | 1226324.4941
29 | 2753459.774 | 1226233.1793 | 2753458.0526 | 1226234.1337 | 2753452.2014 | 1226236.5203
30 | 2753506.0105 | 1226256.6356 | 2753506.4449 | 1226248.3281 | 2753508.3338 | 1226239.5021 | 2753507.3123 | 1226233.8261 | 2753506.3983 | 1226230.0044
31 | 2753494.782 | 1226261.784 | 2753496.4329 | 1226260.7034 | 2753497.4899 | 1226260.0078 | 2753498.4706 | 1226259.6216 | 2753500.9456 | 1226258.6401 | 2753503.2519 | 1226257.7321 | 2753506.0105 | 1226256.6356
32 | 2753494.782 | 1226261.784 | 2753493.208 | 1226262.8222 | 2753491.5032 | 1226263.9348 | 2753490.7432 | 1226262.9122
33 | 2753504.4554 | 1226194.6455 | 2753508.799 | 1226182.7065 | 2753510.2752 | 1226179.4372
34 | 2753517.1644 | 1226201.5062 | 2753522.7108 | 1226203.4733 | 2753535.9391 | 1226210.7979
35 | 2753533.1362 | 1226343.6818 | 2753538.8025 | 1226365.805
36 | 2753533.1362 | 1226343.6818 | 2753564.8604 | 1226339.5339
37 | 2753514.3123 | 1226324.4941 | 2753509.2051 | 1226324.8757
38 | 2753428.5988 | 1226338.6926 | 2753428.6934 | 1226339.0246
39 | 2753353.7626 | 1226133.0842 | 2753358.3988 | 1226129.8257
40 | 2753330.1025 | 1226138.4481 | 2753343.0356 | 1226138.081 | 2753353.1341 | 1226133.5259 | 2753353.7626 | 1226133.0842
41 | 2753367.9288 | 1226123.3131 | 2753362.6736 | 1226126.8212 | 2753358.3988 | 1226129.8257
42 | 2753330.1025 | 1226138.4481 | 2753322.1371 | 1226133.8164
43 | 2753367.9288 | 1226123.3131 | 2753371.2552 | 1226121.0927 | 2753390.7301 | 1226128.2122 | 2753392.0727 | 1226132.9067 | 2753395.2196 | 1226134.9897 | 2753397.8583 | 1226130.8984 | 2753405.7298 | 1226134.7604 | 2753410.6149 | 1226127.969 | 2753415.7144 | 1226131.0922 | 2753425.0771 | 1226136.8277 | 2753438.3981 | 1226137.5941 | 2753447.9385 | 1226144.3796 | 2753448.6922 | 1226145.4445 | 2753448.418 | 1226152.999
44 | 2753453.9694 | 1226164.3089 | 2753448.1672 | 1226159.9108 | 2753448.418 | 1226152.999
45 | 2753407.3554 | 1226201.3855 | 2753399.592 | 1226208.0359 | 2753384.2131 | 1226214.7234 | 2753369.125 | 1226218.9607 | 2753363.6901 | 1226221.7191
46 | 2753407.3554 | 1226201.3855 | 2753411.8777 | 1226200.4234 | 2753415.4031 | 1226197.5339 | 2753419.6823 | 1226193.8585
47 | 2753419.6823 | 1226193.8585 | 2753423.8883 | 1226190.246 | 2753428.843 | 1226186.0476 | 2753436.2029 | 1226179.68
48 | 2753453.9694 | 1226164.3089 | 2753458.8842 | 1226159.3089 | 2753458.8842 | 1226159.3089
49 | 2753453.9694 | 1226164.3089 | 2753451.6915 | 1226166.2797
50 | 2753436.2029 | 1226179.68 | 2753441.0748 | 1226175.465
51 | 2753458.8842 | 1226159.3089 | 2753463.5707 | 1226152.5604
52 | 2753451.6915 | 1226166.2797 | 2753441.0748 | 1226175.465
53 | 2753466.0425 | 1226149.001 | 2753463.5707 | 1226152.5604
54 | 2753267.5964 | 1226248.9279 | 2753274.1668 | 1226245.0047 | 2753286.1617 | 1226242.1888 | 2753290.2759 | 1226241.4608 | 2753299.8444 | 1226238.6269 | 2753305.9692 | 1226237.3358
55 | 2753267.5964 | 1226248.9279 | 2753272.8213 | 1226261.3071
56 | 2753457.4549 | 1226097.8369 | 2753461.3391 | 1226103.2415
57 | 2753455.8269 | 1226095.5717 | 2753457.4549 | 1226097.8369
58 | 2753466.2056 | 1226109.2656 | 2753463.2948 | 1226105.9627 | 2753461.3391 | 1226103.2415
59 | 2753455.8269 | 1226095.5717 | 2753457.1065 | 1226094.4815 | 2753460.9267 | 1226091.1352
60 | 2753455.8269 | 1226095.5717 | 2753452.4593 | 1226091.1148
61 | 2753466.2056 | 1226109.2656 | 2753468.3874 | 1226111.7414
62 | 2753461.5471 | 1226090.5919 | 2753460.9267 | 1226091.1352
63 | 2753448.0616 | 1226085.2949 | 2753452.4593 | 1226091.1148
64 | 2753471.7078 | 1226115.5092 | 2753468.3874 | 1226111.7414
65 | 2753448.0616 | 1226085.2949 | 2753444.0446 | 1226079.9786
66 | 2753478.1276 | 1226122.7939 | 2753471.7078 | 1226115.5092
67 | 2753443.8282 | 1226079.6922 | 2753444.0446 | 1226079.9786
68 | 2753478.1276 | 1226122.7939 | 2753474.6666 | 1226131.7529
69 | 2753478.1276 | 1226122.7939 | 2753481.7188 | 1226124.5924
70 | 2753439.7144 | 1226074.2478 | 2753439.7144 | 1226074.2478 | 2753443.8282 | 1226079.6922
71 | 2753433.2684 | 1226052.762 | 2753439.4531 | 1226049.5381
72 | 2753429.6656 | 1226065.7032 | 2753431.6526 | 1226056.3013 | 2753433.2684 | 1226052.762
73 | 2753429.6656 | 1226065.7032 | 2753425.8607 | 1226063.5475 | 2753420.8573 | 1226060.2266 | 2753417.2925 | 1226056.877
74 | 2753429.6656 | 1226065.7032 | 2753436.9584 | 1226071.9044
75 | 2753436.9584 | 1226071.9044 | 2753439.7144 | 1226074.2478
76 | 2753416.9668 | 1226056.571 | 2753417.2925 | 1226056.877
77 | 2753267.6932 | 1225979.653 | 2753270.8227 | 1225980.4878 | 2753288.4031 | 1225982.5647 | 2753307.6452 | 1225988.7326 | 2753332.6748 | 1226001.6448 | 2753354.7906 | 1226016.6617 | 2753370.3307 | 1226031.0865 | 2753382.0471 | 1226038.2061 | 2753394.5488 | 1226043.3997 | 2753410.3423 | 1226050.3465 | 2753416.9668 | 1226056.571
78 | 2753551.948 | 1226213.459 | 2753540.9555 | 1226213.5755 | 2753535.9391 | 1226210.7979
79 | 2753515.7232 | 1226140.1239 | 2753529.3743 | 1226146.9045 | 2753523.4318 | 1226154.4025 | 2753517.9457 | 1226162.435 | 2753516.8352 | 1226164.9086
80 | 2753515.7232 | 1226140.1239 | 2753504.5133 | 1226135.8689
81 | 2753516.8352 | 1226164.9086 | 2753510.2752 | 1226179.4372
82 | 2753504.5133 | 1226135.8689 | 2753503.3681 | 1226135.4343 | 2753497.784 | 1226132.6377
83 | 2753452.2014 | 1226236.5203 | 2753445.4362 | 1226239.2797 | 2753434.8585 | 1226241.1334
84 | 2753546.7962 | 1226397.015 | 2753538.8025 | 1226365.805
85 | 2753494.4558 | 1226326.7838 | 2753498.2057 | 1226325.6975 | 2753509.2051 | 1226324.8757
86 | 2753487.9053 | 1226127.6906 | 2753481.7188 | 1226124.5924
87 | 2753487.9053 | 1226127.6906 | 2753488.7274 | 1226128.1022
88 | 2753488.7274 | 1226128.1022 | 2753497.4856 | 1226132.4883
89 | 2753474.6666 | 1226131.7529 | 2753474.1289 | 1226133.1447 | 2753472.6918 | 1226136.1951
90 | 2753497.4856 | 1226132.4883 | 2753497.784 | 1226132.6377
91 | 2753471.0104 | 1226139.7641 | 2753472.6918 | 1226136.1951
92 | 2753471.0104 | 1226139.7641 | 2753470.1061 | 1226141.6836
93 | 2753470.1061 | 1226141.6836 | 2753467.9585 | 1226146.242 | 2753467.9585 | 1226146.242
94 | 2753272.8213 | 1226261.3071 | 2753283.8618 | 1226257.855 | 2753294.4288 | 1226256.5112
95 | 2753466.0425 | 1226149.001 | 2753467.9585 | 1226146.242
96 | 2753494.4558 | 1226326.7838 | 2753490.5443 | 1226327.9169
97 | 2753490.5443 | 1226327.9169 | 2753488.5472 | 1226328.4954 | 2753482.6508 | 1226335.6833
98 | 2753467.3724 | 1226339.4806 | 2753482.6508 | 1226335.6833 | 2753482.6508 | 1226335.6833
99 | 2753551.4619 | 1226415.2313 | 2753546.7962 | 1226397.015
100 | 2753546.7962 | 1226397.015 | 2753580.076 | 1226392.3376
101 | 2753431.3722 | 1226348.4282 | 2753467.3724 | 1226339.4806
102 | 2753551.4619 | 1226415.2313 | 2753515.1047 | 1226424.5892
103 | 2753580.076 | 1226392.3376 | 2753586.4618 | 1226418.0569
104 | 2753665.8775 | 1226362.5586 | 2753668.6115 | 1226376.4744
105 | 2753674.0739 | 1226404.2771 | 2753668.6115 | 1226376.4744
106 | 2753665.8775 | 1226362.5586 | 2753648.1317 | 1226364.4504
107 | 2753645.7333 | 1226364.7061 | 2753648.1317 | 1226364.4504
108 | 2753645.7333 | 1226364.7061 | 2753631.5844 | 1226366.2145
109 | 2753614.2238 | 1226368.0653 | 2753631.5844 | 1226366.2145
110 | 2753608.5912 | 1226388.6974 | 2753605.5262 | 1226376.8469 | 2753606.431 | 1226370.887 | 2753610.5436 | 1226368.4576 | 2753614.2238 | 1226368.0653
111 | 2753615.0354 | 1226413.6133 | 2753608.5912 | 1226388.6974
112 | 2753462.1189 | 1226367.1937 | 2753449.5509 | 1226369.8135
113 | 2753471.2137 | 1226399.6029 | 2753468.2874 | 1226387.9496 | 2753462.1189 | 1226367.1937 | 2753462.1189 | 1226367.1937
114 | 2753437.7645 | 1226372.2704 | 2753449.5509 | 1226369.8135
115 | 2753471.2137 | 1226399.6029 | 2753471.6594 | 1226401.3778
116 | 2753437.7645 | 1226372.2704 | 2753436.5001 | 1226367.5544
117 | 2753437.7645 | 1226372.2704 | 2753435.6998 | 1226377.6332 | 2753433.9769 | 1226382.0928 | 2753422.2459 | 1226392.322 | 2753417.7334 | 1226396.3041
118 | 2753436.5001 | 1226367.5544 | 2753435.1761 | 1226362.6161
119 | 2753406.4995 | 1226406.2176 | 2753417.7334 | 1226396.3041
120 | 2753431.3722 | 1226348.4282 | 2753435.1761 | 1226362.6161
121 | 2753406.4995 | 1226406.2176 | 2753419.6844 | 1226419.3704
122 | 2753406.4995 | 1226406.2176 | 2753391.3499 | 1226392.5702 | 2753386.3019 | 1226392.1619
123 | 2753494.2067 | 1226429.9681 | 2753515.1047 | 1226424.5892
124 | 2753431.3722 | 1226348.4282 | 2753428.6934 | 1226339.0246
125 | 2753386.3019 | 1226392.1619 | 2753377.8702 | 1226398.7709
126 | 2753351.0897 | 1226284.3835 | 2753349.2377 | 1226277.0901
127 | 2753353.6269 | 1226294.3747 | 2753351.0897 | 1226284.3835
128 | 2753347.8448 | 1226271.6052 | 2753349.2377 | 1226277.0901
129 | 2753342.6937 | 1226251.3203 | 2753347.8448 | 1226271.6052
130 | 2753342.6937 | 1226251.3203 | 2753340.9371 | 1226251.4484
131 | 2753340.9371 | 1226251.4484 | 2753325.2325 | 1226252.5937 | 2753294.4288 | 1226256.5112
132 | 2753617.3032 | 1226422.3815 | 2753602.2638 | 1226426.249
133 | 2753617.3032 | 1226422.3815 | 2753615.0354 | 1226413.6133
134 | 2753589.3221 | 1226429.577 | 2753602.2638 | 1226426.249
135 | 2753589.3221 | 1226429.577 | 2753586.4618 | 1226418.0569
136 | 2753321.3034 | 1226379.0749 | 2753313.2157 | 1226369.2709
137 | 2753321.3034 | 1226379.0749 | 2753330.3137 | 1226389.7589
138 | 2753353.8151 | 1226417.6257 | 2753330.3137 | 1226389.7589
139 | 2753353.8151 | 1226417.6257 | 2753364.6642 | 1226409.122
140 | 2753364.6642 | 1226409.122 | 2753377.8702 | 1226398.7709

## bus_geodata
| x | y | coords
0 | 2753438.3492 | 1226274.0638
1 | 2753467.5306 | 1226268.5985
2 | 2753410.2663 | 1226274.3384
3 | 2753407.262 | 1226263.7958
4 | 2753420.8395 | 1226311.4544
5 | 2753403.2212 | 1226249.6231
6 | 2753421.2668 | 1226312.9543
7 | 2753391.9458 | 1226249.6507
8 | 2753407.532 | 1226249.661
9 | 2753467.1628 | 1226253.4641
10 | 2753462.346 | 1226231.7533
11 | 2753427.2707 | 1226334.0303
12 | 2753354.2415 | 1226250.4765
13 | 2753428.0538 | 1226249.8412
14 | 2753492.9791 | 1226214.6944
15 | 2753487.7144 | 1226212.1007
16 | 2753503.188 | 1226217.9051
17 | 2753503.4437 | 1226197.4263
18 | 2753429.7266 | 1226242.0328
19 | 2753538.1229 | 1226300.6488
20 | 2753527.9623 | 1226323.4742
21 | 2753541.3613 | 1226285.2167
22 | 2753459.774 | 1226233.1793
23 | 2753477.9836 | 1226221.2432
24 | 2753506.3983 | 1226230.0044
25 | 2753506.0105 | 1226256.6356
26 | 2753494.782 | 1226261.784
27 | 2753504.4554 | 1226194.6455
28 | 2753517.1644 | 1226201.5062
29 | 2753490.7432 | 1226262.9122
30 | 2753533.1362 | 1226343.6818
31 | 2753514.3123 | 1226324.4941
32 | 2753428.5988 | 1226338.6926
33 | 2753353.7626 | 1226133.0842
34 | 2753358.3988 | 1226129.8257
35 | 2753330.1025 | 1226138.4481
36 | 2753367.9288 | 1226123.3131
37 | 2753322.1371 | 1226133.8164
38 | 2753448.4181 | 1226152.999
39 | 2753407.3554 | 1226201.3855
40 | 2753363.6901 | 1226221.7191
41 | 2753419.6823 | 1226193.8585
42 | 2753453.9694 | 1226164.3089
43 | 2753436.2029 | 1226179.68
44 | 2753458.8842 | 1226159.3089
45 | 2753451.6915 | 1226166.2797
46 | 2753441.0748 | 1226175.465
47 | 2753463.5707 | 1226152.5604
48 | 2753305.9692 | 1226237.3358
49 | 2753267.5964 | 1226248.9279
50 | 2753457.4549 | 1226097.8369
51 | 2753461.3391 | 1226103.2415
52 | 2753455.8269 | 1226095.5717
53 | 2753466.2056 | 1226109.2656
54 | 2753460.9267 | 1226091.1352
55 | 2753452.4593 | 1226091.1148
56 | 2753468.3874 | 1226111.7414
57 | 2753461.5471 | 1226090.5919
58 | 2753448.0616 | 1226085.2949
59 | 2753471.7078 | 1226115.5092
60 | 2753444.0446 | 1226079.9786
61 | 2753478.1276 | 1226122.7939
62 | 2753443.8282 | 1226079.6922
63 | 2753439.4531 | 1226049.5381
64 | 2753433.2684 | 1226052.762
65 | 2753429.6656 | 1226065.7032
66 | 2753439.7144 | 1226074.2478
67 | 2753436.9584 | 1226071.9044
68 | 2753417.2925 | 1226056.877
69 | 2753416.9668 | 1226056.571
70 | 2753267.6932 | 1225979.653
71 | 2753535.9391 | 1226210.7979
72 | 2753515.7232 | 1226140.1239
73 | 2753516.8352 | 1226164.9086
74 | 2753504.5133 | 1226135.8689
75 | 2753510.2752 | 1226179.4372
76 | 2753551.948 | 1226213.459
77 | 2753434.8585 | 1226241.1334
78 | 2753538.8025 | 1226365.805
79 | 2753564.8604 | 1226339.5339
80 | 2753509.2051 | 1226324.8757
81 | 2753452.2014 | 1226236.5203
82 | 2753481.7188 | 1226124.5924
83 | 2753487.9053 | 1226127.6906
84 | 2753488.7274 | 1226128.1022
85 | 2753474.6666 | 1226131.7529
86 | 2753497.4856 | 1226132.4883
87 | 2753472.6918 | 1226136.1951
88 | 2753497.784 | 1226132.6377
89 | 2753471.0104 | 1226139.7641
90 | 2753470.1061 | 1226141.6836
91 | 2753272.8213 | 1226261.3071
92 | 2753467.9585 | 1226146.242
93 | 2753466.0425 | 1226149.001
94 | 2753494.4558 | 1226326.7838
95 | 2753490.5443 | 1226327.9169
96 | 2753482.6508 | 1226335.6833
97 | 2753546.7962 | 1226397.015
98 | 2753467.3724 | 1226339.4806
99 | 2753551.4619 | 1226415.2313
100 | 2753580.076 | 1226392.3376
101 | 2753668.6115 | 1226376.4744
102 | 2753665.8775 | 1226362.5586
103 | 2753674.0739 | 1226404.2771
104 | 2753648.1317 | 1226364.4504
105 | 2753645.7333 | 1226364.7061
106 | 2753614.2238 | 1226368.0653
107 | 2753631.5844 | 1226366.2145
108 | 2753608.5912 | 1226388.6974
109 | 2753462.1189 | 1226367.1937
110 | 2753449.5509 | 1226369.8135
111 | 2753471.2137 | 1226399.6029
112 | 2753437.7645 | 1226372.2704
113 | 2753471.6594 | 1226401.3778
114 | 2753436.5001 | 1226367.5544
115 | 2753417.7334 | 1226396.3041
116 | 2753435.1761 | 1226362.6161
117 | 2753406.4995 | 1226406.2176
118 | 2753494.2067 | 1226429.9681
119 | 2753515.1047 | 1226424.5892
120 | 2753431.3722 | 1226348.4282
121 | 2753419.6844 | 1226419.3704
122 | 2753386.3019 | 1226392.1619
123 | 2753428.6934 | 1226339.0246
124 | 2753351.0897 | 1226284.3835
125 | 2753349.2377 | 1226277.0901
126 | 2753353.6269 | 1226294.3747
127 | 2753347.8448 | 1226271.6052
128 | 2753342.6937 | 1226251.3203
129 | 2753340.9371 | 1226251.4484
130 | 2753294.4288 | 1226256.5112
131 | 2753617.3032 | 1226422.3815
132 | 2753602.2638 | 1226426.249
133 | 2753615.0354 | 1226413.6133
134 | 2753589.3221 | 1226429.577
135 | 2753586.4618 | 1226418.0569
136 | 2753313.2157 | 1226369.2709
137 | 2753321.3034 | 1226379.0749
138 | 2753330.3137 | 1226389.7589
139 | 2753353.8151 | 1226417.6257
140 | 2753364.6642 | 1226409.122
141 | 2753377.8702 | 1226398.7709
142 | 2753466.5728 | 1226248.4109

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9917 | -0.15856 | 0.022019 | 0.0055185
1 | 0.99106 | -0.17104 | 0.022954 | 0.0057527
2 | 0.99286 | -0.1362 | 0 | 0
3 | 0.99333 | -0.12714 | 0 | 0
4 | 0.99159 | -0.16045 | 0.0010064 | 0.00025224
5 | 0.99396 | -0.11498 | 0 | 0
6 | 0.99154 | -0.16143 | 0.0024343 | 0.00061008
7 | 0.99353 | -0.12327 | 0.0025444 | 0.0006377
8 | 0.99419 | -0.11064 | 0.0033772 | 0.0008464
9 | 1 | 0 | -0.46889 | -0.1192
10 | 0.99763 | -0.04503 | 0 | 0
11 | 0.99083 | -0.1749 | 0.0021338 | 0.00053479
12 | 0.99219 | -0.14936 | 0.0021726 | 0.00054449
13 | 0.99529 | -0.089671 | 0 | 0
14 | 0.99578 | -0.080376 | 0 | 0
15 | 0.99606 | -0.07514 | 0.007124 | 0.0017854
16 | 0.99567 | -0.082477 | 0 | 0
17 | 0.99488 | -0.09772 | 0 | 0
18 | 0.99571 | -0.081524 | 0.0057613 | 0.0014439
19 | 0.98356 | -0.31497 | 0 | 0
20 | 0.98364 | -0.31326 | 0 | 0
21 | 0.98351 | -0.31582 | 0.0028914 | 0.00072466
22 | 0.99746 | -0.048223 | 0.0044926 | 0.0011259
23 | 0.99671 | -0.06269 | 0.0036857 | 0.00092372
24 | 0.99555 | -0.084922 | 0.0076413 | 0.0019151
25 | 0.99546 | -0.086567 | 0 | 0
26 | 0.99542 | -0.087321 | 0 | 0
27 | 0.99476 | -0.099993 | 0.0033774 | 0.00084645
28 | 0.99465 | -0.10213 | 0 | 0
29 | 0.99541 | -0.087637 | 0.003458 | 0.00086666
30 | 0.98209 | -0.34342 | 0 | 0
31 | 0.9847 | -0.2928 | 0.0042889 | 0.0010749
32 | 0.99068 | -0.17783 | 0.001608 | 0.00040301
33 | 0.98224 | -0.34247 | 0.022591 | 0.0056618
34 | 0.98238 | -0.33984 | 0.002675 | 0.00067041
35 | 0.98217 | -0.3439 | 0 | 0
36 | 0.98268 | -0.33391 | 0.0034195 | 0.00085702
37 | 0.98214 | -0.34443 | 0.0031829 | 0.00079771
38 | 0.98581 | -0.27297 | 0.0044903 | 0.0011254
39 | 0.9858 | -0.27312 | 0 | 0
40 | 0.98571 | -0.27487 | 0.0020098 | 0.00050371
41 | 0.98583 | -0.27258 | 0.0044677 | 0.0011197
42 | 0.98628 | -0.26371 | 0 | 0
43 | 0.98596 | -0.27005 | 0.0053377 | 0.0013378
44 | 0.98665 | -0.25649 | 0.0037406 | 0.00093748
45 | 0.98622 | -0.26486 | 0.0059437 | 0.0014896
46 | 0.98603 | -0.26869 | 0.0033986 | 0.00085176
47 | 0.98712 | -0.24748 | 0.0020803 | 0.00052137
48 | 0.99138 | -0.16505 | 0.0031225 | 0.00078256
49 | 0.99149 | -0.16281 | 0 | 0
50 | 0.98817 | -0.22717 | 0.0039339 | 0.00098592
51 | 0.98837 | -0.22324 | 0.0018861 | 0.00047269
52 | 0.98809 | -0.22863 | 0 | 0
53 | 0.98862 | -0.21839 | 0.003565 | 0.00089348
54 | 0.98807 | -0.22904 | 0.0012991 | 0.00032559
55 | 0.98796 | -0.2312 | 0.002799 | 0.0007015
56 | 0.98874 | -0.21612 | 0.0043564 | 0.0010918
57 | 0.98807 | -0.22907 | 0.0021228 | 0.00053204
58 | 0.98781 | -0.23419 | 0.0015936 | 0.0003994
59 | 0.98894 | -0.21228 | 0.0052565 | 0.0013174
60 | 0.98768 | -0.23674 | 0.0017831 | 0.00044689
61 | 0.98937 | -0.20394 | 0 | 0
62 | 0.98767 | -0.23686 | 0.0021082 | 0.00052837
63 | 0.98731 | -0.24392 | 0.0037381 | 0.00093687
64 | 0.98733 | -0.24345 | 0.0024432 | 0.00061233
65 | 0.98741 | -0.24196 | 0 | 0
66 | 0.98756 | -0.239 | 0.0024946 | 0.00062521
67 | 0.98751 | -0.23997 | 0.0033402 | 0.00083714
68 | 0.98733 | -0.24346 | 0.0030891 | 0.00077421
69 | 0.98733 | -0.24348 | 0.0021161 | 0.00053035
70 | 0.98729 | -0.24431 | 0.00026932 | 6.7497e-05
71 | 0.99431 | -0.10861 | 0.0083483 | 0.0020923
72 | 0.99217 | -0.14969 | 0 | 0
73 | 0.99354 | -0.12347 | 0 | 0
74 | 0.99173 | -0.15815 | 0.0058577 | 0.0014681
75 | 0.99412 | -0.11227 | 0.011853 | 0.0029707
76 | 0.99417 | -0.11131 | 0.0091485 | 0.0022928
77 | 0.996 | -0.076081 | 0.0024022 | 0.00060205
78 | 0.98047 | -0.37491 | 0.0086611 | 0.0021707
79 | 0.98197 | -0.3457 | 0.0039516 | 0.00099035
80 | 0.98512 | -0.28477 | 0.0043764 | 0.0010968
81 | 0.997 | -0.057063 | 0.0032796 | 0.00082195
82 | 0.98984 | -0.19466 | 0.0046369 | 0.0011621
83 | 0.9907 | -0.17812 | 0.0047715 | 0.0011959
84 | 0.99082 | -0.17584 | 0.0034319 | 0.00086011
85 | 0.98864 | -0.21791 | 0.0050876 | 0.0012751
86 | 0.99146 | -0.16344 | 0.007394 | 0.0018531
87 | 0.9883 | -0.22455 | 0.0030015 | 0.00075225
88 | 0.99147 | -0.16322 | 0.0032847 | 0.00082322
89 | 0.98803 | -0.22973 | 0.0028227 | 0.00070743
90 | 0.98789 | -0.23241 | 0.0017336 | 0.00043447
91 | 0.99153 | -0.16207 | 0 | 0
92 | 0.98757 | -0.23863 | 0.0032308 | 0.00080971
93 | 0.98737 | -0.24257 | 0.0024233 | 0.00060734
94 | 0.98639 | -0.2602 | 0.0015954 | 0.00039984
95 | 0.98674 | -0.2534 | 0.0021887 | 0.00054853
96 | 0.98775 | -0.23397 | 0.0037146 | 0.00093096
97 | 0.97844 | -0.41444 | 0.0057132 | 0.0014319
98 | 0.98921 | -0.20611 | 0.0020009 | 0.00050147
99 | 0.97835 | -0.41633 | 0 | 0
100 | 0.97668 | -0.44895 | 0.007139 | 0.0017892
101 | 0.97082 | -0.56426 | 0.0040417 | 0.0010129
102 | 0.9709 | -0.56272 | 0 | 0
103 | 0.97077 | -0.56523 | 0.001842 | 0.00046166
104 | 0.971 | -0.56078 | 0.0092631 | 0.0023216
105 | 0.97103 | -0.5601 | 0.0042599 | 0.0010676
106 | 0.97167 | -0.54751 | 0.0099464 | 0.0024928
107 | 0.97129 | -0.555 | 0.0038287 | 0.00095956
108 | 0.9725 | -0.53114 | 0.0054474 | 0.0013653
109 | 0.98942 | -0.20225 | 0.0020881 | 0.00052333
110 | 0.98953 | -0.20001 | 0.0024165 | 0.00060564
111 | 0.98918 | -0.20685 | 0.004162 | 0.0010431
112 | 0.98967 | -0.1974 | 0 | 0
113 | 0.98918 | -0.20697 | 0.0035173 | 0.00088152
114 | 0.98979 | -0.19503 | 0.0022485 | 0.00056353
115 | 0.98922 | -0.20603 | 0.0021288 | 0.00053354
116 | 0.98993 | -0.19235 | 0.0030123 | 0.00075494
117 | 0.98905 | -0.2095 | 0 | 0
118 | 0.97809 | -0.42133 | 0.0031325 | 0.00078507
119 | 0.97815 | -0.4201 | 0.0023826 | 0.00059715
120 | 0.99037 | -0.18385 | 0 | 0
121 | 0.989 | -0.21043 | 0.0028078 | 0.00070371
122 | 0.98881 | -0.2141 | 0.0032528 | 0.00081524
123 | 0.99067 | -0.17804 | 0.0010517 | 0.00026359
124 | 0.9909 | -0.17428 | 0.018679 | 0.0046813
125 | 0.99106 | -0.17117 | 0.0038065 | 0.00095399
126 | 0.99086 | -0.17514 | 0.0046563 | 0.001167
127 | 0.9912 | -0.16844 | 0.0038691 | 0.00096968
128 | 0.99179 | -0.15693 | 0 | 0
129 | 0.99178 | -0.15712 | 0.0014373 | 0.00036021
130 | 0.99159 | -0.16084 | 0.0013557 | 0.00033978
131 | 0.97378 | -0.50585 | 0 | 0
132 | 0.97439 | -0.4939 | 0.0037281 | 0.00093434
133 | 0.97343 | -0.51283 | 0.0032725 | 0.00082017
134 | 0.97496 | -0.48271 | 0 | 0
135 | 0.97546 | -0.47278 | 0.0035225 | 0.00088282
136 | 0.98846 | -0.221 | 0.0022066 | 0.00055303
137 | 0.98848 | -0.2205 | 0 | 0
138 | 0.98851 | -0.21995 | 0.0012037 | 0.00030168
139 | 0.98862 | -0.21774 | 0 | 0
140 | 0.98867 | -0.2169 | 0.0015119 | 0.00037891
141 | 0.98874 | -0.21542 | 0.0019815 | 0.00049661
142 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.022967 | 0.0057611 | -0.022954 | -0.0057527 | 1.3652e-05 | 8.3423e-06 | 0.034464 | 0.034464 | 0.034464 | 0.9917 | -0.15856 | 0.99106 | -0.17104 | 9.4681
1 | -0.044986 | -0.01128 | 0.045034 | 0.01131 | 4.7988e-05 | 3.035e-05 | 0.067503 | 0.067502 | 0.067503 | 0.9917 | -0.15856 | 0.99286 | -0.1362 | 18.5446
2 | -0.18862 | -0.047912 | 0.1887 | 0.047965 | 8.225e-05 | 5.2073e-05 | 0.28292 | 0.28292 | 0.28292 | 0.99286 | -0.1362 | 0.99333 | -0.12714 | 19.4311
3 | 0.14359 | 0.036603 | -0.14342 | -0.036497 | 0.00016789 | 0.00010546 | 0.21541 | 0.21542 | 0.21542 | 0.99286 | -0.1362 | 0.99159 | -0.16045 | 14.795
4 | -0.1887 | -0.047965 | 0.18881 | 0.048035 | 0.00011059 | 7.0013e-05 | 0.28292 | 0.28292 | 0.28292 | 0.99333 | -0.12714 | 0.99396 | -0.11498 | 19.4311
5 | 0.14241 | 0.036245 | -0.1424 | -0.036241 | 6.6896e-06 | 4.2009e-06 | 0.2139 | 0.2139 | 0.2139 | 0.99159 | -0.16045 | 0.99154 | -0.16143 | 14.6913
6 | 0.041747 | 0.0105 | -0.041731 | -0.01049 | 1.6523e-05 | 1.0428e-05 | 0.062511 | 0.062511 | 0.062511 | 0.99396 | -0.11498 | 0.99353 | -0.12327 | 17.1734
7 | -0.23056 | -0.058535 | 0.23061 | 0.058566 | 4.8223e-05 | 3.0639e-05 | 0.34543 | 0.34543 | 0.34543 | 0.99396 | -0.11498 | 0.99419 | -0.11064 | 23.7244
8 | 0.13997 | 0.035631 | -0.13988 | -0.035574 | 9.082e-05 | 5.6995e-05 | 0.21025 | 0.21025 | 0.21025 | 0.99154 | -0.16143 | 0.99083 | -0.1749 | 14.4404
9 | 0.039186 | 0.0098524 | -0.039137 | -0.0098216 | 4.8756e-05 | 3.0716e-05 | 0.0587 | 0.0587 | 0.0587 | 0.99353 | -0.12327 | 0.99219 | -0.14936 | 16.1265
10 | -0.23399 | -0.059412 | 0.23422 | 0.059562 | 0.00023634 | 0.00015019 | 0.35048 | 0.35048 | 0.35048 | 0.99419 | -0.11064 | 0.99529 | -0.089671 | 24.0715
11 | 0.46724 | 0.1192 | -0.46622 | -0.11855 | 0.0010138 | 0.00064764 | 0.696 | 0.696 | 0.696 | 1 | 0 | 0.99763 | -0.04503 | 47.802
12 | 0.25068 | 0.063887 | -0.25064 | -0.063863 | 3.8621e-05 | 2.4564e-05 | 0.37428 | 0.37428 | 0.37428 | 0.99763 | -0.04503 | 0.99746 | -0.048223 | 25.7057
13 | 0.21554 | 0.054664 | -0.21536 | -0.054548 | 0.00018283 | 0.00011603 | 0.32172 | 0.32172 | 0.32172 | 0.99763 | -0.04503 | 0.99671 | -0.06269 | 22.0963
14 | 0.13775 | 0.035039 | -0.13773 | -0.035027 | 1.9483e-05 | 1.2219e-05 | 0.20705 | 0.20705 | 0.20705 | 0.99083 | -0.1749 | 0.99068 | -0.17783 | 14.2203
15 | 0.036965 | 0.0092771 | -0.036952 | -0.0092688 | 1.3347e-05 | 8.3923e-06 | 0.055442 | 0.055442 | 0.055442 | 0.99219 | -0.14936 | 0.99179 | -0.15693 | 15.2314
16 | -0.23422 | -0.059562 | 0.23431 | 0.059621 | 9.1962e-05 | 5.8441e-05 | 0.35048 | 0.35048 | 0.35048 | 0.99529 | -0.089671 | 0.99571 | -0.081524 | 24.0715
17 | -0.20437 | -0.051726 | 0.20442 | 0.051759 | 5.1378e-05 | 3.2577e-05 | 0.30558 | 0.30558 | 0.30558 | 0.99578 | -0.080376 | 0.99606 | -0.07514 | 20.9875
18 | 0.011102 | 0.0027827 | -0.011101 | -0.0027821 | 1.1116e-06 | 5.7132e-07 | 0.01659 | 0.01659 | 0.01659 | 0.99578 | -0.080376 | 0.99567 | -0.082477 | 4.5578
19 | 0.19327 | 0.048944 | -0.19311 | -0.048842 | 0.00016083 | 0.00010186 | 0.28899 | 0.28899 | 0.28899 | 0.99578 | -0.080376 | 0.99488 | -0.09772 | 19.8481
20 | -0.21155 | -0.053544 | 0.21168 | 0.053625 | 0.0001265 | 8.0259e-05 | 0.31622 | 0.31622 | 0.31622 | 0.99606 | -0.07514 | 0.99671 | -0.06269 | 21.7184
21 | 0.011101 | 0.0027821 | -0.0111 | -0.0027815 | 1.2925e-06 | 6.6437e-07 | 0.01659 | 0.01659 | 0.01659 | 0.99567 | -0.082477 | 0.99555 | -0.084922 | 4.5578
22 | 0.1756 | 0.044451 | -0.17558 | -0.044439 | 1.916e-05 | 1.2109e-05 | 0.2628 | 0.2628 | 0.2628 | 0.99488 | -0.09772 | 0.99476 | -0.099993 | 18.0496
23 | 0.017507 | 0.004391 | -0.017503 | -0.0043888 | 3.6809e-06 | 2.1699e-06 | 0.026186 | 0.026186 | 0.026186 | 0.99488 | -0.09772 | 0.99465 | -0.10213 | 7.194
24 | -0.24007 | -0.061065 | 0.24014 | 0.061105 | 6.2984e-05 | 4.0038e-05 | 0.35909 | 0.35909 | 0.35909 | 0.99571 | -0.081524 | 0.996 | -0.076081 | 24.6628
25 | -0.0028915 | -0.00072452 | 0.0028918 | 0.00072426 | 2.3673e-07 | -2.6721e-07 | 0.0043745 | 0.0043744 | 0.0043745 | 0.98356 | -0.31497 | 0.98364 | -0.31326 | 1.2018
26 | 0.0028915 | 0.00072452 | -0.0028914 | -0.00072466 | 1.1699e-07 | -1.3202e-07 | 0.0043745 | 0.0043746 | 0.0043746 | 0.98356 | -0.31497 | 0.98351 | -0.31582 | 1.2018
27 | 0.080804 | 0.020508 | -0.080687 | -0.020433 | 0.00011705 | 7.4646e-05 | 0.12233 | 0.12233 | 0.12233 | 0.98364 | -0.31326 | 0.98209 | -0.34342 | 33.6069
28 | -0.083696 | -0.021232 | 0.083778 | 0.021284 | 8.2404e-05 | 5.2565e-05 | 0.1267 | 0.1267 | 0.1267 | 0.98364 | -0.31326 | 0.9847 | -0.2928 | 34.8087
29 | 0.24615 | 0.062737 | -0.24604 | -0.06267 | 0.00010497 | 6.6751e-05 | 0.36757 | 0.36757 | 0.36757 | 0.99746 | -0.048223 | 0.997 | -0.057063 | 25.2455
30 | 0.0034584 | 0.00086636 | -0.0034582 | -0.00086654 | 2.7096e-07 | -1.7817e-07 | 0.0051691 | 0.0051692 | 0.0051692 | 0.99555 | -0.084922 | 0.99546 | -0.086567 | 1.4201
31 | 0.0034582 | 0.00086654 | -0.0034581 | -0.00086662 | 1.2428e-07 | -8.1692e-08 | 0.0051692 | 0.0051693 | 0.0051693 | 0.99546 | -0.086567 | 0.99542 | -0.087321 | 1.4201
32 | 0.0034581 | 0.00086662 | -0.003458 | -0.00086666 | 5.206e-08 | -3.4217e-08 | 0.0051693 | 0.0051693 | 0.0051693 | 0.99542 | -0.087321 | 0.99541 | -0.087637 | 1.4201
33 | 0.17221 | 0.043592 | -0.17211 | -0.043528 | 0.00010147 | 6.4095e-05 | 0.25775 | 0.25775 | 0.25775 | 0.99476 | -0.099993 | 0.99412 | -0.11227 | 17.7026
34 | 0.017503 | 0.0043888 | -0.017498 | -0.0043856 | 5.4015e-06 | 3.1844e-06 | 0.026186 | 0.026186 | 0.026186 | 0.99465 | -0.10213 | 0.99431 | -0.10861 | 7.194
35 | 0.076735 | 0.019443 | -0.076619 | -0.019369 | 0.00011592 | 7.3898e-05 | 0.11634 | 0.11634 | 0.11634 | 0.98209 | -0.34342 | 0.98047 | -0.37491 | 31.962
36 | 0.003952 | 0.00099023 | -0.0039516 | -0.00099035 | 4.3018e-07 | -1.2948e-07 | 0.0059878 | 0.0059879 | 0.0059879 | 0.98209 | -0.34342 | 0.98197 | -0.3457 | 1.645
37 | -0.088067 | -0.022359 | 0.088101 | 0.022381 | 3.4067e-05 | 2.1738e-05 | 0.13318 | 0.13318 | 0.13318 | 0.9847 | -0.2928 | 0.98512 | -0.28477 | 36.5892
38 | 0.13612 | 0.034624 | -0.13612 | -0.034623 | 1.355e-06 | 8.494e-07 | 0.20463 | 0.20463 | 0.20463 | 0.99068 | -0.17783 | 0.99067 | -0.17804 | 14.0544
39 | -0.025774 | -0.0064593 | 0.025777 | 0.0064613 | 3.2397e-06 | 2.0017e-06 | 0.039045 | 0.039045 | 0.039045 | 0.98224 | -0.34247 | 0.98238 | -0.33984 | 10.7268
40 | 0.0031832 | 0.00079747 | -0.003183 | -0.00079765 | 2.1613e-07 | -1.7537e-07 | 0.0048222 | 0.0048223 | 0.0048223 | 0.98224 | -0.34247 | 0.98217 | -0.3439 | 1.3248
41 | -0.028452 | -0.0071317 | 0.02846 | 0.0071367 | 8.0402e-06 | 4.9996e-06 | 0.043097 | 0.043097 | 0.043097 | 0.98238 | -0.33984 | 0.98268 | -0.33391 | 11.8399
42 | 0.003183 | 0.00079765 | -0.0031829 | -0.00079771 | 8.0352e-08 | -6.5182e-08 | 0.0048223 | 0.0048223 | 0.0048223 | 0.98217 | -0.3439 | 0.98214 | -0.34443 | 1.3248
43 | -0.03188 | -0.0079937 | 0.031973 | 0.0080518 | 9.287e-05 | 5.8086e-05 | 0.048275 | 0.048275 | 0.048275 | 0.98268 | -0.33391 | 0.98581 | -0.27297 | 13.2624
44 | -0.036463 | -0.0091771 | 0.036479 | 0.0091873 | 1.6136e-05 | 1.0146e-05 | 0.055052 | 0.055052 | 0.055052 | 0.98581 | -0.27297 | 0.98628 | -0.26371 | 15.1243
45 | 0.00201 | 0.00050319 | -0.0020098 | -0.00050371 | 1.683e-07 | -5.1388e-07 | 0.0030338 | 0.003034 | 0.003034 | 0.9858 | -0.27312 | 0.98571 | -0.27487 | 0.83351
46 | -0.00201 | -0.00050319 | 0.00201 | 0.00050304 | 5.1158e-08 | -1.5624e-07 | 0.0030338 | 0.0030337 | 0.0030338 | 0.9858 | -0.27312 | 0.98583 | -0.27258 | 0.83345
47 | -0.0064778 | -0.0016228 | 0.0064785 | 0.001623 | 7.8044e-07 | 2.2187e-07 | 0.0097773 | 0.0097772 | 0.0097773 | 0.98583 | -0.27258 | 0.98596 | -0.27005 | 2.6861
48 | -0.057642 | -0.014492 | 0.057662 | 0.014505 | 1.9892e-05 | 1.2641e-05 | 0.086982 | 0.086982 | 0.086982 | 0.98628 | -0.26371 | 0.98665 | -0.25649 | 23.8961
49 | 0.021163 | 0.0053048 | -0.021162 | -0.0053041 | 1.1516e-06 | 6.9857e-07 | 0.03193 | 0.03193 | 0.03193 | 0.98628 | -0.26371 | 0.98622 | -0.26486 | 8.7718
50 | -0.011816 | -0.0029607 | 0.011817 | 0.0029611 | 7.6826e-07 | 4.0952e-07 | 0.017833 | 0.017833 | 0.017833 | 0.98596 | -0.27005 | 0.98603 | -0.26869 | 4.8992
51 | -0.061403 | -0.015442 | 0.061429 | 0.015459 | 2.6433e-05 | 1.6812e-05 | 0.092623 | 0.092623 | 0.092623 | 0.98665 | -0.25649 | 0.98712 | -0.24748 | 25.4459
52 | 0.015218 | 0.0038145 | -0.015216 | -0.0038129 | 2.7757e-06 | 1.5973e-06 | 0.022962 | 0.022962 | 0.022962 | 0.98622 | -0.26486 | 0.98603 | -0.26869 | 6.3082
53 | -0.063509 | -0.01598 | 0.063524 | 0.01599 | 1.4901e-05 | 9.4813e-06 | 0.095759 | 0.095759 | 0.095759 | 0.98712 | -0.24748 | 0.98737 | -0.24257 | 26.3074
54 | -0.0031225 | -0.00078256 | 0.0031228 | 0.00078226 | 3.3268e-07 | -3.0794e-07 | 0.0046867 | 0.0046865 | 0.0046867 | 0.99138 | -0.16505 | 0.99149 | -0.16281 | 1.2876
55 | -0.0031228 | -0.00078226 | 0.0031229 | 0.00078215 | 1.1063e-07 | -1.0244e-07 | 0.0046865 | 0.0046865 | 0.0046865 | 0.99149 | -0.16281 | 0.99153 | -0.16207 | 1.2875
56 | -0.033146 | -0.0083101 | 0.033153 | 0.008314 | 6.2181e-06 | 3.8943e-06 | 0.049914 | 0.049914 | 0.049914 | 0.98817 | -0.22717 | 0.98837 | -0.22324 | 13.7126
57 | 0.029212 | 0.0073242 | -0.02921 | -0.0073229 | 2.0243e-06 | 1.2598e-06 | 0.04399 | 0.04399 | 0.04399 | 0.98817 | -0.22717 | 0.98809 | -0.22863 | 12.0852
58 | -0.035039 | -0.0087867 | 0.035047 | 0.0087918 | 8.0916e-06 | 5.0792e-06 | 0.052753 | 0.052753 | 0.052753 | 0.98837 | -0.22324 | 0.98862 | -0.21839 | 14.4927
59 | 0.003422 | 0.00085757 | -0.003422 | -0.00085761 | 6.7318e-08 | -4.3496e-08 | 0.0051533 | 0.0051534 | 0.0051534 | 0.98809 | -0.22863 | 0.98807 | -0.22904 | 1.4158
60 | 0.025788 | 0.0064654 | -0.025785 | -0.0064634 | 3.1596e-06 | 1.9506e-06 | 0.038837 | 0.038837 | 0.038837 | 0.98809 | -0.22863 | 0.98796 | -0.2312 | 10.6694
61 | -0.038612 | -0.0096852 | 0.038616 | 0.0096879 | 4.1801e-06 | 2.6329e-06 | 0.058119 | 0.058119 | 0.058119 | 0.98862 | -0.21839 | 0.98874 | -0.21612 | 15.9668
62 | 0.0021228 | 0.00053203 | -0.0021228 | -0.00053204 | 3.1608e-09 | -8.5401e-09 | 0.003197 | 0.003197 | 0.003197 | 0.98807 | -0.22904 | 0.98807 | -0.22907 | 0.87829
63 | 0.022986 | 0.0057619 | -0.022983 | -0.0057599 | 3.2788e-06 | 2.005e-06 | 0.034621 | 0.034621 | 0.034621 | 0.98796 | -0.2312 | 0.98781 | -0.23419 | 9.5113
64 | -0.042972 | -0.01078 | 0.04298 | 0.010785 | 7.8775e-06 | 4.9772e-06 | 0.064675 | 0.064675 | 0.064675 | 0.98874 | -0.21612 | 0.98894 | -0.21228 | 17.768
65 | 0.021389 | 0.0053605 | -0.021387 | -0.0053589 | 2.5941e-06 | 1.5749e-06 | 0.03222 | 0.03222 | 0.03222 | 0.98781 | -0.23419 | 0.98768 | -0.23674 | 8.8518
66 | -0.048237 | -0.012102 | 0.048256 | 0.012114 | 1.9184e-05 | 1.2153e-05 | 0.072585 | 0.072585 | 0.072585 | 0.98894 | -0.21228 | 0.98937 | -0.20394 | 19.9409
67 | 0.019604 | 0.004912 | -0.019604 | -0.004912 | 1.1742e-07 | 7.0555e-08 | 0.029534 | 0.029534 | 0.029534 | 0.98768 | -0.23674 | 0.98767 | -0.23686 | 8.1138
68 | 0.081963 | 0.020665 | -0.081909 | -0.02063 | 5.477e-05 | 3.493e-05 | 0.12332 | 0.12332 | 0.12332 | 0.98937 | -0.20394 | 0.98864 | -0.21791 | 33.8785
69 | -0.13022 | -0.032779 | 0.13028 | 0.032816 | 5.7802e-05 | 3.6941e-05 | 0.1959 | 0.1959 | 0.1959 | 0.98937 | -0.20394 | 0.98984 | -0.19466 | 53.8193
70 | 0.017495 | 0.0043836 | -0.017494 | -0.0043825 | 1.7778e-06 | 1.0505e-06 | 0.026358 | 0.026358 | 0.026358 | 0.98767 | -0.23686 | 0.98756 | -0.239 | 7.2412
71 | -0.0037381 | -0.00093687 | 0.0037382 | 0.00093683 | 8.3016e-08 | -3.6065e-08 | 0.0056339 | 0.0056339 | 0.0056339 | 0.98731 | -0.24392 | 0.98733 | -0.24345 | 1.5478
72 | -0.0061814 | -0.0015492 | 0.0061819 | 0.0015493 | 4.3937e-07 | 1.0853e-07 | 0.0093161 | 0.009316 | 0.0093161 | 0.98733 | -0.24345 | 0.98741 | -0.24196 | 2.5594
73 | 0.005475 | 0.0013699 | -0.0054746 | -0.0013699 | 3.8974e-07 | 5.4132e-08 | 0.00825 | 0.00825 | 0.00825 | 0.98741 | -0.24196 | 0.98733 | -0.24346 | 2.2665
74 | -0.011657 | -0.0029192 | 0.011658 | 0.0029198 | 1.1077e-06 | 5.8646e-07 | 0.017566 | 0.017566 | 0.017566 | 0.98741 | -0.24196 | 0.98751 | -0.23997 | 4.8258
75 | 0.014999 | 0.0037573 | -0.014998 | -0.0037569 | 6.9284e-07 | 3.9713e-07 | 0.022599 | 0.022599 | 0.022599 | 0.98756 | -0.239 | 0.98751 | -0.23997 | 6.2086
76 | 0.0023855 | 0.00059567 | -0.0023855 | -0.00059567 | 2.1648e-09 | -4.329e-09 | 0.0035944 | 0.0035944 | 0.0035944 | 0.98733 | -0.24346 | 0.98733 | -0.24348 | 0.98747
77 | 0.00026933 | 6.5319e-05 | -0.00026932 | -6.7497e-05 | 1.0535e-08 | -2.178e-06 | 0.00040514 | 0.0004059 | 0.0004059 | 0.98733 | -0.24348 | 0.98729 | -0.24431 | 0.11151
78 | 0.0091496 | 0.0022934 | -0.0091485 | -0.0022928 | 1.1761e-06 | 5.3576e-07 | 0.013693 | 0.013693 | 0.013693 | 0.99431 | -0.10861 | 0.99417 | -0.11131 | 3.7618
79 | -0.15996 | -0.040376 | 0.16017 | 0.040503 | 0.00020116 | 0.00012681 | 0.24001 | 0.24001 | 0.24001 | 0.99217 | -0.14969 | 0.99354 | -0.12347 | 16.4841
80 | 0.15996 | 0.040376 | -0.1599 | -0.040336 | 6.4752e-05 | 4.0822e-05 | 0.24001 | 0.24001 | 0.24001 | 0.99217 | -0.14969 | 0.99173 | -0.15815 | 16.4842
81 | -0.16017 | -0.040503 | 0.16025 | 0.040557 | 8.6087e-05 | 5.4269e-05 | 0.24001 | 0.24001 | 0.24001 | 0.99354 | -0.12347 | 0.99412 | -0.11227 | 16.4841
82 | 0.15404 | 0.038867 | -0.154 | -0.038844 | 3.7441e-05 | 2.3577e-05 | 0.23122 | 0.23122 | 0.23122 | 0.99173 | -0.15815 | 0.99147 | -0.16322 | 15.8805
83 | -0.24254 | -0.061707 | 0.24276 | 0.061848 | 0.00022252 | 0.00014148 | 0.36268 | 0.36268 | 0.36268 | 0.996 | -0.076081 | 0.997 | -0.057063 | 24.9093
84 | 0.067958 | 0.017198 | -0.06783 | -0.017116 | 0.00012866 | 8.194e-05 | 0.1032 | 0.1032 | 0.1032 | 0.98047 | -0.37491 | 0.97844 | -0.41444 | 28.3509
85 | -0.092478 | -0.023478 | 0.092587 | 0.023548 | 0.00010944 | 6.9854e-05 | 0.13979 | 0.13979 | 0.13979 | 0.98512 | -0.28477 | 0.98639 | -0.2602 | 38.4052
86 | -0.13491 | -0.033978 | 0.13502 | 0.034047 | 0.00010679 | 6.8255e-05 | 0.20287 | 0.20287 | 0.20287 | 0.98984 | -0.19466 | 0.9907 | -0.17812 | 55.7343
87 | -0.13979 | -0.035243 | 0.13981 | 0.035252 | 1.5209e-05 | 9.722e-06 | 0.21004 | 0.21004 | 0.21004 | 0.9907 | -0.17812 | 0.99082 | -0.17584 | 57.7032
88 | -0.14324 | -0.036112 | 0.14332 | 0.036167 | 8.505e-05 | 5.4179e-05 | 0.21519 | 0.21519 | 0.21519 | 0.99082 | -0.17584 | 0.99146 | -0.16344 | 29.5596
89 | 0.076821 | 0.019355 | -0.076797 | -0.01934 | 2.44e-05 | 1.5554e-05 | 0.11566 | 0.11566 | 0.11566 | 0.98864 | -0.21791 | 0.9883 | -0.22455 | 31.7748
90 | -0.15072 | -0.03802 | 0.15072 | 0.038021 | 1.6017e-06 | 1.0079e-06 | 0.22629 | 0.22629 | 0.22629 | 0.99146 | -0.16344 | 0.99147 | -0.16322 | 15.5419
91 | 0.073795 | 0.018587 | -0.073777 | -0.018576 | 1.8275e-05 | 1.1645e-05 | 0.11114 | 0.11114 | 0.11114 | 0.9883 | -0.22455 | 0.98803 | -0.22973 | 30.5333
92 | 0.070954 | 0.017868 | -0.070945 | -0.017862 | 9.0911e-06 | 5.7912e-06 | 0.10689 | 0.10689 | 0.10689 | 0.98803 | -0.22973 | 0.98789 | -0.23241 | 29.3654
93 | 0.069211 | 0.017428 | -0.069191 | -0.017415 | 2.0548e-05 | 1.3086e-05 | 0.10428 | 0.10428 | 0.10428 | 0.98789 | -0.23241 | 0.98757 | -0.23863 | 28.6481
94 | -0.0031229 | -0.00078215 | 0.0031231 | 0.00078198 | 1.83e-07 | -1.6949e-07 | 0.0046865 | 0.0046864 | 0.0046865 | 0.99153 | -0.16207 | 0.99159 | -0.16084 | 1.2875
95 | 0.06596 | 0.016605 | -0.065948 | -0.016597 | 1.2449e-05 | 7.9241e-06 | 0.099411 | 0.099411 | 0.099411 | 0.98757 | -0.23863 | 0.98737 | -0.24257 | 27.3107
96 | -0.094183 | -0.023948 | 0.094213 | 0.023967 | 3.0881e-05 | 1.9712e-05 | 0.1422 | 0.1422 | 0.1422 | 0.98639 | -0.2602 | 0.98674 | -0.2534 | 39.0664
97 | -0.096402 | -0.024516 | 0.096492 | 0.024573 | 9.0316e-05 | 5.7657e-05 | 0.1455 | 0.1455 | 0.1455 | 0.98674 | -0.2534 | 0.98775 | -0.23397 | 39.9731
98 | -0.10021 | -0.025504 | 0.10034 | 0.02559 | 0.00013479 | 8.6061e-05 | 0.1511 | 0.1511 | 0.1511 | 0.98775 | -0.23397 | 0.98921 | -0.20611 | 41.5104
99 | 0.0055168 | 0.0013823 | -0.0055163 | -0.0013822 | 4.9636e-07 | 8.1518e-08 | 0.0083898 | 0.0083899 | 0.0083899 | 0.97844 | -0.41444 | 0.97835 | -0.41633 | 2.3049
100 | 0.056599 | 0.014302 | -0.056506 | -0.014243 | 9.3466e-05 | 5.9397e-05 | 0.086119 | 0.086119 | 0.086119 | 0.97844 | -0.41444 | 0.97668 | -0.44895 | 23.659
101 | -0.10234 | -0.026092 | 0.10245 | 0.026161 | 0.00011012 | 6.9048e-05 | 0.15411 | 0.15411 | 0.15411 | 0.98921 | -0.20611 | 0.99037 | -0.18385 | 14.1124
102 | 0.0055163 | 0.0013822 | -0.0055153 | -0.0013821 | 9.91e-07 | 1.6291e-07 | 0.0083899 | 0.0083901 | 0.0083901 | 0.97835 | -0.41633 | 0.97815 | -0.4201 | 2.305
103 | 0.049367 | 0.012453 | -0.049311 | -0.012418 | 5.6261e-05 | 3.5676e-05 | 0.075242 | 0.075242 | 0.075242 | 0.97668 | -0.44895 | 0.97546 | -0.47278 | 20.671
104 | -0.0058838 | -0.0014743 | 0.0058843 | 0.0014744 | 4.3252e-07 | 1.0144e-07 | 0.0090182 | 0.0090182 | 0.0090182 | 0.97082 | -0.56426 | 0.9709 | -0.56272 | 2.4775
105 | 0.0018421 | 0.00046136 | -0.001842 | -0.00046166 | 8.4704e-08 | -2.9612e-07 | 0.0028234 | 0.0028235 | 0.0028235 | 0.97082 | -0.56426 | 0.97077 | -0.56523 | 0.77569
106 | -0.0058843 | -0.0014744 | 0.0058848 | 0.0014745 | 5.4427e-07 | 1.2761e-07 | 0.0090182 | 0.0090181 | 0.0090182 | 0.9709 | -0.56272 | 0.971 | -0.56078 | 2.4775
107 | -0.015148 | -0.0037961 | 0.015148 | 0.0037964 | 4.8741e-07 | 2.8211e-07 | 0.023213 | 0.023213 | 0.023213 | 0.971 | -0.56078 | 0.97103 | -0.5601 | 6.3773
108 | -0.019408 | -0.004864 | 0.019413 | 0.0048669 | 4.7199e-06 | 2.8447e-06 | 0.029741 | 0.029741 | 0.029741 | 0.97103 | -0.5601 | 0.97129 | -0.555 | 8.1707
109 | 0.02325 | 0.0058315 | -0.023242 | -0.0058264 | 8.3007e-06 | 5.0963e-06 | 0.035607 | 0.035607 | 0.035607 | 0.97167 | -0.54751 | 0.97129 | -0.555 | 9.7821
110 | -0.033196 | -0.0083243 | 0.033222 | 0.0083406 | 2.5923e-05 | 1.6259e-05 | 0.050839 | 0.050839 | 0.050839 | 0.97167 | -0.54751 | 0.9725 | -0.53114 | 13.9667
111 | -0.03867 | -0.0097058 | 0.038704 | 0.0097271 | 3.3793e-05 | 2.1308e-05 | 0.059174 | 0.059174 | 0.059174 | 0.9725 | -0.53114 | 0.97343 | -0.51283 | 16.2565
112 | -0.009769 | -0.0024486 | 0.0097701 | 0.0024491 | 1.0392e-06 | 5.0018e-07 | 0.014692 | 0.014692 | 0.014692 | 0.98942 | -0.20225 | 0.98953 | -0.20001 | 4.0363
113 | 0.0076809 | 0.0019252 | -0.0076793 | -0.0019246 | 1.6848e-06 | 6.4596e-07 | 0.011552 | 0.011552 | 0.011552 | 0.98942 | -0.20225 | 0.98918 | -0.20685 | 3.1736
114 | -0.012187 | -0.0030547 | 0.012188 | 0.0030555 | 1.5163e-06 | 8.1573e-07 | 0.018326 | 0.018326 | 0.018326 | 0.98953 | -0.20001 | 0.98967 | -0.1974 | 5.0346
115 | 0.0035173 | 0.00088151 | -0.0035173 | -0.00088152 | 1.9212e-08 | -1.1196e-08 | 0.005291 | 0.0052911 | 0.0052911 | 0.98918 | -0.20685 | 0.98918 | -0.20697 | 1.4536
116 | -0.027293 | -0.0068435 | 0.027297 | 0.0068454 | 3.0836e-06 | 1.9107e-06 | 0.041038 | 0.041038 | 0.041038 | 0.98967 | -0.1974 | 0.98979 | -0.19503 | 11.2742
117 | 0.015105 | 0.0037879 | -0.015099 | -0.0037844 | 6.2115e-06 | 3.563e-06 | 0.022712 | 0.022712 | 0.022712 | 0.98967 | -0.1974 | 0.98922 | -0.20603 | 6.2397
118 | -0.029545 | -0.0074089 | 0.029549 | 0.0074113 | 3.7827e-06 | 2.3552e-06 | 0.044418 | 0.044418 | 0.044418 | 0.98979 | -0.19503 | 0.98993 | -0.19235 | 12.2029
119 | 0.01297 | 0.0032508 | -0.012968 | -0.0032497 | 2.1387e-06 | 1.1764e-06 | 0.01951 | 0.01951 | 0.01951 | 0.98922 | -0.20603 | 0.98905 | -0.2095 | 5.36
120 | -0.032561 | -0.0081662 | 0.032574 | 0.0081745 | 1.3197e-05 | 8.2569e-06 | 0.048946 | 0.048946 | 0.048946 | 0.98993 | -0.19235 | 0.99037 | -0.18385 | 13.4468
121 | 0.002808 | 0.00070355 | -0.0028078 | -0.00070371 | 1.2464e-07 | -1.5922e-07 | 0.0042245 | 0.0042246 | 0.0042246 | 0.98905 | -0.2095 | 0.989 | -0.21043 | 1.1606
122 | 0.01016 | 0.0025461 | -0.010158 | -0.002545 | 2.2304e-06 | 1.1008e-06 | 0.015286 | 0.015286 | 0.015286 | 0.98905 | -0.2095 | 0.98881 | -0.2141 | 4.1994
123 | -0.0031325 | -0.00078507 | 0.0031327 | 0.00078492 | 1.8378e-07 | -1.5323e-07 | 0.0047656 | 0.0047655 | 0.0047656 | 0.97809 | -0.42133 | 0.97815 | -0.4201 | 1.3092
124 | -0.13503 | -0.034335 | 0.13506 | 0.034359 | 3.7794e-05 | 2.3685e-05 | 0.20305 | 0.20305 | 0.20305 | 0.99037 | -0.18385 | 0.99067 | -0.17804 | 13.9459
125 | 0.0069051 | 0.0017298 | -0.0069046 | -0.0017296 | 4.3376e-07 | 1.402e-07 | 0.010391 | 0.010391 | 0.010391 | 0.98881 | -0.2141 | 0.98874 | -0.21542 | 2.8546
126 | -0.023335 | -0.0058483 | 0.023339 | 0.0058504 | 3.465e-06 | 2.1207e-06 | 0.035042 | 0.035042 | 0.035042 | 0.9909 | -0.17428 | 0.99106 | -0.17117 | 9.6269
127 | 0.0046565 | 0.001167 | -0.0046563 | -0.001167 | 1.8901e-07 | -1.1814e-08 | 0.0069925 | 0.0069926 | 0.0069926 | 0.9909 | -0.17428 | 0.99086 | -0.17514 | 1.921
128 | -0.027145 | -0.0068044 | 0.027149 | 0.0068066 | 3.5251e-06 | 2.1832e-06 | 0.040757 | 0.040757 | 0.040757 | 0.99106 | -0.17117 | 0.9912 | -0.16844 | 11.197
129 | -0.031018 | -0.0077762 | 0.031035 | 0.0077869 | 1.7018e-05 | 1.0621e-05 | 0.046565 | 0.046565 | 0.046565 | 0.9912 | -0.16844 | 0.99179 | -0.15693 | 12.7927
130 | 0.0059169 | 0.0014819 | -0.0059169 | -0.0014819 | 5.2046e-08 | 1.0581e-08 | 0.008877 | 0.008877 | 0.008877 | 0.99179 | -0.15693 | 0.99178 | -0.15712 | 2.4387
131 | 0.0044796 | 0.0011217 | -0.0044788 | -0.0011218 | 7.9267e-07 | -9.6489e-08 | 0.0067206 | 0.0067208 | 0.0067208 | 0.99178 | -0.15712 | 0.99159 | -0.16084 | 1.8464
132 | -0.04199 | -0.010556 | 0.042014 | 0.010571 | 2.3983e-05 | 1.5156e-05 | 0.064176 | 0.064176 | 0.064176 | 0.97378 | -0.50585 | 0.97439 | -0.4939 | 17.6308
133 | 0.04199 | 0.010556 | -0.041976 | -0.010547 | 1.3988e-05 | 8.8396e-06 | 0.064176 | 0.064176 | 0.064176 | 0.97378 | -0.50585 | 0.97343 | -0.51283 | 17.6308
134 | -0.045742 | -0.011506 | 0.045767 | 0.011521 | 2.4462e-05 | 1.5489e-05 | 0.069869 | 0.069869 | 0.069869 | 0.97439 | -0.4939 | 0.97496 | -0.48271 | 19.1948
135 | -0.045767 | -0.011521 | 0.045788 | 0.011535 | 2.1729e-05 | 1.3759e-05 | 0.069869 | 0.069869 | 0.069869 | 0.97496 | -0.48271 | 0.97546 | -0.47278 | 19.1948
136 | -0.0022066 | -0.00055303 | 0.0022067 | 0.0005529 | 5.2589e-08 | -1.2926e-07 | 0.0033218 | 0.0033217 | 0.0033218 | 0.98846 | -0.221 | 0.98848 | -0.2205 | 0.91258
137 | -0.0022067 | -0.0005529 | 0.0022067 | 0.00055275 | 5.7829e-08 | -1.4215e-07 | 0.0033217 | 0.0033217 | 0.0033217 | 0.98848 | -0.2205 | 0.98851 | -0.21995 | 0.91257
138 | -0.0034104 | -0.00085443 | 0.0034108 | 0.0008542 | 3.6026e-07 | -2.3681e-07 | 0.0051336 | 0.0051335 | 0.0051336 | 0.98851 | -0.21995 | 0.98862 | -0.21774 | 1.4103
139 | -0.0034108 | -0.0008542 | 0.0034109 | 0.00085411 | 1.3622e-07 | -8.9579e-08 | 0.0051335 | 0.0051334 | 0.0051335 | 0.98862 | -0.21774 | 0.98867 | -0.2169 | 1.4103
140 | -0.0049228 | -0.001233 | 0.0049231 | 0.001233 | 3.4539e-07 | 5.8608e-09 | 0.0074089 | 0.0074088 | 0.0074089 | 0.98867 | -0.2169 | 0.98874 | -0.21542 | 2.0354

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46889 | 0.1192

## res_load
| p_mw | q_mvar
0 | 0.022019 | 0.0055185
1 | 0.022954 | 0.0057527
2 | 0.0010064 | 0.00025224
3 | 0.0024343 | 0.00061008
4 | 0.0025444 | 0.0006377
5 | 0.0033772 | 0.0008464
6 | 0.0021338 | 0.00053479
7 | 0.0021726 | 0.00054449
8 | 0.007124 | 0.0017854
9 | 0.0057613 | 0.0014439
10 | 0.0028914 | 0.00072466
11 | 0.0044926 | 0.0011259
12 | 0.0036857 | 0.00092372
13 | 0.0076413 | 0.0019151
14 | 0.0033774 | 0.00084645
15 | 0.003458 | 0.00086666
16 | 0.0042889 | 0.0010749
17 | 0.001608 | 0.00040301
18 | 0.022591 | 0.0056618
19 | 0.002675 | 0.00067041
20 | 0.0034195 | 0.00085702
21 | 0.0031829 | 0.00079771
22 | 0.0044903 | 0.0011254
23 | 0.0020098 | 0.00050371
24 | 0.0044677 | 0.0011197
25 | 0.0053377 | 0.0013378
26 | 0.0037406 | 0.00093748
27 | 0.0059437 | 0.0014896
28 | 0.0033986 | 0.00085176
29 | 0.0020803 | 0.00052137
30 | 0.0031225 | 0.00078256
31 | 0.0039339 | 0.00098592
32 | 0.0018861 | 0.00047269
33 | 0.003565 | 0.00089348
34 | 0.0012991 | 0.00032559
35 | 0.002799 | 0.0007015
36 | 0.0043564 | 0.0010918
37 | 0.0021228 | 0.00053204
38 | 0.0015936 | 0.0003994
39 | 0.0052565 | 0.0013174
40 | 0.0017831 | 0.00044689
41 | 0.0021082 | 0.00052837
42 | 0.0037381 | 0.00093687
43 | 0.0024432 | 0.00061233
44 | 0.0024946 | 0.00062521
45 | 0.0033402 | 0.00083714
46 | 0.0030891 | 0.00077421
47 | 0.0021161 | 0.00053035
48 | 0.00026932 | 6.7497e-05
49 | 0.0083483 | 0.0020923
50 | 0.0058577 | 0.0014681
51 | 0.011853 | 0.0029707
52 | 0.0091485 | 0.0022928
53 | 0.0024022 | 0.00060205
54 | 0.0086611 | 0.0021707
55 | 0.0039516 | 0.00099035
56 | 0.0043764 | 0.0010968
57 | 0.0032796 | 0.00082195
58 | 0.0046369 | 0.0011621
59 | 0.0047715 | 0.0011959
60 | 0.0034319 | 0.00086011
61 | 0.0050876 | 0.0012751
62 | 0.007394 | 0.0018531
63 | 0.0030015 | 0.00075225
64 | 0.0032847 | 0.00082322
65 | 0.0028227 | 0.00070743
66 | 0.0017336 | 0.00043447
67 | 0.0032308 | 0.00080971
68 | 0.0024233 | 0.00060734
69 | 0.0015954 | 0.00039984
70 | 0.0021887 | 0.00054853
71 | 0.0037146 | 0.00093096
72 | 0.0057132 | 0.0014319
73 | 0.0020009 | 0.00050147
74 | 0.007139 | 0.0017892
75 | 0.0040417 | 0.0010129
76 | 0.001842 | 0.00046166
77 | 0.0092631 | 0.0023216
78 | 0.0042599 | 0.0010676
79 | 0.0099464 | 0.0024928
80 | 0.0038287 | 0.00095956
81 | 0.0054474 | 0.0013653
82 | 0.0020881 | 0.00052333
83 | 0.0024165 | 0.00060564
84 | 0.004162 | 0.0010431
85 | 0.0035173 | 0.00088152
86 | 0.0022485 | 0.00056353
87 | 0.0021288 | 0.00053354
88 | 0.0030123 | 0.00075494
89 | 0.0031325 | 0.00078507
90 | 0.0023826 | 0.00059715
91 | 0.0028078 | 0.00070371
92 | 0.0032528 | 0.00081524
93 | 0.0010517 | 0.00026359
94 | 0.018679 | 0.0046813
95 | 0.0038065 | 0.00095399
96 | 0.0046563 | 0.001167
97 | 0.0038691 | 0.00096968
98 | 0.0014373 | 0.00036021
99 | 0.0013557 | 0.00033978
100 | 0.0037281 | 0.00093434
101 | 0.0032725 | 0.00082017
102 | 0.0035225 | 0.00088282
103 | 0.0022066 | 0.00055303
104 | 0.0012037 | 0.00030168
105 | 0.0015119 | 0.00037891
106 | 0.0019815 | 0.00049661

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1