## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3273-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3273-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3273-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3273-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3273-4_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3273-4_0_4_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3273-4_0_4_node_83 | 0.4 | n |  | TRUE
7 | bus_LV_3273-4_0_4_node_82 | 0.4 | n |  | TRUE
8 | bus_LV_3273-4_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_3273-4_0_4_node_20 | 0.4 | n |  | TRUE
10 | bus_LV_3273-4_0_4_node_30 | 0.4 | n |  | TRUE
11 | bus_LV_3273-4_0_4_node_95 | 0.4 | n |  | TRUE
12 | bus_LV_3273-4_0_4_node_94 | 0.4 | n |  | TRUE
13 | bus_LV_3273-4_0_4_node_21 | 0.4 | n |  | TRUE
14 | bus_LV_3273-4_0_4_node_31 | 0.4 | n |  | TRUE
15 | bus_LV_3273-4_0_4_node_7 | 0.4 | n |  | TRUE
16 | bus_LV_3273-4_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_3273-4_0_4_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_3273-4_0_4_node_12 | 0.4 | n |  | TRUE
19 | bus_LV_3273-4_0_4_node_13 | 0.4 | n |  | TRUE
20 | bus_LV_3273-4_0_4_node_10 | 0.4 | n |  | TRUE
21 | bus_LV_3273-4_0_4_node_11 | 0.4 | n |  | TRUE
22 | bus_LV_3273-4_0_4_node_32 | 0.4 | n |  | TRUE
23 | bus_LV_3273-4_0_4_node_106 | 0.4 | n |  | TRUE
24 | bus_LV_3273-4_0_4_node_105 | 0.4 | n |  | TRUE
25 | bus_LV_3273-4_0_4_node_33 | 0.4 | n |  | TRUE
26 | bus_LV_3273-4_0_4_node_109 | 0.4 | n |  | TRUE
27 | bus_LV_3273-4_0_4_node_104 | 0.4 | n |  | TRUE
28 | bus_LV_3273-4_0_4_node_14 | 0.4 | n |  | TRUE
29 | bus_LV_3273-4_0_4_node_58 | 0.4 | n |  | TRUE
30 | bus_LV_3273-4_0_4_node_59 | 0.4 | n |  | TRUE
31 | bus_LV_3273-4_0_4_node_15 | 0.4 | n |  | TRUE
32 | bus_LV_3273-4_0_4_node_16 | 0.4 | n |  | TRUE
33 | bus_LV_3273-4_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_3273-4_0_4_node_28 | 0.4 | n |  | TRUE
35 | bus_LV_3273-4_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_3273-4_0_4_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_3273-4_0_4_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_3273-4_0_4_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_3273-4_0_4_node_22 | 0.4 | n |  | TRUE
40 | bus_LV_3273-4_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_3273-4_0_4_node_38 | 0.4 | n |  | TRUE
42 | bus_LV_3273-4_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_3273-4_0_4_node_35 | 0.4 | n |  | TRUE
44 | bus_LV_3273-4_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_3273-4_0_4_node_39 | 0.4 | n |  | TRUE
46 | bus_LV_3273-4_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_3273-4_0_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_3273-4_0_4_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_3273-4_0_4_node_43 | 0.4 | n |  | TRUE
50 | bus_LV_3273-4_0_4_node_44 | 0.4 | n |  | TRUE
51 | bus_LV_3273-4_0_4_node_45 | 0.4 | n |  | TRUE
52 | bus_LV_3273-4_0_4_node_46 | 0.4 | n |  | TRUE
53 | bus_LV_3273-4_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_3273-4_0_4_node_48 | 0.4 | n |  | TRUE
55 | bus_LV_3273-4_0_4_node_49 | 0.4 | n |  | TRUE
56 | bus_LV_3273-4_0_4_node_50 | 0.4 | n |  | TRUE
57 | bus_LV_3273-4_0_4_node_51 | 0.4 | n |  | TRUE
58 | bus_LV_3273-4_0_4_node_52 | 0.4 | n |  | TRUE
59 | bus_LV_3273-4_0_4_node_74 | 0.4 | n |  | TRUE
60 | bus_LV_3273-4_0_4_node_72 | 0.4 | n |  | TRUE
61 | bus_LV_3273-4_0_4_node_75 | 0.4 | n |  | TRUE
62 | bus_LV_3273-4_0_4_node_71 | 0.4 | n |  | TRUE
63 | bus_LV_3273-4_0_4_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_3273-4_0_4_node_54 | 0.4 | n |  | TRUE
65 | bus_LV_3273-4_0_4_node_55 | 0.4 | n |  | TRUE
66 | bus_LV_3273-4_0_4_node_56 | 0.4 | n |  | TRUE
67 | bus_LV_3273-4_0_4_node_57 | 0.4 | n |  | TRUE
68 | bus_LV_3273-4_0_4_node_67 | 0.4 | n |  | TRUE
69 | bus_LV_3273-4_0_4_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_3273-4_0_4_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_3273-4_0_4_node_68 | 0.4 | n |  | TRUE
72 | bus_LV_3273-4_0_4_node_60 | 0.4 | n |  | TRUE
73 | bus_LV_3273-4_0_4_node_62 | 0.4 | n |  | TRUE
74 | bus_LV_3273-4_0_4_node_63 | 0.4 | n |  | TRUE
75 | bus_LV_3273-4_0_4_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_3273-4_0_4_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_3273-4_0_4_node_69 | 0.4 | n |  | TRUE
78 | bus_LV_3273-4_0_4_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_3273-4_0_4_node_73 | 0.4 | n |  | TRUE
80 | bus_LV_3273-4_0_4_node_79 | 0.4 | n |  | TRUE
81 | bus_LV_3273-4_0_4_node_77 | 0.4 | n |  | TRUE
82 | bus_LV_3273-4_0_4_node_84 | 0.4 | n |  | TRUE
83 | bus_LV_3273-4_0_4_node_78 | 0.4 | n |  | TRUE
84 | bus_LV_3273-4_0_4_node_76 | 0.4 | n |  | TRUE
85 | bus_LV_3273-4_0_4_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_3273-4_0_4_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_3273-4_0_4_node_97 | 0.4 | n |  | TRUE
88 | bus_LV_3273-4_0_4_node_100 | 0.4 | n |  | TRUE
89 | bus_LV_3273-4_0_4_node_85 | 0.4 | n |  | TRUE
90 | bus_LV_3273-4_0_4_node_98 | 0.4 | n |  | TRUE
91 | bus_LV_3273-4_0_4_node_101 | 0.4 | n |  | TRUE
92 | bus_LV_3273-4_0_4_node_86 | 0.4 | n |  | TRUE
93 | bus_LV_3273-4_0_4_node_87 | 0.4 | n |  | TRUE
94 | bus_LV_3273-4_0_4_node_88 | 0.4 | n |  | TRUE
95 | bus_LV_3273-4_0_4_node_89 | 0.4 | n |  | TRUE
96 | bus_LV_3273-4_0_4_node_90 | 0.4 | n |  | TRUE
97 | bus_LV_3273-4_0_4_node_91 | 0.4 | n |  | TRUE
98 | bus_LV_3273-4_0_4_node_93 | 0.4 | n |  | TRUE
99 | bus_LV_3273-4_0_4_node_122 | 0.4 | n |  | TRUE
100 | bus_LV_3273-4_0_4_node_123 | 0.4 | n |  | TRUE
101 | bus_LV_3273-4_0_4_node_99 | 0.4 | n |  | TRUE
102 | bus_LV_3273-4_0_4_node_102 | 0.4 | n |  | TRUE
103 | bus_LV_3273-4_0_4_node_107 | 0.4 | n |  | TRUE
104 | bus_LV_3273-4_0_4_node_103 | 0.4 | n |  | TRUE
105 | bus_LV_3273-4_0_4_node_108 | 0.4 | n |  | TRUE
106 | bus_LV_3273-4_0_4_node_120 | 0.4 | n |  | TRUE
107 | bus_LV_3273-4_0_4_node_121 | 0.4 | n |  | TRUE
108 | bus_LV_3273-4_0_4_node_110 | 0.4 | n |  | TRUE
109 | bus_LV_3273-4_0_4_node_111 | 0.4 | n |  | TRUE
110 | bus_LV_3273-4_0_4_node_112 | 0.4 | n |  | TRUE
111 | bus_LV_3273-4_0_4_node_113 | 0.4 | n |  | TRUE
112 | bus_LV_3273-4_0_4_node_114 | 0.4 | n |  | TRUE
113 | bus_LV_3273-4_0_4_node_115 | 0.4 | n |  | TRUE
114 | bus_LV_3273-4_0_4_node_116 | 0.4 | n |  | TRUE
115 | bus_LV_3273-4_0_4_node_117 | 0.4 | n |  | TRUE
116 | bus_LV_3273-4_0_4_node_118 | 0.4 | n |  | TRUE
117 | bus_LV_3273-4_0_4_node_126 | 0.4 | n |  | TRUE
118 | bus_LV_3273-4_0_4_node_119 | 0.4 | n |  | TRUE
119 | bus_LV_3273-4_0_4_node_125 | 0.4 | n |  | TRUE
120 | bus_LV_3273-4_0_4_node_124 | 0.4 | n |  | TRUE
121 | bus_MV_237_0_node_132 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3273-4_0_4_load_0 | 0 | 0.0004353 | 0.0001091 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3273-4_0_4_load_1 | 1 | 0.00063703 | 0.00015966 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3273-4_0_4_load_3 | 3 | 0.00083805 | 0.00021003 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3273-4_0_4_load_4 | 4 | 0.00087795 | 0.00022004 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3273-4_0_4_load_5 | 5 | 0.00046878 | 0.00011749 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3273-4_0_4_load_83 | 6 | 0.0010994 | 0.00027553 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3273-4_0_4_load_82 | 7 | 0.0050851 | 0.0012744 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3273-4_0_4_load_95 | 11 | 0.0010547 | 0.00026433 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3273-4_0_4_load_21 | 13 | 0.0011328 | 0.0002839 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3273-4_0_4_load_31 | 14 | 0.0010251 | 0.00025692 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3273-4_0_4_load_7 | 15 | 0.00092677 | 0.00023227 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3273-4_0_4_load_8 | 16 | 0.002222 | 0.00055689 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3273-4_0_4_load_9 | 17 | 0.0051735 | 0.0012966 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3273-4_0_4_load_12 | 18 | 0.0012808 | 0.00032101 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3273-4_0_4_load_13 | 19 | 0.0011733 | 0.00029406 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3273-4_0_4_load_32 | 22 | 0.001187 | 0.00029749 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3273-4_0_4_load_106 | 23 | 0.002381 | 0.00059673 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3273-4_0_4_load_105 | 24 | 0.0024313 | 0.00060934 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3273-4_0_4_load_33 | 25 | 0.00084752 | 0.00021241 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3273-4_0_4_load_109 | 26 | 0.0012459 | 0.00031226 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3273-4_0_4_load_104 | 27 | 0.0021447 | 0.0005375 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3273-4_0_4_load_14 | 28 | 0.0010756 | 0.00026957 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3273-4_0_4_load_58 | 29 | 0.0013576 | 0.00034024 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3273-4_0_4_load_59 | 30 | 0.001293 | 0.00032406 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3273-4_0_4_load_15 | 31 | 0.0093382 | 0.0023404 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3273-4_0_4_load_16 | 32 | 0.00073696 | 0.0001847 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3273-4_0_4_load_19 | 33 | 0.0009344 | 0.00023418 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3273-4_0_4_load_28 | 34 | 0.00026053 | 6.5294e-05 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3273-4_0_4_load_26 | 35 | 0.00036398 | 9.1222e-05 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3273-4_0_4_load_25 | 36 | 0.00050221 | 0.00012587 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3273-4_0_4_load_24 | 38 | 0.0019042 | 0.00047724 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3273-4_0_4_load_22 | 39 | 0.0010102 | 0.00025319 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3273-4_0_4_load_37 | 40 | 0.00073805 | 0.00018497 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3273-4_0_4_load_38 | 41 | 0.00044673 | 0.00011196 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3273-4_0_4_load_34 | 42 | 0.0017535 | 0.00043948 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3273-4_0_4_load_35 | 43 | 0.0030864 | 0.00077353 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3273-4_0_4_load_36 | 44 | 0.0028018 | 0.0007022 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3273-4_0_4_load_39 | 45 | 0.00075634 | 0.00018956 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3273-4_0_4_load_41 | 47 | 0.00054966 | 0.00013776 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3273-4_0_4_load_42 | 48 | 0.00050061 | 0.00012546 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3273-4_0_4_load_43 | 49 | 0.00049234 | 0.00012339 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3273-4_0_4_load_44 | 50 | 0.00045282 | 0.00011349 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3273-4_0_4_load_45 | 51 | 0.00025305 | 6.342e-05 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3273-4_0_4_load_46 | 52 | 0.00043846 | 0.00010989 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3273-4_0_4_load_47 | 53 | 0.00033106 | 8.2972e-05 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3273-4_0_4_load_48 | 54 | 0.0010171 | 0.00025491 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3273-4_0_4_load_49 | 55 | 0.00049414 | 0.00012384 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3273-4_0_4_load_50 | 56 | 0.00027312 | 6.845e-05 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3273-4_0_4_load_51 | 57 | 0.0011596 | 0.00029062 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3273-4_0_4_load_74 | 59 | 0.030408 | 0.007621 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3273-4_0_4_load_72 | 60 | 0.031978 | 0.0080145 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3273-4_0_4_load_75 | 61 | 0.00035468 | 8.889e-05 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3273-4_0_4_load_53 | 63 | 0.00063017 | 0.00015794 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3273-4_0_4_load_54 | 64 | 0.00077419 | 0.00019403 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3273-4_0_4_load_57 | 67 | 0.0016872 | 0.00042285 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3273-4_0_4_load_67 | 68 | 0.0011644 | 0.00029182 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3273-4_0_4_load_64 | 69 | 0.00069323 | 0.00017374 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3273-4_0_4_load_68 | 71 | 0.0018697 | 0.0004686 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3273-4_0_4_load_60 | 72 | 0.0023159 | 0.00058041 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3273-4_0_4_load_62 | 73 | 0.0030193 | 0.00075672 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3273-4_0_4_load_65 | 75 | 0.0040536 | 0.0010159 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3273-4_0_4_load_66 | 76 | 0.0019684 | 0.00049333 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3273-4_0_4_load_69 | 77 | 0.010012 | 0.0025092 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3273-4_0_4_load_70 | 78 | 0.0070135 | 0.0017578 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3273-4_0_4_load_79 | 80 | 0.01582 | 0.0039648 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3273-4_0_4_load_77 | 81 | 0.0081352 | 0.0020389 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3273-4_0_4_load_84 | 82 | 0.01516 | 0.0037993 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3273-4_0_4_load_76 | 84 | 0.0011539 | 0.0002892 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3273-4_0_4_load_80 | 85 | 0.0064924 | 0.0016272 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3273-4_0_4_load_81 | 86 | 0.018365 | 0.0046027 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3273-4_0_4_load_97 | 87 | 0.016315 | 0.004089 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3273-4_0_4_load_100 | 88 | 0.0049544 | 0.0012417 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3273-4_0_4_load_85 | 89 | 0.0073591 | 0.0018444 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3273-4_0_4_load_98 | 90 | 0.0077338 | 0.0019383 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3273-4_0_4_load_101 | 91 | 0.0019001 | 0.00047622 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3273-4_0_4_load_86 | 92 | 0.0007881 | 0.00019752 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_3273-4_0_4_load_87 | 93 | 0.0037718 | 0.00094531 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_3273-4_0_4_load_89 | 95 | 0.00071677 | 0.00017964 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_3273-4_0_4_load_90 | 96 | 0.00025202 | 6.3161e-05 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_3273-4_0_4_load_91 | 97 | 0.0022389 | 0.00056113 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_3273-4_0_4_load_93 | 98 | 0.0013157 | 0.00032975 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_3273-4_0_4_load_122 | 99 | 0.0023469 | 0.00058818 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_3273-4_0_4_load_123 | 100 | 0.001258 | 0.00031528 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_3273-4_0_4_load_99 | 101 | 0.0017022 | 0.00042662 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_3273-4_0_4_load_102 | 102 | 0.001906 | 0.00047769 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_3273-4_0_4_load_107 | 103 | 0.0050721 | 0.0012712 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_3273-4_0_4_load_103 | 104 | 0.0018421 | 0.00046166 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_3273-4_0_4_load_108 | 105 | 0.0039406 | 0.00098761 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_3273-4_0_4_load_120 | 106 | 0.0051066 | 0.0012798 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_3273-4_0_4_load_121 | 107 | 0.0046501 | 0.0011654 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_3273-4_0_4_load_110 | 108 | 0.0026668 | 0.00066836 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_3273-4_0_4_load_111 | 109 | 0.0038003 | 0.00095245 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_3273-4_0_4_load_112 | 110 | 0.0020335 | 0.00050965 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_3273-4_0_4_load_113 | 111 | 0.0030282 | 0.00075894 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_3273-4_0_4_load_114 | 112 | 0.0040329 | 0.0010107 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_3273-4_0_4_load_116 | 114 | 0.007351 | 0.0018423 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_3273-4_0_4_load_118 | 116 | 0.0011615 | 0.00029111 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_3273-4_0_4_load_126 | 117 | 0.0020817 | 0.00052172 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_3273-4_0_4_load_119 | 118 | 0.0037912 | 0.00095016 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_3273-4_0_4_load_125 | 119 | 0.0025212 | 0.00063188 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 79 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3273-4_0_4_line_0 |  | 0 | 1 | 0.0013161 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3273-4_0_4_line_1 |  | 0 | 2 | 0.052335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3273-4_0_4_line_2 |  | 1 | 3 | 0.050685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3273-4_0_4_line_3 |  | 2 | 4 | 0.026904 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3273-4_0_4_line_4 |  | 2 | 5 | 0.03324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3273-4_0_4_line_5 |  | 3 | 8 | 0.024202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3273-4_0_4_line_6 |  | 4 | 9 | 0.01005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3273-4_0_4_line_7 |  | 5 | 10 | 0.098177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3273-4_0_4_line_8 |  | 6 | 7 | 0.027263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3273-4_0_4_line_9 |  | 7 | 84 | 0.035354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3273-4_0_4_line_10 |  | 8 | 11 | 0.11681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3273-4_0_4_line_11 |  | 9 | 13 | 0.021963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3273-4_0_4_line_12 |  | 10 | 14 | 0.05128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3273-4_0_4_line_13 |  | 11 | 12 | 0.0014425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3273-4_0_4_line_14 |  | 12 | 98 | 0.0047687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3273-4_0_4_line_15 |  | 13 | 38 | 0.027806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3273-4_0_4_line_16 |  | 14 | 39 | 0.0547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3273-4_0_4_line_17 |  | 15 | 16 | 0.047008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3273-4_0_4_line_18 |  | 16 | 17 | 0.019679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3273-4_0_4_line_19 |  | 17 | 18 | 0.0027164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3273-4_0_4_line_20 |  | 18 | 19 | 0.04837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3273-4_0_4_line_21 |  | 19 | 28 | 0.041868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3273-4_0_4_line_22 |  | 20 | 21 | 0.088563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3273-4_0_4_line_23 |  | 20 | 22 | 0.11683 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3273-4_0_4_line_24 |  | 21 | 23 | 0.020375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3273-4_0_4_line_25 |  | 21 | 24 | 0.0078837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3273-4_0_4_line_26 |  | 22 | 25 | 0.035953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3273-4_0_4_line_27 |  | 23 | 26 | 0.0028336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3273-4_0_4_line_28 |  | 24 | 27 | 0.0023137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3273-4_0_4_line_29 |  | 26 | 44 | 0.024835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3273-4_0_4_line_30 |  | 27 | 104 | 0.026532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3273-4_0_4_line_31 |  | 28 | 29 | 0.01185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3273-4_0_4_line_32 |  | 29 | 30 | 0.041756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3273-4_0_4_line_33 |  | 30 | 72 | 0.0053514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3273-4_0_4_line_34 |  | 31 | 32 | 0.003516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3273-4_0_4_line_35 |  | 32 | 33 | 0.16562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3273-4_0_4_line_36 |  | 33 | 36 | 0.17867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3273-4_0_4_line_37 |  | 34 | 35 | 0.012895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3273-4_0_4_line_38 |  | 35 | 36 | 0.018027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3273-4_0_4_line_39 |  | 36 | 37 | 0.074754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3273-4_0_4_line_40 |  | 37 | 40 | 0.09521 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3273-4_0_4_line_41 |  | 40 | 41 | 0.0036207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3273-4_0_4_line_42 |  | 41 | 45 | 0.04506 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3273-4_0_4_line_43 |  | 42 | 43 | 0.028349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3273-4_0_4_line_44 |  | 43 | 44 | 0.0002707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3273-4_0_4_line_45 |  | 45 | 46 | 0.018501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3273-4_0_4_line_46 |  | 46 | 47 | 0.015713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3273-4_0_4_line_47 |  | 46 | 48 | 0.026727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3273-4_0_4_line_48 |  | 47 | 49 | 0.049189 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3273-4_0_4_line_49 |  | 48 | 50 | 0.032253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3273-4_0_4_line_50 |  | 50 | 51 | 0.012447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3273-4_0_4_line_51 |  | 51 | 52 | 0.0095993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3273-4_0_4_line_52 |  | 52 | 53 | 0.013986 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3273-4_0_4_line_53 |  | 53 | 54 | 0.042293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3273-4_0_4_line_54 |  | 54 | 55 | 0.035992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3273-4_0_4_line_55 |  | 55 | 56 | 0.013176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3273-4_0_4_line_56 |  | 56 | 57 | 0.038056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3273-4_0_4_line_57 |  | 57 | 58 | 0.023604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3273-4_0_4_line_58 |  | 58 | 59 | 0.014479 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3273-4_0_4_line_59 |  | 58 | 60 | 0.044017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3273-4_0_4_line_60 |  | 59 | 61 | 0.024828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3273-4_0_4_line_61 |  | 60 | 62 | 0.017333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3273-4_0_4_line_62 |  | 61 | 84 | 0.0089424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3273-4_0_4_line_63 |  | 62 | 79 | 0.025071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3273-4_0_4_line_64 |  | 62 | 78 | 0.0064483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3273-4_0_4_line_65 |  | 63 | 64 | 0.02249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3273-4_0_4_line_66 |  | 64 | 65 | 0.032009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3273-4_0_4_line_67 |  | 65 | 66 | 0.055146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3273-4_0_4_line_68 |  | 65 | 67 | 0.017162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3273-4_0_4_line_69 |  | 66 | 68 | 0.0099629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3273-4_0_4_line_70 |  | 66 | 69 | 0.011593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3273-4_0_4_line_71 |  | 67 | 70 | 0.037555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3273-4_0_4_line_72 |  | 68 | 71 | 0.010905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3273-4_0_4_line_73 |  | 69 | 72 | 0.0063948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3273-4_0_4_line_74 |  | 70 | 73 | 0.02889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3273-4_0_4_line_75 |  | 70 | 74 | 0.005822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3273-4_0_4_line_76 |  | 71 | 77 | 0.050216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3273-4_0_4_line_77 |  | 73 | 75 | 0.016285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3273-4_0_4_line_78 |  | 74 | 76 | 0.051174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3273-4_0_4_line_79 |  | 77 | 78 | 0.023049 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3273-4_0_4_line_80 |  | 79 | 80 | 0.01741 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3273-4_0_4_line_81 |  | 79 | 81 | 0.014755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_3273-4_0_4_line_82 |  | 80 | 82 | 0.012246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3273-4_0_4_line_83 |  | 81 | 83 | 0.012767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3273-4_0_4_line_84 |  | 82 | 89 | 0.0061557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3273-4_0_4_line_85 |  | 83 | 85 | 0.020421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3273-4_0_4_line_86 |  | 83 | 86 | 0.028753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3273-4_0_4_line_87 |  | 85 | 87 | 0.019384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3273-4_0_4_line_88 |  | 86 | 88 | 0.01408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3273-4_0_4_line_89 |  | 87 | 90 | 0.0039596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3273-4_0_4_line_90 |  | 88 | 91 | 0.013743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3273-4_0_4_line_91 |  | 89 | 92 | 0.0050647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3273-4_0_4_line_92 |  | 90 | 101 | 0.023452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3273-4_0_4_line_93 |  | 91 | 104 | 0.015948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3273-4_0_4_line_94 |  | 92 | 93 | 0.04216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3273-4_0_4_line_95 |  | 93 | 94 | 0.0040121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3273-4_0_4_line_96 |  | 94 | 95 | 0.019959 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3273-4_0_4_line_97 |  | 95 | 96 | 0.0066895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_3273-4_0_4_line_98 |  | 96 | 97 | 0.012364 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_3273-4_0_4_line_99 |  | 97 | 98 | 0.028958 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_3273-4_0_4_line_100 |  | 99 | 100 | 0.01065 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3273-4_0_4_line_101 |  | 100 | 120 | 0.028943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_3273-4_0_4_line_102 |  | 101 | 102 | 0.013528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3273-4_0_4_line_103 |  | 102 | 103 | 0.0016222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3273-4_0_4_line_104 |  | 103 | 105 | 0.010541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3273-4_0_4_line_105 |  | 105 | 106 | 0.029151 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3273-4_0_4_line_106 |  | 106 | 107 | 0.0048207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3273-4_0_4_line_107 |  | 107 | 120 | 0.018292 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3273-4_0_4_line_108 |  | 108 | 109 | 0.0088059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_3273-4_0_4_line_109 |  | 108 | 110 | 0.0022772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_3273-4_0_4_line_110 |  | 109 | 111 | 0.0229 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_3273-4_0_4_line_111 |  | 111 | 112 | 0.002602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_3273-4_0_4_line_112 |  | 112 | 113 | 0.017467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_3273-4_0_4_line_113 |  | 113 | 114 | 0.037993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_3273-4_0_4_line_114 |  | 113 | 115 | 0.05037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_3273-4_0_4_line_115 |  | 114 | 116 | 0.017036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_3273-4_0_4_line_116 |  | 115 | 117 | 0.020609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_3273-4_0_4_line_117 |  | 116 | 118 | 0.021316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_3273-4_0_4_line_118 |  | 117 | 119 | 0.012975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_3273-4_0_4_line_119 |  | 118 | 120 | 0.0021828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3273-4_0_4_trafo_73 | 0.63 MVA 20/0.4 kV | 121 | 79 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2753184.477 | 1226099.4827 | 2753184.711 | 1226100.7779
1 | 2753154.4523 | 1226058.8635 | 2753166.2978 | 1226066.8646 | 2753175.2403 | 1226077.1486 | 2753183.1513 | 1226092.1437 | 2753184.477 | 1226099.4827
2 | 2753227.4063 | 1226116.1107 | 2753223.3386 | 1226114.0093 | 2753219.6409 | 1226113.5804 | 2753208.4797 | 1226113.7599 | 2753197.2312 | 1226113.5034 | 2753192.3729 | 1226112.1994 | 2753188.5388 | 1226110.5881 | 2753185.7732 | 1226106.6577 | 2753184.711 | 1226100.7779
3 | 2753154.4523 | 1226058.8635 | 2753153.1206 | 1226052.5568 | 2753143.1352 | 1226034.7006
4 | 2753154.4523 | 1226058.8635 | 2753150.2127 | 1226063.5698 | 2753132.8989 | 1226079.1274 | 2753129.8948 | 1226081.1625
5 | 2753247.0231 | 1226130.2451 | 2753229.1616 | 1226117.0175 | 2753227.4063 | 1226116.1107
6 | 2753137.4177 | 1226026.4733 | 2753141.2009 | 1226031.2417 | 2753143.1352 | 1226034.7006
7 | 2753034.5484 | 1226096.0796 | 2753037.2376 | 1226096.2045 | 2753063.0323 | 1226096.7795 | 2753080.6158 | 1226094.8967 | 2753104.6709 | 1226091.4568 | 2753119.9463 | 1226087.9021 | 2753129.8948 | 1226081.1625
8 | 2753111.0327 | 1226219.6847 | 2753098.1439 | 1226243.7086
9 | 2753081.43 | 1226274.8622 | 2753098.1439 | 1226243.7086
10 | 2753217.5351 | 1226243.2759 | 2753247.0231 | 1226130.2451
11 | 2753137.4177 | 1226026.4733 | 2753142.5055 | 1226005.6185 | 2753142.6233 | 1226005.1359
12 | 2753034.5484 | 1226096.0796 | 2753035.376 | 1226092.5088 | 2753033.6848 | 1226086.3152 | 2753028.9703 | 1226082.3681 | 2753021.1516 | 1226079.0974 | 2753012.7465 | 1226074.4437 | 2752999.5623 | 1226063.6393
13 | 2753216.1241 | 1226243.5754 | 2753217.5351 | 1226243.2759
14 | 2753216.1241 | 1226243.5754 | 2753212.6389 | 1226244.3197 | 2753211.6855 | 1226245.0564
15 | 2753142.6233 | 1226005.1359 | 2753143.5145 | 1226001.4852 | 2753153.7603 | 1225979.7289
16 | 2752999.5623 | 1226063.6393 | 2752998.0965 | 1226008.9591
17 | 2753062.4445 | 1226552.4228 | 2753058.4159 | 1226563.3316 | 2753054.2741 | 1226573.9793 | 2753046.0392 | 1226585.7227 | 2753036.6372 | 1226587.716
18 | 2753036.6372 | 1226587.716 | 2753036.6372 | 1226587.716 | 2753030.3058 | 1226584.7282 | 2753024.0294 | 1226573.7123
19 | 2753024.0294 | 1226573.7123 | 2753024.0294 | 1226573.7123 | 2753023.3736 | 1226571.0762
20 | 2753022.2334 | 1226524.3474 | 2753019.9745 | 1226528.8337 | 2753016.8816 | 1226541.4546 | 2753018.2288 | 1226550.3974 | 2753023.3736 | 1226571.0762
21 | 2753024.8873 | 1226485.0474 | 2753029.1177 | 1226496.8284 | 2753029.8531 | 1226509.2142 | 2753022.2334 | 1226524.3474
22 | 2753186.3444 | 1226534.2635 | 2753190.7595 | 1226510.6667 | 2753206.4335 | 1226448.0462
23 | 2753186.3444 | 1226534.2635 | 2753164.6377 | 1226649.0604
24 | 2753206.4335 | 1226448.0462 | 2753223.4902 | 1226459.192
25 | 2753206.4335 | 1226448.0462 | 2753199.7278 | 1226443.9007
26 | 2753164.6377 | 1226649.0604 | 2753157.7048 | 1226684.3383
27 | 2753223.4902 | 1226459.192 | 2753225.8623 | 1226460.742
28 | 2753197.7598 | 1226442.684 | 2753199.7278 | 1226443.9007
29 | 2753245.3065 | 1226475.7981 | 2753241.48 | 1226470.9474 | 2753225.8623 | 1226460.742
30 | 2753175.5902 | 1226428.1889 | 2753178.8578 | 1226430.9985 | 2753197.7598 | 1226442.684
31 | 2753024.8873 | 1226485.0474 | 2753020.8827 | 1226473.8951
32 | 2753020.8827 | 1226473.8951 | 2753014.7805 | 1226456.901 | 2753014.9078 | 1226446.0611 | 2753018.7034 | 1226433.7756
33 | 2753018.7034 | 1226433.7756 | 2753019.2098 | 1226432.1367 | 2753019.5507 | 1226428.5166
34 | 2752660.2925 | 1225722.0339 | 2752661.8826 | 1225725.1698
35 | 2752661.8826 | 1225725.1698 | 2752715.1609 | 1225881.9897
36 | 2752760.3212 | 1226054.8571 | 2752715.1609 | 1225881.9897
37 | 2752743.0348 | 1226059.9693 | 2752740.1729 | 1226060.8405 | 2752730.2698 | 1226060.8511
38 | 2752760.3212 | 1226054.8571 | 2752752.4035 | 1226057.1177 | 2752743.0348 | 1226059.9693
39 | 2752834.051 | 1226052.3318 | 2752817.1531 | 1226049.3729 | 2752798.4762 | 1226048.0588 | 2752786.8225 | 1226049.105 | 2752773.4528 | 1226051.1081 | 2752760.3212 | 1226054.8571
40 | 2752803.8768 | 1226142.6334 | 2752834.051 | 1226052.3318
41 | 2752803.8768 | 1226142.6334 | 2752806.3382 | 1226145.2889
42 | 2752806.3382 | 1226145.2889 | 2752836.9698 | 1226178.3357
43 | 2753263.0066 | 1226498.2845 | 2753262.9095 | 1226498.113 | 2753245.4741 | 1226476.0106
44 | 2753245.4741 | 1226476.0106 | 2753245.3065 | 1226475.7981
45 | 2752848.128 | 1226193.0439 | 2752840.8004 | 1226182.4683 | 2752836.9698 | 1226178.3357
46 | 2752848.128 | 1226193.0439 | 2752833.3891 | 1226198.4908
47 | 2752848.128 | 1226193.0439 | 2752868.179 | 1226210.7149
48 | 2752833.3891 | 1226198.4908 | 2752808.1741 | 1226207.8091 | 2752803.1671 | 1226210.2272 | 2752796.0187 | 1226213.3354 | 2752792.4468 | 1226216.2797 | 2752790.1756 | 1226219.9581
49 | 2752868.179 | 1226210.7149 | 2752878.0373 | 1226219.4029 | 2752887.9096 | 1226225.0951 | 2752895.3274 | 1226227.2234
50 | 2752895.3274 | 1226227.2234 | 2752907.2913 | 1226230.6562
51 | 2752916.5183 | 1226233.3036 | 2752907.2913 | 1226230.6562
52 | 2752916.5183 | 1226233.3036 | 2752929.0384 | 1226236.896 | 2752929.9194 | 1226237.2784
53 | 2752929.9194 | 1226237.2784 | 2752968.7148 | 1226254.1203
54 | 2752968.7148 | 1226254.1203 | 2752988.6214 | 1226262.7622 | 2753000.5702 | 1226270.6011
55 | 2753000.5702 | 1226270.6011 | 2753011.5873 | 1226277.8288
56 | 2753011.5873 | 1226277.8288 | 2753019.8339 | 1226283.2389 | 2753041.8334 | 1226300.8712
57 | 2753058.6199 | 1226317.3787 | 2753048.0189 | 1226305.8288 | 2753041.8334 | 1226300.8712
58 | 2753058.6199 | 1226317.3787 | 2753065.465 | 1226304.62
59 | 2753058.6199 | 1226317.3787 | 2753068.2987 | 1226327.9261 | 2753089.7471 | 1226348.4725
60 | 2753065.465 | 1226304.62 | 2753077.2024 | 1226282.7422
61 | 2753102.264 | 1226360.463 | 2753089.7471 | 1226348.4725
62 | 2753081.43 | 1226274.8622 | 2753077.2024 | 1226282.7422
63 | 2753122.9412 | 1226346.2042 | 2753120.9646 | 1226347.5657 | 2753117.9612 | 1226349.6347 | 2753115.7914 | 1226351.1358 | 2753102.264 | 1226360.463
64 | 2753102.264 | 1226360.463 | 2753096.8149 | 1226363.9109
65 | 2752929.7068 | 1226477.6984 | 2752930.5252 | 1226476.2973 | 2752936.3796 | 1226469.5305 | 2752944.4524 | 1226460.7611
66 | 2752967.5907 | 1226438.7379 | 2752954.9715 | 1226449.3343 | 2752944.4524 | 1226460.7611
67 | 2752967.5907 | 1226438.7379 | 2752983.1431 | 1226429.0955 | 2753015.6096 | 1226411.4252
68 | 2752967.5907 | 1226438.7379 | 2752956.332 | 1226425.7849
69 | 2753015.6096 | 1226411.4252 | 2753021.0966 | 1226408.3302 | 2753024.3336 | 1226406.6154
70 | 2753015.6096 | 1226411.4252 | 2753019.9361 | 1226422.1811
71 | 2752926.2295 | 1226403.5983 | 2752952.6306 | 1226421.5265 | 2752956.332 | 1226425.7849
72 | 2753024.3336 | 1226406.6154 | 2753033.9703 | 1226401.5106
73 | 2753019.5507 | 1226428.5166 | 2753020.1073 | 1226422.6067 | 2753019.9361 | 1226422.1811
74 | 2752926.2295 | 1226403.5983 | 2752912.8151 | 1226429.1856
75 | 2752921.3992 | 1226400.3267 | 2752926.2295 | 1226403.5983
76 | 2753033.9703 | 1226401.5106 | 2753048.2457 | 1226393.9485 | 2753071.3408 | 1226380.0298 | 2753077.3378 | 1226376.2352
77 | 2752907.508 | 1226444.1654 | 2752907.0654 | 1226441.6183 | 2752912.0257 | 1226430.6914 | 2752912.8151 | 1226429.1856
78 | 2752921.3992 | 1226400.3267 | 2752909.6558 | 1226424.3469 | 2752903.7811 | 1226428.9557 | 2752896.1436 | 1226429.2709 | 2752887.6436 | 1226425.434
79 | 2753077.3378 | 1226376.2352 | 2753096.8149 | 1226363.9109
80 | 2753122.9412 | 1226346.2042 | 2753137.5381 | 1226336.7157
81 | 2753122.9412 | 1226346.2042 | 2753131.5555 | 1226355.9681 | 2753132.8674 | 1226357.1016
82 | 2753137.5381 | 1226336.7157 | 2753147.8056 | 1226330.0415
83 | 2753142.528 | 1226365.448 | 2753132.8674 | 1226357.1016
84 | 2753152.9668 | 1226326.6865 | 2753147.8056 | 1226330.0415
85 | 2753142.528 | 1226365.448 | 2753155.3707 | 1226369.1597 | 2753162.4166 | 1226369.4743
86 | 2753142.528 | 1226365.448 | 2753152.3361 | 1226392.4761
87 | 2753162.4166 | 1226369.4743 | 2753168.9154 | 1226369.7644 | 2753181.5158 | 1226367.1006
88 | 2753152.3361 | 1226392.4761 | 2753153.0792 | 1226394.5239 | 2753157.6552 | 1226405.5107
89 | 2753181.5158 | 1226367.1006 | 2753185.3897 | 1226366.2817
90 | 2753163.4981 | 1226417.7916 | 2753162.3641 | 1226416.8166 | 2753157.6552 | 1226405.5107
91 | 2753152.9668 | 1226326.6865 | 2753157.2132 | 1226323.9262
92 | 2753185.3897 | 1226366.2817 | 2753186.4998 | 1226366.047 | 2753197.5832 | 1226362.3956 | 2753206.6705 | 1226362.9189 | 2753208.1573 | 1226362.4958
93 | 2753175.5902 | 1226428.1889 | 2753163.4981 | 1226417.7916
94 | 2753157.2132 | 1226323.9262 | 2753173.5784 | 1226313.2883 | 2753192.5229 | 1226300.8905
95 | 2753195.88 | 1226298.6935 | 2753192.5229 | 1226300.8905
96 | 2753195.88 | 1226298.6935 | 2753184.6869 | 1226282.168
97 | 2753184.6869 | 1226282.168 | 2753184.8346 | 1226275.4801
98 | 2753190.914 | 1226264.9904 | 2753188.9287 | 1226267.3637 | 2753184.8688 | 1226273.9318 | 2753184.8346 | 1226275.4801
99 | 2753190.914 | 1226264.9904 | 2753200.103 | 1226254.0058 | 2753211.6855 | 1226245.0564
100 | 2753246.1461 | 1226287.9494 | 2753252.9207 | 1226296.1669
101 | 2753271.3317 | 1226318.4989 | 2753252.9207 | 1226296.1669
102 | 2753221.1691 | 1226358.7931 | 2753208.1573 | 1226362.4958
103 | 2753221.1691 | 1226358.7931 | 2753222.1874 | 1226358.5033 | 2753222.6253 | 1226358.1488
104 | 2753222.6253 | 1226358.1488 | 2753230.818 | 1226351.5162
105 | 2753230.818 | 1226351.5162 | 2753241.5051 | 1226342.8642 | 2753253.4319 | 1226333.1212
106 | 2753257.1652 | 1226330.0714 | 2753253.4319 | 1226333.1212
107 | 2753271.3317 | 1226318.4989 | 2753257.1652 | 1226330.0714
108 | 2753281.2793 | 1226411.9187 | 2753288.0866 | 1226406.3326
109 | 2753279.5189 | 1226413.3632 | 2753281.2793 | 1226411.9187
110 | 2753288.0866 | 1226406.3326 | 2753305.7892 | 1226391.8058
111 | 2753307.8007 | 1226390.1552 | 2753305.7892 | 1226391.8058
112 | 2753321.3034 | 1226379.0749 | 2753307.8007 | 1226390.1552
113 | 2753321.3034 | 1226379.0749 | 2753297.126 | 1226349.7669
114 | 2753353.8151 | 1226417.6257 | 2753321.3034 | 1226379.0749
115 | 2753297.126 | 1226349.7669 | 2753286.2852 | 1226336.6256
116 | 2753353.8151 | 1226417.6257 | 2753338.2914 | 1226431.1807
117 | 2753272.7208 | 1226320.1827 | 2753286.2852 | 1226336.6256
118 | 2753329.3934 | 1226440.168 | 2753329.5305 | 1226438.8305 | 2753338.2914 | 1226431.1807
119 | 2753271.3317 | 1226318.4989 | 2753272.7208 | 1226320.1827

## bus_geodata
| x | y | coords
0 | 2753184.477 | 1226099.4827
1 | 2753184.711 | 1226100.7779
2 | 2753154.4523 | 1226058.8635
3 | 2753227.4063 | 1226116.1107
4 | 2753143.1352 | 1226034.7006
5 | 2753129.8948 | 1226081.1625
6 | 2753111.0327 | 1226219.6847
7 | 2753098.1439 | 1226243.7086
8 | 2753247.0231 | 1226130.2451
9 | 2753137.4177 | 1226026.4733
10 | 2753034.5484 | 1226096.0796
11 | 2753217.5351 | 1226243.2759
12 | 2753216.1241 | 1226243.5754
13 | 2753142.6233 | 1226005.1359
14 | 2752999.5623 | 1226063.6393
15 | 2753062.4445 | 1226552.4228
16 | 2753036.6372 | 1226587.716
17 | 2753024.0294 | 1226573.7123
18 | 2753023.3736 | 1226571.0762
19 | 2753022.2334 | 1226524.3474
20 | 2753186.3444 | 1226534.2635
21 | 2753206.4335 | 1226448.0462
22 | 2753164.6377 | 1226649.0604
23 | 2753223.4902 | 1226459.192
24 | 2753199.7278 | 1226443.9007
25 | 2753157.7048 | 1226684.3383
26 | 2753225.8623 | 1226460.742
27 | 2753197.7598 | 1226442.684
28 | 2753024.8873 | 1226485.0474
29 | 2753020.8827 | 1226473.8951
30 | 2753018.7034 | 1226433.7756
31 | 2752660.2925 | 1225722.0339
32 | 2752661.8826 | 1225725.1698
33 | 2752715.1609 | 1225881.9897
34 | 2752730.2698 | 1226060.8511
35 | 2752743.0348 | 1226059.9693
36 | 2752760.3212 | 1226054.8571
37 | 2752834.051 | 1226052.3318
38 | 2753153.7603 | 1225979.7289
39 | 2752998.0965 | 1226008.9591
40 | 2752803.8768 | 1226142.6334
41 | 2752806.3382 | 1226145.2889
42 | 2753263.0066 | 1226498.2845
43 | 2753245.4741 | 1226476.0106
44 | 2753245.3065 | 1226475.7981
45 | 2752836.9698 | 1226178.3357
46 | 2752848.128 | 1226193.0439
47 | 2752833.3891 | 1226198.4908
48 | 2752868.179 | 1226210.7149
49 | 2752790.1756 | 1226219.9581
50 | 2752895.3274 | 1226227.2234
51 | 2752907.2913 | 1226230.6562
52 | 2752916.5183 | 1226233.3036
53 | 2752929.9194 | 1226237.2784
54 | 2752968.7148 | 1226254.1203
55 | 2753000.5702 | 1226270.6011
56 | 2753011.5873 | 1226277.8288
57 | 2753041.8334 | 1226300.8712
58 | 2753058.6199 | 1226317.3787
59 | 2753065.465 | 1226304.62
60 | 2753089.7471 | 1226348.4725
61 | 2753077.2024 | 1226282.7422
62 | 2753102.264 | 1226360.463
63 | 2752929.7068 | 1226477.6984
64 | 2752944.4524 | 1226460.7611
65 | 2752967.5907 | 1226438.7379
66 | 2753015.6096 | 1226411.4252
67 | 2752956.332 | 1226425.7849
68 | 2753024.3336 | 1226406.6154
69 | 2753019.9361 | 1226422.1811
70 | 2752926.2295 | 1226403.5983
71 | 2753033.9703 | 1226401.5106
72 | 2753019.5507 | 1226428.5166
73 | 2752912.8151 | 1226429.1856
74 | 2752921.3992 | 1226400.3267
75 | 2752907.508 | 1226444.1654
76 | 2752887.6436 | 1226425.434
77 | 2753077.3378 | 1226376.2352
78 | 2753096.8149 | 1226363.9109
79 | 2753122.9412 | 1226346.2042
80 | 2753137.5381 | 1226336.7157
81 | 2753132.8674 | 1226357.1016
82 | 2753147.8056 | 1226330.0415
83 | 2753142.528 | 1226365.448
84 | 2753081.43 | 1226274.8622
85 | 2753162.4166 | 1226369.4743
86 | 2753152.3361 | 1226392.4761
87 | 2753181.5158 | 1226367.1006
88 | 2753157.6552 | 1226405.5107
89 | 2753152.9668 | 1226326.6865
90 | 2753185.3897 | 1226366.2817
91 | 2753163.4981 | 1226417.7916
92 | 2753157.2132 | 1226323.9262
93 | 2753192.5229 | 1226300.8905
94 | 2753195.88 | 1226298.6935
95 | 2753184.6869 | 1226282.168
96 | 2753184.8346 | 1226275.4801
97 | 2753190.914 | 1226264.9904
98 | 2753211.6855 | 1226245.0564
99 | 2753246.1461 | 1226287.9494
100 | 2753252.9207 | 1226296.1669
101 | 2753208.1573 | 1226362.4958
102 | 2753221.1691 | 1226358.7931
103 | 2753222.6253 | 1226358.1488
104 | 2753175.5902 | 1226428.1889
105 | 2753230.818 | 1226351.5162
106 | 2753253.4319 | 1226333.1212
107 | 2753257.1652 | 1226330.0714
108 | 2753281.2793 | 1226411.9187
109 | 2753288.0866 | 1226406.3326
110 | 2753279.5189 | 1226413.3632
111 | 2753305.7892 | 1226391.8058
112 | 2753307.8007 | 1226390.1552
113 | 2753321.3034 | 1226379.0749
114 | 2753297.126 | 1226349.7669
115 | 2753353.8151 | 1226417.6257
116 | 2753286.2852 | 1226336.6256
117 | 2753338.2914 | 1226431.1807
118 | 2753272.7208 | 1226320.1827
119 | 2753329.3934 | 1226440.168
120 | 2753271.3317 | 1226318.4989
121 | 2753102.264 | 1226360.463

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.99545 | -0.087692 | 0.0004353 | 0.0001091
1 | 0.99546 | -0.087533 | 0.00063703 | 0.00015966
2 | 0.99514 | -0.093613 | 0 | 0
3 | 0.9958 | -0.080845 | 0.00083805 | 0.00021003
4 | 0.99505 | -0.095468 | 0.00087795 | 0.00022004
5 | 0.99507 | -0.095083 | 0.00046878 | 0.00011749
6 | 0.99206 | -0.15263 | 0.0010994 | 0.00027553
7 | 0.99209 | -0.1521 | 0.0050851 | 0.0012744
8 | 0.99599 | -0.077296 | 0 | 0
9 | 0.99502 | -0.096006 | 0 | 0
10 | 0.99489 | -0.09861 | 0 | 0
11 | 0.99687 | -0.06018 | 0.0010547 | 0.00026433
12 | 0.99689 | -0.059943 | 0 | 0
13 | 0.99496 | -0.097181 | 0.0011328 | 0.0002839
14 | 0.99479 | -0.10045 | 0.0010251 | 0.00025692
15 | 0.99159 | -0.1619 | 0.00092677 | 0.00023227
16 | 0.99163 | -0.16112 | 0.002222 | 0.00055689
17 | 0.99168 | -0.16002 | 0.0051735 | 0.0012966
18 | 0.99171 | -0.15962 | 0.0012808 | 0.00032101
19 | 0.99213 | -0.15139 | 0.0011733 | 0.00029406
20 | 0.99468 | -0.10223 | 0 | 0
21 | 0.99484 | -0.099049 | 0 | 0
22 | 0.99446 | -0.10643 | 0.001187 | 0.00029749
23 | 0.99463 | -0.10309 | 0.002381 | 0.00059673
24 | 0.99494 | -0.097201 | 0.0024313 | 0.00060934
25 | 0.99444 | -0.10696 | 0.00084752 | 0.00021241
26 | 0.99461 | -0.10354 | 0.0012459 | 0.00031226
27 | 0.99497 | -0.096559 | 0.0021447 | 0.0005375
28 | 0.99254 | -0.1434 | 0.0010756 | 0.00026957
29 | 0.99267 | -0.14092 | 0.0013576 | 0.00034024
30 | 0.99318 | -0.13116 | 0.001293 | 0.00032406
31 | 0.98294 | -0.32966 | 0.0093382 | 0.0023404
32 | 0.98297 | -0.32907 | 0.00073696 | 0.0001847
33 | 0.9845 | -0.29901 | 0.0009344 | 0.00023418
34 | 0.98631 | -0.26394 | 0.00026053 | 6.5294e-05
35 | 0.98631 | -0.26388 | 0.00036398 | 9.1222e-05
36 | 0.98632 | -0.26367 | 0.00050221 | 0.00012587
37 | 0.98716 | -0.24741 | 0 | 0
38 | 0.99491 | -0.098113 | 0.0019042 | 0.00047724
39 | 0.99474 | -0.10142 | 0.0010102 | 0.00025319
40 | 0.98822 | -0.22674 | 0.00073805 | 0.00018497
41 | 0.98826 | -0.22591 | 0.00044673 | 0.00011196
42 | 0.99439 | -0.10778 | 0.0017535 | 0.00043948
43 | 0.99444 | -0.10691 | 0.0030864 | 0.00077353
44 | 0.99444 | -0.10688 | 0.0028018 | 0.0007022
45 | 0.98882 | -0.21519 | 0.00075634 | 0.00018956
46 | 0.98906 | -0.21054 | 0 | 0
47 | 0.98904 | -0.21083 | 0.00054966 | 0.00013776
48 | 0.98943 | -0.20333 | 0.00050061 | 0.00012546
49 | 0.98902 | -0.21126 | 0.00049234 | 0.00012339
50 | 0.98989 | -0.19435 | 0.00045282 | 0.00011349
51 | 0.99008 | -0.19079 | 0.00025305 | 6.342e-05
52 | 0.99022 | -0.188 | 0.00043846 | 0.00010989
53 | 0.99044 | -0.18383 | 0.00033106 | 8.2972e-05
54 | 0.9911 | -0.17097 | 0.0010171 | 0.00025491
55 | 0.9917 | -0.15939 | 0.00049414 | 0.00012384
56 | 0.99193 | -0.15504 | 0.00027312 | 6.845e-05
57 | 0.99259 | -0.1423 | 0.0011596 | 0.00029062
58 | 0.99302 | -0.13393 | 0 | 0
59 | 0.99252 | -0.14368 | 0.030408 | 0.007621
60 | 0.99537 | -0.088771 | 0.031978 | 0.0080145
61 | 0.99235 | -0.14706 | 0.00035468 | 8.889e-05
62 | 0.9968 | -0.06132 | 0 | 0
63 | 0.99286 | -0.13718 | 0.00063017 | 0.00015794
64 | 0.99288 | -0.13693 | 0.00077419 | 0.00019403
65 | 0.99292 | -0.13613 | 0 | 0
66 | 0.99353 | -0.1243 | 0 | 0
67 | 0.99275 | -0.13939 | 0.0016872 | 0.00042285
68 | 0.9938 | -0.11909 | 0.0011644 | 0.00029182
69 | 0.99334 | -0.12789 | 0.00069323 | 0.00017374
70 | 0.99244 | -0.1454 | 0 | 0
71 | 0.99411 | -0.11315 | 0.0018697 | 0.0004686
72 | 0.99325 | -0.12979 | 0.0023159 | 0.00058041
73 | 0.99225 | -0.14901 | 0.0030193 | 0.00075672
74 | 0.99243 | -0.1456 | 0 | 0
75 | 0.99219 | -0.15018 | 0.0040536 | 0.0010159
76 | 0.99234 | -0.14738 | 0.0019684 | 0.00049333
77 | 0.99561 | -0.08424 | 0.010012 | 0.0025092
78 | 0.9965 | -0.066946 | 0.0070135 | 0.0017578
79 | 1 | 0 | -0.34232 | -0.086108
80 | 0.9991 | -0.01726 | 0.01582 | 0.0039648
81 | 0.99904 | -0.018288 | 0.0081352 | 0.0020389
82 | 0.99865 | -0.026033 | 0.01516 | 0.0037993
83 | 0.99748 | -0.048201 | 0 | 0
84 | 0.99229 | -0.14823 | 0.0011539 | 0.0002892
85 | 0.99582 | -0.080094 | 0.0064924 | 0.0016272
86 | 0.9963 | -0.07087 | 0.018365 | 0.0046027
87 | 0.99435 | -0.10825 | 0.016315 | 0.004089
88 | 0.99596 | -0.077446 | 0.0049544 | 0.0012417
89 | 0.9985 | -0.028815 | 0.0073591 | 0.0018444
90 | 0.99411 | -0.11287 | 0.0077338 | 0.0019383
91 | 0.99569 | -0.082672 | 0.0019001 | 0.00047622
92 | 0.99842 | -0.030452 | 0.0007881 | 0.00019752
93 | 0.99774 | -0.04351 | 0.0037718 | 0.00094531
94 | 0.99769 | -0.044488 | 0 | 0
95 | 0.99743 | -0.049357 | 0.00071677 | 0.00017964
96 | 0.99735 | -0.050906 | 0.00025202 | 6.3161e-05
97 | 0.99721 | -0.053714 | 0.0022389 | 0.00056113
98 | 0.99693 | -0.059156 | 0.0013157 | 0.00032975
99 | 0.98946 | -0.20279 | 0.0023469 | 0.00058818
100 | 0.98948 | -0.20234 | 0.001258 | 0.00031528
101 | 0.99286 | -0.13708 | 0.0017022 | 0.00042662
102 | 0.99215 | -0.15067 | 0.001906 | 0.00047769
103 | 0.99207 | -0.15224 | 0.0050721 | 0.0012712
104 | 0.9954 | -0.088206 | 0.0018421 | 0.00046166
105 | 0.99159 | -0.16154 | 0.0039406 | 0.00098761
106 | 0.99036 | -0.18526 | 0.0051066 | 0.0012798
107 | 0.99018 | -0.18875 | 0.0046501 | 0.0011654
108 | 0.98732 | -0.24429 | 0.0026668 | 0.00066836
109 | 0.98736 | -0.24355 | 0.0038003 | 0.00095245
110 | 0.98732 | -0.24437 | 0.0020335 | 0.00050965
111 | 0.98754 | -0.24007 | 0.0030282 | 0.00075894
112 | 0.98757 | -0.23953 | 0.0040329 | 0.0010107
113 | 0.98782 | -0.23467 | 0 | 0
114 | 0.98852 | -0.221 | 0.007351 | 0.0018423
115 | 0.98761 | -0.23882 | 0 | 0
116 | 0.98895 | -0.21264 | 0.0011615 | 0.00029111
117 | 0.98752 | -0.24051 | 0.0020817 | 0.00052172
118 | 0.98951 | -0.20175 | 0.0037912 | 0.00095016
119 | 0.98749 | -0.2411 | 0.0025212 | 0.00063188
120 | 0.98958 | -0.20049 | 0 | 0
121 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0068576 | -0.001715 | 0.0068576 | 0.0017151 | 5.1848e-08 | 1.6073e-08 | 0.01025 | 0.01025 | 0.01025 | 0.99545 | -0.087692 | 0.99546 | -0.087533 | 2.8158
1 | 0.0064223 | 0.0016059 | -0.0064205 | -0.0016055 | 1.8083e-06 | 4.7716e-07 | 0.0095989 | 0.0095991 | 0.0095991 | 0.99545 | -0.087692 | 0.99514 | -0.093613 | 2.6371
2 | -0.0074947 | -0.0018747 | 0.0074971 | 0.0018756 | 2.3849e-06 | 8.6721e-07 | 0.011202 | 0.011202 | 0.011202 | 0.99546 | -0.087533 | 0.9958 | -0.080845 | 3.0774
3 | 0.0039156 | 0.00098048 | -0.0039153 | -0.00098061 | 3.4583e-07 | -1.2818e-07 | 0.0058546 | 0.0058547 | 0.0058547 | 0.99514 | -0.093613 | 0.99505 | -0.095468 | 1.6084
4 | 0.0025049 | 0.00062498 | -0.0025047 | -0.0006253 | 1.7478e-07 | -3.1996e-07 | 0.0037445 | 0.0037446 | 0.0037446 | 0.99514 | -0.093613 | 0.99507 | -0.095083 | 1.0287
5 | -0.0083351 | -0.0020856 | 0.0083365 | 0.0020862 | 1.4076e-06 | 5.8596e-07 | 0.012454 | 0.012454 | 0.012454 | 0.9958 | -0.080845 | 0.99599 | -0.077296 | 3.4214
6 | 0.0030373 | 0.00076057 | -0.0030372 | -0.00076065 | 7.7742e-08 | -8.0786e-08 | 0.0045418 | 0.0045419 | 0.0045419 | 0.99505 | -0.095468 | 0.99502 | -0.096006 | 1.2478
7 | 0.0020359 | 0.00050782 | -0.0020356 | -0.00050887 | 3.4111e-07 | -1.0568e-06 | 0.0030436 | 0.0030441 | 0.0030441 | 0.99507 | -0.095083 | 0.99489 | -0.09861 | 0.83629
8 | -0.0010994 | -0.00027553 | 0.0010994 | 0.0002752 | 2.7798e-08 | -3.3423e-07 | 0.001649 | 0.0016489 | 0.001649 | 0.99206 | -0.15263 | 0.99209 | -0.1521 | 0.45302
9 | -0.0061845 | -0.0015496 | 0.0061856 | 0.0015499 | 1.1407e-06 | 2.7346e-07 | 0.0092759 | 0.0092758 | 0.0092759 | 0.99209 | -0.1521 | 0.99229 | -0.14823 | 2.5483
10 | -0.0083365 | -0.0020862 | 0.0083433 | 0.002089 | 6.7937e-06 | 2.8264e-06 | 0.012454 | 0.012453 | 0.012454 | 0.99599 | -0.077296 | 0.99687 | -0.06018 | 3.4214
11 | 0.0030372 | 0.00076065 | -0.0030371 | -0.00076083 | 1.6991e-07 | -1.7652e-07 | 0.0045419 | 0.004542 | 0.004542 | 0.99502 | -0.096006 | 0.99496 | -0.097181 | 1.2478
12 | 0.0020356 | 0.00050887 | -0.0020354 | -0.00050943 | 1.7821e-07 | -5.5178e-07 | 0.0030441 | 0.0030443 | 0.0030443 | 0.99489 | -0.09861 | 0.99479 | -0.10045 | 0.83635
13 | -0.009398 | -0.0023534 | 0.0093981 | 0.0023534 | 1.0644e-07 | 4.9314e-08 | 0.014028 | 0.014028 | 0.014028 | 0.99687 | -0.06018 | 0.99689 | -0.059943 | 3.8537
14 | -0.0093981 | -0.0023534 | 0.0093985 | 0.0023536 | 3.5188e-07 | 1.6303e-07 | 0.014028 | 0.014028 | 0.014028 | 0.99689 | -0.059943 | 0.99693 | -0.059156 | 3.8537
15 | 0.0019043 | 0.00047693 | -0.0019042 | -0.00047724 | 8.4571e-08 | -3.0698e-07 | 0.0028479 | 0.002848 | 0.002848 | 0.99496 | -0.097181 | 0.99491 | -0.098113 | 0.78241
16 | 0.0010103 | 0.00025251 | -0.0010102 | -0.00025319 | 4.6836e-08 | -6.8016e-07 | 0.0015109 | 0.0015112 | 0.0015112 | 0.99479 | -0.10045 | 0.99474 | -0.10142 | 0.41516
17 | -0.00092677 | -0.00023227 | 0.00092681 | 0.00023169 | 3.4091e-08 | -5.8458e-07 | 0.0013908 | 0.0013905 | 0.0013908 | 0.99159 | -0.1619 | 0.99163 | -0.16112 | 0.38208
18 | -0.0031488 | -0.00078858 | 0.003149 | 0.00078843 | 1.6475e-07 | -1.4845e-07 | 0.0047249 | 0.0047248 | 0.0047249 | 0.99163 | -0.16112 | 0.99168 | -0.16002 | 1.298
19 | -0.0083225 | -0.002085 | 0.0083227 | 0.0020851 | 1.5885e-07 | 6.6616e-08 | 0.012488 | 0.012488 | 0.012488 | 0.99168 | -0.16002 | 0.99171 | -0.15962 | 3.4307
20 | -0.0096035 | -0.0024061 | 0.0096073 | 0.0024079 | 3.7661e-06 | 1.786e-06 | 0.014409 | 0.014409 | 0.014409 | 0.99171 | -0.15962 | 0.99213 | -0.15139 | 3.9586
21 | -0.010781 | -0.002702 | 0.010785 | 0.002704 | 4.1047e-06 | 2.0861e-06 | 0.016169 | 0.016169 | 0.016169 | 0.99213 | -0.15139 | 0.99254 | -0.1434 | 4.442
22 | -0.002035 | -0.00050819 | 0.0020353 | 0.00050724 | 3.0761e-07 | -9.5287e-07 | 0.0030436 | 0.0030432 | 0.0030436 | 0.99468 | -0.10223 | 0.99484 | -0.099049 | 0.83616
23 | 0.002035 | 0.00050819 | -0.0020346 | -0.00050945 | 4.0592e-07 | -1.2564e-06 | 0.0030436 | 0.0030441 | 0.0030441 | 0.99468 | -0.10223 | 0.99446 | -0.10643 | 0.8363
24 | 0.011272 | 0.0028255 | -0.01127 | -0.0028244 | 2.1721e-06 | 1.1256e-06 | 0.01686 | 0.016861 | 0.016861 | 0.99484 | -0.099049 | 0.99463 | -0.10309 | 4.632
25 | -0.013308 | -0.0033328 | 0.013309 | 0.0033334 | 1.1712e-06 | 6.4719e-07 | 0.019904 | 0.019904 | 0.019904 | 0.99484 | -0.099049 | 0.99494 | -0.097201 | 5.468
26 | 0.00084754 | 0.00021195 | -0.00084752 | -0.00021241 | 2.168e-08 | -4.5258e-07 | 0.001268 | 0.0012682 | 0.0012682 | 0.99446 | -0.10643 | 0.99444 | -0.10696 | 0.3484
27 | 0.0088892 | 0.0022277 | -0.008889 | -0.0022276 | 1.8792e-07 | 8.3493e-08 | 0.013299 | 0.013299 | 0.013299 | 0.99463 | -0.10309 | 0.99461 | -0.10354 | 3.6534
28 | -0.01574 | -0.0039428 | 0.015741 | 0.003943 | 4.8079e-07 | 2.7766e-07 | 0.02354 | 0.02354 | 0.02354 | 0.99494 | -0.097201 | 0.99497 | -0.096559 | 6.467
29 | 0.0076431 | 0.0019153 | -0.0076419 | -0.0019149 | 1.2177e-06 | 4.5706e-07 | 0.011435 | 0.011435 | 0.011435 | 0.99461 | -0.10354 | 0.99444 | -0.10688 | 3.1414
30 | -0.017885 | -0.0044805 | 0.017892 | 0.0044848 | 7.1179e-06 | 4.2107e-06 | 0.026747 | 0.026747 | 0.026747 | 0.99497 | -0.096559 | 0.9954 | -0.088206 | 7.3481
31 | -0.01186 | -0.0029736 | 0.011862 | 0.0029744 | 1.4049e-06 | 7.46e-07 | 0.017781 | 0.017781 | 0.017781 | 0.99254 | -0.1434 | 0.99267 | -0.14092 | 4.885
32 | -0.013219 | -0.0033146 | 0.013225 | 0.003318 | 6.1488e-06 | 3.3951e-06 | 0.019816 | 0.019816 | 0.019816 | 0.99267 | -0.14092 | 0.99318 | -0.13116 | 5.444
33 | -0.014518 | -0.0036421 | 0.014519 | 0.0036426 | 9.4962e-07 | 5.385e-07 | 0.021753 | 0.021753 | 0.021753 | 0.99318 | -0.13116 | 0.99325 | -0.12979 | 5.9762
34 | -0.0093382 | -0.0023404 | 0.0093385 | 0.0023405 | 2.635e-07 | 1.2407e-07 | 0.014137 | 0.014137 | 0.014137 | 0.98294 | -0.32966 | 0.98297 | -0.32907 | 3.8837
35 | -0.010075 | -0.0025252 | 0.01009 | 0.0025323 | 1.4448e-05 | 7.1438e-06 | 0.015252 | 0.015251 | 0.015252 | 0.98297 | -0.32907 | 0.9845 | -0.29901 | 4.1902
36 | -0.011024 | -0.0027665 | 0.011043 | 0.0027762 | 1.8604e-05 | 9.6304e-06 | 0.016664 | 0.016663 | 0.016664 | 0.9845 | -0.29901 | 0.98632 | -0.26367 | 4.578
37 | -0.00026053 | -6.5294e-05 | 0.00026053 | 6.513e-05 | 7.4691e-10 | -1.6409e-07 | 0.00039305 | 0.00039299 | 0.00039305 | 0.98631 | -0.26394 | 0.98631 | -0.26388 | 0.10798
38 | -0.0006245 | -0.00015635 | 0.00062451 | 0.00015613 | 5.9997e-09 | -2.2623e-07 | 0.00094211 | 0.00094203 | 0.00094211 | 0.98631 | -0.26388 | 0.98632 | -0.26367 | 0.25882
39 | -0.01217 | -0.0030581 | 0.012179 | 0.0030632 | 9.4521e-06 | 5.0945e-06 | 0.018363 | 0.018362 | 0.018363 | 0.98632 | -0.26367 | 0.98716 | -0.24741 | 5.0447
40 | -0.012179 | -0.0030632 | 0.012191 | 0.0030697 | 1.2038e-05 | 6.4858e-06 | 0.018362 | 0.018362 | 0.018362 | 0.98716 | -0.24741 | 0.98822 | -0.22674 | 5.0446
41 | -0.012929 | -0.0032547 | 0.01293 | 0.003255 | 5.1487e-07 | 2.8313e-07 | 0.019473 | 0.019473 | 0.019473 | 0.98822 | -0.22674 | 0.98826 | -0.22591 | 5.3498
42 | -0.013376 | -0.0033669 | 0.013383 | 0.0033708 | 6.8578e-06 | 3.8113e-06 | 0.020146 | 0.020146 | 0.020146 | 0.98826 | -0.22591 | 0.98882 | -0.21519 | 5.5346
43 | -0.0017535 | -0.00043948 | 0.0017536 | 0.00043916 | 7.3194e-08 | -3.2093e-07 | 0.002624 | 0.0026239 | 0.002624 | 0.99439 | -0.10778 | 0.99444 | -0.10691 | 0.72088
44 | -0.0048401 | -0.0012127 | 0.0048401 | 0.0012127 | 5.3245e-09 | -1.044e-10 | 0.0072422 | 0.0072422 | 0.0072422 | 0.99444 | -0.10691 | 0.99444 | -0.10688 | 1.9896
45 | -0.01414 | -0.0035603 | 0.014143 | 0.0035621 | 3.1428e-06 | 1.774e-06 | 0.021284 | 0.021284 | 0.021284 | 0.98882 | -0.21519 | 0.98906 | -0.21054 | 5.8472
46 | 0.001042 | 0.00026033 | -0.001042 | -0.00026053 | 1.4477e-08 | -1.9239e-07 | 0.0015674 | 0.0015675 | 0.0015675 | 0.98906 | -0.21054 | 0.98904 | -0.21083 | 0.43063
47 | -0.015185 | -0.0038224 | 0.01519 | 0.0038254 | 5.2334e-06 | 3.0063e-06 | 0.022851 | 0.022851 | 0.022851 | 0.98906 | -0.21054 | 0.98943 | -0.20333 | 6.2778
48 | 0.00049235 | 0.00012277 | -0.00049234 | -0.00012339 | 1.0118e-08 | -6.2477e-07 | 0.00074052 | 0.00074074 | 0.00074074 | 0.98904 | -0.21083 | 0.98902 | -0.21126 | 0.2035
49 | -0.015691 | -0.0039509 | 0.015697 | 0.0039548 | 6.7385e-06 | 3.8982e-06 | 0.023604 | 0.023604 | 0.023604 | 0.98943 | -0.20333 | 0.98989 | -0.19435 | 6.4846
50 | -0.01615 | -0.0040683 | 0.016153 | 0.0040699 | 2.7526e-06 | 1.6016e-06 | 0.024284 | 0.024284 | 0.024284 | 0.98989 | -0.19435 | 0.99008 | -0.19079 | 6.6715
51 | -0.016406 | -0.0041333 | 0.016408 | 0.0041346 | 2.1899e-06 | 1.2781e-06 | 0.024665 | 0.024665 | 0.024665 | 0.99008 | -0.19079 | 0.99022 | -0.188 | 6.776
52 | -0.016847 | -0.0042445 | 0.01685 | 0.0042464 | 3.3633e-06 | 1.9725e-06 | 0.025323 | 0.025323 | 0.025323 | 0.99022 | -0.188 | 0.99044 | -0.18383 | 6.957
53 | -0.017181 | -0.0043294 | 0.017192 | 0.0043356 | 1.0574e-05 | 6.2227e-06 | 0.025821 | 0.025821 | 0.025821 | 0.99044 | -0.18383 | 0.9911 | -0.17097 | 7.0936
54 | -0.018209 | -0.0045905 | 0.018219 | 0.0045965 | 1.0094e-05 | 5.9962e-06 | 0.027348 | 0.027347 | 0.027348 | 0.9911 | -0.17097 | 0.9917 | -0.15939 | 7.5131
55 | -0.018713 | -0.0047204 | 0.018717 | 0.0047227 | 3.8985e-06 | 2.325e-06 | 0.028089 | 0.028089 | 0.028089 | 0.9917 | -0.15939 | 0.99193 | -0.15504 | 7.7167
56 | -0.01899 | -0.0047912 | 0.019002 | 0.0047981 | 1.1591e-05 | 6.9263e-06 | 0.028499 | 0.028498 | 0.028499 | 0.99193 | -0.15504 | 0.99259 | -0.1423 | 7.8293
57 | -0.020161 | -0.0050887 | 0.020169 | 0.0050936 | 8.0927e-06 | 4.8741e-06 | 0.030237 | 0.030237 | 0.030237 | 0.99259 | -0.1423 | 0.99302 | -0.13393 | 8.3068
58 | 0.038122 | 0.0095608 | -0.038104 | -0.0095496 | 1.7719e-05 | 1.1153e-05 | 0.057127 | 0.057127 | 0.057127 | 0.99302 | -0.13393 | 0.99252 | -0.14368 | 15.6941
59 | -0.058291 | -0.014654 | 0.058417 | 0.014734 | 0.00012598 | 8.0057e-05 | 0.087363 | 0.087363 | 0.087363 | 0.99302 | -0.13393 | 0.99537 | -0.088771 | 24.0009
60 | 0.0076959 | 0.0019286 | -0.0076947 | -0.0019282 | 1.2394e-06 | 4.7242e-07 | 0.011538 | 0.011538 | 0.011538 | 0.99252 | -0.14368 | 0.99235 | -0.14706 | 3.1698
61 | -0.090395 | -0.022749 | 0.090514 | 0.022825 | 0.00011876 | 7.578e-05 | 0.13517 | 0.13517 | 0.13517 | 0.99537 | -0.088771 | 0.9968 | -0.06132 | 37.1342
62 | 0.00734 | 0.0018393 | -0.0073396 | -0.0018391 | 4.0622e-07 | 1.4446e-07 | 0.011006 | 0.011006 | 0.011006 | 0.99235 | -0.14706 | 0.99229 | -0.14823 | 3.0237
63 | -0.14036 | -0.035366 | 0.14078 | 0.03563 | 0.00041303 | 0.00026401 | 0.2096 | 0.2096 | 0.2096 | 0.9968 | -0.06132 | 1 | 0 | 57.5821
64 | 0.049848 | 0.012541 | -0.049835 | -0.012533 | 1.3396e-05 | 8.4895e-06 | 0.074431 | 0.074431 | 0.074431 | 0.9968 | -0.06132 | 0.9965 | -0.066946 | 20.448
65 | -0.00063017 | -0.00015794 | 0.00063018 | 0.00015765 | 7.5219e-09 | -2.8605e-07 | 0.00094445 | 0.00094435 | 0.00094445 | 0.99286 | -0.13718 | 0.99288 | -0.13693 | 0.25946
66 | -0.0014044 | -0.00035168 | 0.0014044 | 0.0003513 | 5.3165e-08 | -3.7997e-07 | 0.0021046 | 0.0021045 | 0.0021046 | 0.99288 | -0.13693 | 0.99292 | -0.13613 | 0.57819
67 | -0.012139 | -0.0030419 | 0.012146 | 0.0030455 | 6.8434e-06 | 3.6661e-06 | 0.018191 | 0.018191 | 0.018191 | 0.99292 | -0.13613 | 0.99353 | -0.1243 | 4.9976
68 | 0.010734 | 0.0026906 | -0.010733 | -0.0026897 | 1.6655e-06 | 8.44e-07 | 0.016087 | 0.016087 | 0.016087 | 0.99292 | -0.13613 | 0.99275 | -0.13939 | 4.4195
69 | -0.029679 | -0.0074449 | 0.029686 | 0.0074495 | 7.3825e-06 | 4.5958e-06 | 0.044452 | 0.044452 | 0.044452 | 0.99353 | -0.1243 | 0.9938 | -0.11909 | 12.2122
70 | 0.017533 | 0.0043994 | -0.01753 | -0.0043976 | 2.9983e-06 | 1.7688e-06 | 0.026261 | 0.026261 | 0.026261 | 0.99353 | -0.1243 | 0.99334 | -0.12789 | 7.2146
71 | 0.0090455 | 0.0022669 | -0.0090429 | -0.0022657 | 2.5888e-06 | 1.1714e-06 | 0.013558 | 0.013558 | 0.013558 | 0.99275 | -0.13939 | 0.99244 | -0.1454 | 3.7248
72 | -0.03085 | -0.0077414 | 0.030859 | 0.0077468 | 8.7271e-06 | 5.444e-06 | 0.046196 | 0.046196 | 0.046196 | 0.9938 | -0.11909 | 0.99411 | -0.11315 | 12.6911
73 | 0.016837 | 0.0042239 | -0.016835 | -0.004223 | 1.5256e-06 | 8.9361e-07 | 0.025223 | 0.025223 | 0.025223 | 0.99334 | -0.12789 | 0.99325 | -0.12979 | 6.9293
74 | 0.0070744 | 0.001773 | -0.0070731 | -0.0017726 | 1.2189e-06 | 4.0686e-07 | 0.010607 | 0.010607 | 0.010607 | 0.99244 | -0.1454 | 0.99225 | -0.14901 | 2.914
75 | 0.0019686 | 0.00049271 | -0.0019686 | -0.00049277 | 1.9017e-08 | -6.3058e-08 | 0.0029514 | 0.0029514 | 0.0029514 | 0.99244 | -0.1454 | 0.99243 | -0.1456 | 0.81082
76 | -0.032729 | -0.0082154 | 0.032774 | 0.0082437 | 4.5203e-05 | 2.8278e-05 | 0.048994 | 0.048994 | 0.048994 | 0.99411 | -0.11315 | 0.99561 | -0.08424 | 13.46
77 | 0.0040538 | 0.0010159 | -0.0040536 | -0.0010159 | 2.257e-07 | -6.5897e-08 | 0.0060792 | 0.0060793 | 0.0060793 | 0.99225 | -0.14901 | 0.99219 | -0.15018 | 1.6701
78 | 0.0019686 | 0.00049277 | -0.0019684 | -0.00049333 | 1.6717e-07 | -5.5419e-07 | 0.0029514 | 0.0029516 | 0.0029516 | 0.99243 | -0.1456 | 0.99234 | -0.14738 | 0.81088
79 | -0.042786 | -0.010753 | 0.042821 | 0.010775 | 3.5356e-05 | 2.2328e-05 | 0.063958 | 0.063958 | 0.063958 | 0.99561 | -0.08424 | 0.9965 | -0.066946 | 17.5708
80 | 0.05691 | 0.014294 | -0.056863 | -0.014264 | 4.683e-05 | 2.9743e-05 | 0.084693 | 0.084693 | 0.084693 | 1 | 0 | 0.9991 | -0.01726 | 23.2674
81 | 0.14299 | 0.036184 | -0.14286 | -0.036104 | 0.00012539 | 7.986e-05 | 0.21289 | 0.21289 | 0.21289 | 1 | 0 | 0.99904 | -0.018288 | 29.2435
82 | 0.041043 | 0.010299 | -0.041026 | -0.010288 | 1.7162e-05 | 1.0823e-05 | 0.061132 | 0.061132 | 0.061132 | 0.9991 | -0.01726 | 0.99865 | -0.026033 | 16.7945
83 | 0.13473 | 0.034065 | -0.13454 | -0.033942 | 0.00019299 | 0.00012335 | 0.20078 | 0.20078 | 0.20078 | 0.99904 | -0.018288 | 0.99748 | -0.048201 | 55.1581
84 | 0.025866 | 0.006489 | -0.025863 | -0.0064869 | 3.4294e-06 | 2.1143e-06 | 0.038544 | 0.038544 | 0.038544 | 0.99865 | -0.026033 | 0.9985 | -0.028815 | 10.589
85 | 0.089514 | 0.022632 | -0.089377 | -0.022545 | 0.0001367 | 8.7219e-05 | 0.1336 | 0.1336 | 0.1336 | 0.99748 | -0.048201 | 0.99582 | -0.080094 | 36.7046
86 | 0.045021 | 0.011309 | -0.044973 | -0.011279 | 4.8649e-05 | 3.076e-05 | 0.067171 | 0.067171 | 0.067171 | 0.99748 | -0.048201 | 0.9963 | -0.07087 | 18.4536
87 | 0.082885 | 0.020918 | -0.082773 | -0.020847 | 0.00011159 | 7.1169e-05 | 0.1239 | 0.1239 | 0.1239 | 0.99582 | -0.080094 | 0.99435 | -0.10825 | 34.0394
88 | 0.026608 | 0.0066759 | -0.026599 | -0.0066707 | 8.3396e-06 | 5.1541e-06 | 0.039742 | 0.039742 | 0.039742 | 0.9963 | -0.07087 | 0.99596 | -0.077446 | 10.9182
89 | 0.066458 | 0.016758 | -0.066443 | -0.016748 | 1.4697e-05 | 9.3546e-06 | 0.099488 | 0.099488 | 0.099488 | 0.99435 | -0.10825 | 0.99411 | -0.11287 | 27.3319
90 | 0.021645 | 0.005429 | -0.02164 | -0.0054258 | 5.3901e-06 | 3.2709e-06 | 0.03234 | 0.03234 | 0.03234 | 0.99596 | -0.077446 | 0.99569 | -0.082672 | 8.8847
91 | 0.018504 | 0.0046425 | -0.018502 | -0.0046416 | 1.4443e-06 | 8.5814e-07 | 0.027577 | 0.027577 | 0.027577 | 0.9985 | -0.028815 | 0.99842 | -0.030452 | 7.5761
92 | 0.058709 | 0.01481 | -0.058641 | -0.014767 | 6.7969e-05 | 4.3197e-05 | 0.087912 | 0.087912 | 0.087912 | 0.99411 | -0.11287 | 0.99286 | -0.13708 | 24.1517
93 | 0.01974 | 0.0049495 | -0.019734 | -0.0049464 | 5.2046e-06 | 3.1236e-06 | 0.029501 | 0.029501 | 0.029501 | 0.99569 | -0.082672 | 0.9954 | -0.088206 | 8.1046
94 | 0.017714 | 0.0044441 | -0.017703 | -0.0044376 | 1.1021e-05 | 6.5024e-06 | 0.026402 | 0.026403 | 0.026403 | 0.99842 | -0.030452 | 0.99774 | -0.04351 | 7.2534
95 | 0.013931 | 0.0034923 | -0.013931 | -0.0034919 | 6.495e-07 | 3.6328e-07 | 0.020777 | 0.020777 | 0.020777 | 0.99774 | -0.04351 | 0.99769 | -0.044488 | 5.708
96 | 0.013931 | 0.0034919 | -0.013927 | -0.0034901 | 3.2312e-06 | 1.8074e-06 | 0.020777 | 0.020777 | 0.020777 | 0.99769 | -0.044488 | 0.99743 | -0.049357 | 5.7081
97 | 0.013211 | 0.0033105 | -0.01321 | -0.00331 | 9.7435e-07 | 5.3628e-07 | 0.019708 | 0.019708 | 0.019708 | 0.99743 | -0.049357 | 0.99735 | -0.050906 | 5.4143
98 | 0.012958 | 0.0032468 | -0.012956 | -0.0032459 | 1.7329e-06 | 9.477e-07 | 0.019332 | 0.019332 | 0.019332 | 0.99735 | -0.050906 | 0.99721 | -0.053714 | 5.311
99 | 0.010717 | 0.0026847 | -0.010714 | -0.0026833 | 2.777e-06 | 1.3996e-06 | 0.015991 | 0.015991 | 0.015991 | 0.99721 | -0.053714 | 0.99693 | -0.059156 | 4.3932
100 | -0.0023469 | -0.00058818 | 0.0023469 | 0.00058807 | 4.9746e-08 | -1.0496e-07 | 0.0035294 | 0.0035293 | 0.0035294 | 0.98946 | -0.20279 | 0.98948 | -0.20234 | 0.9696
101 | -0.0036049 | -0.00090335 | 0.0036052 | 0.00090318 | 3.1896e-07 | -1.6767e-07 | 0.0054211 | 0.005421 | 0.0054211 | 0.98948 | -0.20234 | 0.98958 | -0.20049 | 1.4893
102 | 0.056939 | 0.01434 | -0.056902 | -0.014317 | 3.6965e-05 | 2.3483e-05 | 0.085361 | 0.085361 | 0.085361 | 0.99286 | -0.13708 | 0.99215 | -0.15067 | 23.4508
103 | 0.054996 | 0.013839 | -0.054992 | -0.013836 | 4.1406e-06 | 2.629e-06 | 0.082502 | 0.082502 | 0.082502 | 0.99215 | -0.15067 | 0.99207 | -0.15224 | 22.6655
104 | 0.04992 | 0.012565 | -0.049898 | -0.012551 | 2.2172e-05 | 1.4054e-05 | 0.074895 | 0.074895 | 0.074895 | 0.99207 | -0.15224 | 0.99159 | -0.16154 | 20.5755
105 | 0.045957 | 0.011564 | -0.045905 | -0.011531 | 5.2017e-05 | 3.2915e-05 | 0.068981 | 0.068981 | 0.068981 | 0.99159 | -0.16154 | 0.99036 | -0.18526 | 18.9509
106 | 0.040799 | 0.010251 | -0.040792 | -0.010247 | 6.7949e-06 | 4.2867e-06 | 0.061309 | 0.061309 | 0.061309 | 0.99036 | -0.18526 | 0.99018 | -0.18875 | 16.8431
107 | 0.036142 | 0.0090811 | -0.036122 | -0.0090684 | 2.0241e-05 | 1.2719e-05 | 0.054321 | 0.054321 | 0.054321 | 0.99018 | -0.18875 | 0.98958 | -0.20049 | 14.9233
108 | -0.0047003 | -0.001178 | 0.0047005 | 0.001178 | 1.6571e-07 | -6.5657e-09 | 0.007084 | 0.0070839 | 0.007084 | 0.98732 | -0.24429 | 0.98736 | -0.24355 | 1.9461
109 | 0.0020335 | 0.00050963 | -0.0020335 | -0.00050965 | 8.021e-09 | -2.3989e-08 | 0.0030648 | 0.0030648 | 0.0030648 | 0.98732 | -0.24429 | 0.98732 | -0.24437 | 0.84198
110 | -0.0085008 | -0.0021304 | 0.0085022 | 0.002131 | 1.4094e-06 | 6.091e-07 | 0.012811 | 0.012811 | 0.012811 | 0.98736 | -0.24355 | 0.98754 | -0.24007 | 3.5196
111 | -0.01153 | -0.00289 | 0.011531 | 0.0028901 | 2.9454e-07 | 1.5521e-07 | 0.017374 | 0.017374 | 0.017374 | 0.98754 | -0.24007 | 0.98757 | -0.23953 | 4.7731
112 | -0.015564 | -0.0039009 | 0.015567 | 0.003903 | 3.6021e-06 | 2.0818e-06 | 0.023451 | 0.02345 | 0.023451 | 0.98757 | -0.23953 | 0.98782 | -0.23467 | 6.4425
113 | -0.020172 | -0.0050564 | 0.020185 | 0.0050643 | 1.3155e-05 | 7.9324e-06 | 0.030386 | 0.030386 | 0.030386 | 0.98782 | -0.23467 | 0.98852 | -0.221 | 8.3478
114 | 0.0046043 | 0.0011534 | -0.0046034 | -0.0011535 | 9.0862e-07 | -6.3162e-08 | 0.0069356 | 0.0069358 | 0.0069358 | 0.98782 | -0.23467 | 0.98761 | -0.23882 | 1.9054
115 | -0.027536 | -0.0069066 | 0.027547 | 0.0069134 | 1.0977e-05 | 6.8066e-06 | 0.041451 | 0.041451 | 0.041451 | 0.98852 | -0.221 | 0.98895 | -0.21264 | 11.3877
116 | 0.0046034 | 0.0011535 | -0.004603 | -0.0011535 | 3.7178e-07 | -2.5752e-08 | 0.0069358 | 0.0069359 | 0.0069359 | 0.98761 | -0.23882 | 0.98752 | -0.24051 | 1.9055
117 | -0.028708 | -0.0072046 | 0.028723 | 0.0072138 | 1.4917e-05 | 9.2732e-06 | 0.043199 | 0.043199 | 0.043199 | 0.98895 | -0.21264 | 0.98951 | -0.20175 | 11.8678
118 | 0.0025213 | 0.00063176 | -0.0025212 | -0.00063188 | 7.023e-08 | -1.2105e-07 | 0.0037991 | 0.0037992 | 0.0037992 | 0.98752 | -0.24051 | 0.98749 | -0.2411 | 1.0437
119 | -0.032514 | -0.008164 | 0.032516 | 0.0081652 | 1.9573e-06 | 1.2246e-06 | 0.0489 | 0.0489 | 0.0489 | 0.98951 | -0.20175 | 0.98958 | -0.20049 | 13.4341

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.34232 | 0.086108

## res_load
| p_mw | q_mvar
0 | 0.0004353 | 0.0001091
1 | 0.00063703 | 0.00015966
2 | 0.00083805 | 0.00021003
3 | 0.00087795 | 0.00022004
4 | 0.00046878 | 0.00011749
5 | 0.0010994 | 0.00027553
6 | 0.0050851 | 0.0012744
7 | 0.0010547 | 0.00026433
8 | 0.0011328 | 0.0002839
9 | 0.0010251 | 0.00025692
10 | 0.00092677 | 0.00023227
11 | 0.002222 | 0.00055689
12 | 0.0051735 | 0.0012966
13 | 0.0012808 | 0.00032101
14 | 0.0011733 | 0.00029406
15 | 0.001187 | 0.00029749
16 | 0.002381 | 0.00059673
17 | 0.0024313 | 0.00060934
18 | 0.00084752 | 0.00021241
19 | 0.0012459 | 0.00031226
20 | 0.0021447 | 0.0005375
21 | 0.0010756 | 0.00026957
22 | 0.0013576 | 0.00034024
23 | 0.001293 | 0.00032406
24 | 0.0093382 | 0.0023404
25 | 0.00073696 | 0.0001847
26 | 0.0009344 | 0.00023418
27 | 0.00026053 | 6.5294e-05
28 | 0.00036398 | 9.1222e-05
29 | 0.00050221 | 0.00012587
30 | 0.0019042 | 0.00047724
31 | 0.0010102 | 0.00025319
32 | 0.00073805 | 0.00018497
33 | 0.00044673 | 0.00011196
34 | 0.0017535 | 0.00043948
35 | 0.0030864 | 0.00077353
36 | 0.0028018 | 0.0007022
37 | 0.00075634 | 0.00018956
38 | 0.00054966 | 0.00013776
39 | 0.00050061 | 0.00012546
40 | 0.00049234 | 0.00012339
41 | 0.00045282 | 0.00011349
42 | 0.00025305 | 6.342e-05
43 | 0.00043846 | 0.00010989
44 | 0.00033106 | 8.2972e-05
45 | 0.0010171 | 0.00025491
46 | 0.00049414 | 0.00012384
47 | 0.00027312 | 6.845e-05
48 | 0.0011596 | 0.00029062
49 | 0.030408 | 0.007621
50 | 0.031978 | 0.0080145
51 | 0.00035468 | 8.889e-05
52 | 0.00063017 | 0.00015794
53 | 0.00077419 | 0.00019403
54 | 0.0016872 | 0.00042285
55 | 0.0011644 | 0.00029182
56 | 0.00069323 | 0.00017374
57 | 0.0018697 | 0.0004686
58 | 0.0023159 | 0.00058041
59 | 0.0030193 | 0.00075672
60 | 0.0040536 | 0.0010159
61 | 0.0019684 | 0.00049333
62 | 0.010012 | 0.0025092
63 | 0.0070135 | 0.0017578
64 | 0.01582 | 0.0039648
65 | 0.0081352 | 0.0020389
66 | 0.01516 | 0.0037993
67 | 0.0011539 | 0.0002892
68 | 0.0064924 | 0.0016272
69 | 0.018365 | 0.0046027
70 | 0.016315 | 0.004089
71 | 0.0049544 | 0.0012417
72 | 0.0073591 | 0.0018444
73 | 0.0077338 | 0.0019383
74 | 0.0019001 | 0.00047622
75 | 0.0007881 | 0.00019752
76 | 0.0037718 | 0.00094531
77 | 0.00071677 | 0.00017964
78 | 0.00025202 | 6.3161e-05
79 | 0.0022389 | 0.00056113
80 | 0.0013157 | 0.00032975
81 | 0.0023469 | 0.00058818
82 | 0.001258 | 0.00031528
83 | 0.0017022 | 0.00042662
84 | 0.001906 | 0.00047769
85 | 0.0050721 | 0.0012712
86 | 0.0018421 | 0.00046166
87 | 0.0039406 | 0.00098761
88 | 0.0051066 | 0.0012798
89 | 0.0046501 | 0.0011654
90 | 0.0026668 | 0.00066836
91 | 0.0038003 | 0.00095245
92 | 0.0020335 | 0.00050965
93 | 0.0030282 | 0.00075894
94 | 0.0040329 | 0.0010107
95 | 0.007351 | 0.0018423
96 | 0.0011615 | 0.00029111
97 | 0.0020817 | 0.00052172
98 | 0.0037912 | 0.00095016
99 | 0.0025212 | 0.00063188

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1