## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3379-6_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3379-6_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3379-6_0_3_node_109 | 0.4 | n |  | TRUE
3 | bus_LV_3379-6_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3379-6_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3379-6_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3379-6_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_3379-6_0_3_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_3379-6_0_3_node_12 | 0.4 | n |  | TRUE
9 | bus_LV_3379-6_0_3_node_11 | 0.4 | n |  | TRUE
10 | bus_LV_3379-6_0_3_node_10 | 0.4 | n |  | TRUE
11 | bus_LV_3379-6_0_3_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_3379-6_0_3_node_9 | 0.4 | n |  | TRUE
13 | bus_LV_3379-6_0_3_node_15 | 0.4 | n |  | TRUE
14 | bus_LV_3379-6_0_3_node_19 | 0.4 | n |  | TRUE
15 | bus_LV_3379-6_0_3_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_3379-6_0_3_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_3379-6_0_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_3379-6_0_3_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_3379-6_0_3_node_17 | 0.4 | n |  | TRUE
20 | bus_LV_3379-6_0_3_node_106 | 0.4 | n |  | TRUE
21 | bus_LV_3379-6_0_3_node_104 | 0.4 | n |  | TRUE
22 | bus_LV_3379-6_0_3_node_14 | 0.4 | n |  | TRUE
23 | bus_LV_3379-6_0_3_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_3379-6_0_3_node_27 | 0.4 | n |  | TRUE
25 | bus_LV_3379-6_0_3_node_28 | 0.4 | n |  | TRUE
26 | bus_LV_3379-6_0_3_node_98 | 0.4 | n |  | TRUE
27 | bus_LV_3379-6_0_3_node_111 | 0.4 | n |  | TRUE
28 | bus_LV_3379-6_0_3_node_96 | 0.4 | n |  | TRUE
29 | bus_LV_3379-6_0_3_node_94 | 0.4 | n |  | TRUE
30 | bus_LV_3379-6_0_3_node_103 | 0.4 | n |  | TRUE
31 | bus_LV_3379-6_0_3_node_20 | 0.4 | n |  | TRUE
32 | bus_LV_3379-6_0_3_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_3379-6_0_3_node_23 | 0.4 | n |  | TRUE
34 | bus_LV_3379-6_0_3_node_75 | 0.4 | n |  | TRUE
35 | bus_LV_3379-6_0_3_node_22 | 0.4 | n |  | TRUE
36 | bus_LV_3379-6_0_3_node_65 | 0.4 | n |  | TRUE
37 | bus_LV_3379-6_0_3_node_64 | 0.4 | n |  | TRUE
38 | bus_LV_3379-6_0_3_node_24 | 0.4 | n |  | TRUE
39 | bus_LV_3379-6_0_3_node_63 | 0.4 | n |  | TRUE
40 | bus_LV_3379-6_0_3_node_80 | 0.4 | n |  | TRUE
41 | bus_LV_3379-6_0_3_node_76 | 0.4 | n |  | TRUE
42 | bus_LV_3379-6_0_3_node_56 | 0.4 | n |  | TRUE
43 | bus_LV_3379-6_0_3_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_3379-6_0_3_node_81 | 0.4 | n |  | TRUE
45 | bus_LV_3379-6_0_3_node_29 | 0.4 | n |  | TRUE
46 | bus_LV_3379-6_0_3_node_105 | 0.4 | n |  | TRUE
47 | bus_LV_3379-6_0_3_node_101 | 0.4 | n |  | TRUE
48 | bus_LV_3379-6_0_3_node_30 | 0.4 | n |  | TRUE
49 | bus_LV_3379-6_0_3_node_31 | 0.4 | n |  | TRUE
50 | bus_LV_3379-6_0_3_node_32 | 0.4 | n |  | TRUE
51 | bus_LV_3379-6_0_3_node_33 | 0.4 | n |  | TRUE
52 | bus_LV_3379-6_0_3_node_34 | 0.4 | n |  | TRUE
53 | bus_LV_3379-6_0_3_node_78 | 0.4 | n |  | TRUE
54 | bus_LV_3379-6_0_3_node_55 | 0.4 | n |  | TRUE
55 | bus_LV_3379-6_0_3_node_107 | 0.4 | n |  | TRUE
56 | bus_LV_3379-6_0_3_node_108 | 0.4 | n |  | TRUE
57 | bus_LV_3379-6_0_3_node_74 | 0.4 | n |  | TRUE
58 | bus_LV_3379-6_0_3_node_35 | 0.4 | n |  | TRUE
59 | bus_LV_3379-6_0_3_node_36 | 0.4 | n |  | TRUE
60 | bus_LV_3379-6_0_3_node_38 | 0.4 | n |  | TRUE
61 | bus_LV_3379-6_0_3_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_3379-6_0_3_node_39 | 0.4 | n |  | TRUE
63 | bus_LV_3379-6_0_3_node_40 | 0.4 | n |  | TRUE
64 | bus_LV_3379-6_0_3_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_3379-6_0_3_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_3379-6_0_3_node_50 | 0.4 | n |  | TRUE
67 | bus_LV_3379-6_0_3_node_58 | 0.4 | n |  | TRUE
68 | bus_LV_3379-6_0_3_node_72 | 0.4 | n |  | TRUE
69 | bus_LV_3379-6_0_3_node_61 | 0.4 | n |  | TRUE
70 | bus_LV_3379-6_0_3_node_48 | 0.4 | n |  | TRUE
71 | bus_LV_3379-6_0_3_node_42 | 0.4 | n |  | TRUE
72 | bus_LV_3379-6_0_3_node_43 | 0.4 | n |  | TRUE
73 | bus_LV_3379-6_0_3_node_44 | 0.4 | n |  | TRUE
74 | bus_LV_3379-6_0_3_node_45 | 0.4 | n |  | TRUE
75 | bus_LV_3379-6_0_3_node_46 | 0.4 | n |  | TRUE
76 | bus_LV_3379-6_0_3_node_47 | 0.4 | n |  | TRUE
77 | bus_LV_3379-6_0_3_node_77 | 0.4 | n |  | TRUE
78 | bus_LV_3379-6_0_3_node_79 | 0.4 | n |  | TRUE
79 | bus_LV_3379-6_0_3_node_49 | 0.4 | n |  | TRUE
80 | bus_LV_3379-6_0_3_node_60 | 0.4 | n |  | TRUE
81 | bus_LV_3379-6_0_3_node_52 | 0.4 | n |  | TRUE
82 | bus_LV_3379-6_0_3_node_51 | 0.4 | n |  | TRUE
83 | bus_LV_3379-6_0_3_node_54 | 0.4 | n |  | TRUE
84 | bus_LV_3379-6_0_3_node_62 | 0.4 | n |  | TRUE
85 | bus_LV_3379-6_0_3_node_59 | 0.4 | n |  | TRUE
86 | bus_LV_3379-6_0_3_node_82 | 0.4 | n |  | TRUE
87 | bus_LV_3379-6_0_3_node_67 | 0.4 | n |  | TRUE
88 | bus_LV_3379-6_0_3_node_71 | 0.4 | n |  | TRUE
89 | bus_LV_3379-6_0_3_node_66 | 0.4 | n |  | TRUE
90 | bus_LV_3379-6_0_3_node_69 | 0.4 | n |  | TRUE
91 | bus_LV_3379-6_0_3_node_68 | 0.4 | n |  | TRUE
92 | bus_LV_3379-6_0_3_node_89 | 0.4 | n |  | TRUE
93 | bus_LV_3379-6_0_3_node_83 | 0.4 | n |  | TRUE
94 | bus_LV_3379-6_0_3_node_84 | 0.4 | n |  | TRUE
95 | bus_LV_3379-6_0_3_node_86 | 0.4 | n |  | TRUE
96 | bus_LV_3379-6_0_3_node_87 | 0.4 | n |  | TRUE
97 | bus_LV_3379-6_0_3_node_88 | 0.4 | n |  | TRUE
98 | bus_LV_3379-6_0_3_node_112 | 0.4 | n |  | TRUE
99 | bus_LV_3379-6_0_3_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_3379-6_0_3_node_113 | 0.4 | n |  | TRUE
101 | bus_LV_3379-6_0_3_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_3379-6_0_3_node_91 | 0.4 | n |  | TRUE
103 | bus_LV_3379-6_0_3_node_92 | 0.4 | n |  | TRUE
104 | bus_LV_3379-6_0_3_node_93 | 0.4 | n |  | TRUE
105 | bus_LV_3379-6_0_3_node_97 | 0.4 | n |  | TRUE
106 | bus_LV_3379-6_0_3_node_99 | 0.4 | n |  | TRUE
107 | bus_LV_3379-6_0_3_node_95 | 0.4 | n |  | TRUE
108 | bus_LV_3379-6_0_3_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_3379-6_0_3_node_102 | 0.4 | n |  | TRUE
110 | bus_MV_153_0_node_108 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3379-6_0_3_load_0 | 0 | 0.0033132 | 0.00083038 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3379-6_0_3_load_109 | 2 | 0.00054319 | 0.00013614 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3379-6_0_3_load_3 | 3 | 0.0023271 | 0.00058321 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3379-6_0_3_load_4 | 4 | 0.0009823 | 0.00024619 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3379-6_0_3_load_6 | 6 | 0.0048038 | 0.0012039 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3379-6_0_3_load_12 | 8 | 0.0018986 | 0.00047582 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3379-6_0_3_load_11 | 9 | 0.004439 | 0.0011125 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3379-6_0_3_load_10 | 10 | 0.001728 | 0.00043307 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3379-6_0_3_load_15 | 13 | 0.0026294 | 0.000659 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3379-6_0_3_load_19 | 14 | 0.01579 | 0.0039573 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3379-6_0_3_load_25 | 15 | 0.0072294 | 0.0018119 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3379-6_0_3_load_13 | 16 | 0.021001 | 0.0052634 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3379-6_0_3_load_18 | 17 | 0.043641 | 0.010938 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3379-6_0_3_load_26 | 18 | 0.0016647 | 0.0004172 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3379-6_0_3_load_106 | 20 | 0.0099236 | 0.0024871 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3379-6_0_3_load_104 | 21 | 0.0053297 | 0.0013357 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3379-6_0_3_load_14 | 22 | 0.0068887 | 0.0017265 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3379-6_0_3_load_16 | 23 | 0.0035479 | 0.00088919 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3379-6_0_3_load_27 | 24 | 0.011527 | 0.0028891 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3379-6_0_3_load_28 | 25 | 0.0037442 | 0.00093839 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3379-6_0_3_load_111 | 27 | 0.0092827 | 0.0023265 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3379-6_0_3_load_94 | 29 | 0.0054793 | 0.0013732 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3379-6_0_3_load_103 | 30 | 0.0061 | 0.0015288 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3379-6_0_3_load_75 | 34 | 0.0021858 | 0.00054782 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3379-6_0_3_load_64 | 37 | 0.0017132 | 0.00042936 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3379-6_0_3_load_63 | 39 | 0.0018021 | 0.00045164 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3379-6_0_3_load_80 | 40 | 0.0026275 | 0.00065852 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3379-6_0_3_load_76 | 41 | 0.0027334 | 0.00068507 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3379-6_0_3_load_56 | 42 | 0.0029614 | 0.00074221 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3379-6_0_3_load_81 | 44 | 0.0025767 | 0.00064579 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3379-6_0_3_load_105 | 46 | 0.0022471 | 0.00056319 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3379-6_0_3_load_30 | 48 | 0.0020747 | 0.00051996 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3379-6_0_3_load_31 | 49 | 0.001406 | 0.00035238 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3379-6_0_3_load_32 | 50 | 0.0025341 | 0.00063511 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3379-6_0_3_load_33 | 51 | 0.0019157 | 0.00048013 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3379-6_0_3_load_34 | 52 | 0.0013761 | 0.00034489 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3379-6_0_3_load_107 | 55 | 0.0030821 | 0.00077245 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3379-6_0_3_load_108 | 56 | 0.0019986 | 0.0005009 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3379-6_0_3_load_74 | 57 | 0.0018697 | 0.00046859 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3379-6_0_3_load_35 | 58 | 0.0023269 | 0.00058316 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3379-6_0_3_load_36 | 59 | 0.0019589 | 0.00049094 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3379-6_0_3_load_38 | 60 | 0.0018549 | 0.00046489 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3379-6_0_3_load_40 | 63 | 0.0021981 | 0.00055091 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3379-6_0_3_load_57 | 64 | 0.00051651 | 0.00012945 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3379-6_0_3_load_73 | 65 | 0.00042925 | 0.00010758 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3379-6_0_3_load_72 | 68 | 0.00056726 | 0.00014217 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3379-6_0_3_load_61 | 69 | 0.0018373 | 0.00046046 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3379-6_0_3_load_42 | 71 | 0.0022593 | 0.00056624 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3379-6_0_3_load_43 | 72 | 0.0019246 | 0.00048235 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3379-6_0_3_load_44 | 73 | 0.0016393 | 0.00041085 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3379-6_0_3_load_45 | 74 | 0.0022631 | 0.00056719 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3379-6_0_3_load_46 | 75 | 0.0024046 | 0.00060265 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3379-6_0_3_load_47 | 76 | 0.0018502 | 0.00046371 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3379-6_0_3_load_77 | 77 | 0.0013774 | 0.00034522 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3379-6_0_3_load_79 | 78 | 0.003418 | 0.00085664 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3379-6_0_3_load_49 | 79 | 0.0021798 | 0.00054631 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3379-6_0_3_load_60 | 80 | 0.0027706 | 0.00069438 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3379-6_0_3_load_52 | 81 | 0.001354 | 0.00033934 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3379-6_0_3_load_51 | 82 | 0.0024884 | 0.00062366 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3379-6_0_3_load_59 | 85 | 0.0017845 | 0.00044723 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_3379-6_0_3_load_82 | 86 | 0.002329 | 0.00058369 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_3379-6_0_3_load_67 | 87 | 0.0021964 | 0.00055047 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_3379-6_0_3_load_71 | 88 | 0.00066848 | 0.00016754 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_3379-6_0_3_load_66 | 89 | 0.0029366 | 0.00073598 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_3379-6_0_3_load_69 | 90 | 0.00053636 | 0.00013443 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_3379-6_0_3_load_89 | 92 | 0.00016601 | 4.1607e-05 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_3379-6_0_3_load_83 | 93 | 0.00027382 | 6.8626e-05 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_3379-6_0_3_load_87 | 96 | 0.00047487 | 0.00011901 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_3379-6_0_3_load_88 | 97 | 0.00074487 | 0.00018668 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_3379-6_0_3_load_70 | 99 | 0.00048138 | 0.00012065 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_3379-6_0_3_load_113 | 100 | 0.002434 | 0.00061003 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_3379-6_0_3_load_90 | 101 | 0.0081559 | 0.0020441 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_3379-6_0_3_load_92 | 103 | 0.009838 | 0.0024656 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_3379-6_0_3_load_93 | 104 | 0.0057883 | 0.0014507 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_3379-6_0_3_load_100 | 108 | 0.003123 | 0.0007827 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_3379-6_0_3_load_102 | 109 | 0.0027984 | 0.00070135 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3379-6_0_3_line_0 |  | 0 | 1 | 0.019726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3379-6_0_3_line_1 |  | 0 | 2 | 0.34201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3379-6_0_3_line_2 |  | 1 | 3 | 0.023339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3379-6_0_3_line_3 |  | 3 | 4 | 0.0051286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3379-6_0_3_line_4 |  | 4 | 5 | 0.07655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3379-6_0_3_line_5 |  | 5 | 6 | 0.032852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3379-6_0_3_line_6 |  | 5 | 7 | 0.064685 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3379-6_0_3_line_7 |  | 6 | 8 | 0.036556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3379-6_0_3_line_8 |  | 7 | 9 | 0.023472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3379-6_0_3_line_9 |  | 7 | 10 | 0.014016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3379-6_0_3_line_10 |  | 9 | 12 | 0.088667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_3379-6_0_3_line_11 |  | 11 | 12 | 0.22097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3379-6_0_3_line_12 |  | 11 | 13 | 0.015871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_3379-6_0_3_line_13 |  | 11 | 14 | 0.016477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_3379-6_0_3_line_14 |  | 11 | 15 | 0.037493 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3379-6_0_3_line_15 |  | 13 | 16 | 0.0072217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3379-6_0_3_line_16 |  | 14 | 17 | 0.0012174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_3379-6_0_3_line_17 |  | 15 | 18 | 0.022429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3379-6_0_3_line_18 |  | 16 | 22 | 0.017721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_3379-6_0_3_line_19 |  | 17 | 31 | 0.065572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3379-6_0_3_line_20 |  | 19 | 20 | 0.012788 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3379-6_0_3_line_21 |  | 19 | 21 | 0.019595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3379-6_0_3_line_22 |  | 21 | 30 | 0.023634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3379-6_0_3_line_23 |  | 22 | 23 | 0.0042412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3379-6_0_3_line_24 |  | 23 | 24 | 0.0028564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3379-6_0_3_line_25 |  | 24 | 25 | 0.059757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3379-6_0_3_line_26 |  | 25 | 45 | 0.020499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3379-6_0_3_line_27 |  | 26 | 27 | 0.013688 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3379-6_0_3_line_28 |  | 26 | 28 | 0.089013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3379-6_0_3_line_29 |  | 28 | 29 | 0.02169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3379-6_0_3_line_30 |  | 29 | 107 | 0.027445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3379-6_0_3_line_31 |  | 30 | 109 | 0.07692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3379-6_0_3_line_32 |  | 31 | 32 | 0.002992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3379-6_0_3_line_33 |  | 32 | 33 | 0.041116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3379-6_0_3_line_34 |  | 32 | 34 | 0.0076232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3379-6_0_3_line_35 |  | 33 | 38 | 0.050115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3379-6_0_3_line_36 |  | 33 | 39 | 0.027368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3379-6_0_3_line_37 |  | 34 | 36 | 0.017734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3379-6_0_3_line_38 |  | 35 | 36 | 0.003296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_3379-6_0_3_line_39 |  | 35 | 37 | 0.0098079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_3379-6_0_3_line_40 |  | 36 | 41 | 0.017478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_3379-6_0_3_line_41 |  | 38 | 40 | 0.03303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_3379-6_0_3_line_42 |  | 40 | 44 | 0.01473 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_3379-6_0_3_line_43 |  | 41 | 84 | 0.028149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_3379-6_0_3_line_44 |  | 42 | 43 | 0.013797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_3379-6_0_3_line_45 |  | 43 | 83 | 0.002905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_3379-6_0_3_line_46 |  | 43 | 54 | 0.008706 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_3379-6_0_3_line_47 |  | 43 | 82 | 0.014953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3379-6_0_3_line_48 |  | 45 | 46 | 0.01972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3379-6_0_3_line_49 |  | 46 | 47 | 0.016322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3379-6_0_3_line_50 |  | 47 | 109 | 0.014091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3379-6_0_3_line_51 |  | 47 | 106 | 0.027864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3379-6_0_3_line_52 |  | 48 | 49 | 0.012295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_3379-6_0_3_line_53 |  | 48 | 50 | 0.0045777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_3379-6_0_3_line_54 |  | 49 | 51 | 0.020171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_3379-6_0_3_line_55 |  | 50 | 52 | 0.024283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_3379-6_0_3_line_56 |  | 51 | 53 | 0.013414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3379-6_0_3_line_57 |  | 52 | 54 | 0.029944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3379-6_0_3_line_58 |  | 53 | 55 | 0.00855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3379-6_0_3_line_59 |  | 53 | 56 | 0.015026 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3379-6_0_3_line_60 |  | 54 | 57 | 0.038541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3379-6_0_3_line_61 |  | 58 | 59 | 0.030541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3379-6_0_3_line_62 |  | 59 | 60 | 0.019099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3379-6_0_3_line_63 |  | 60 | 64 | 0.032498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3379-6_0_3_line_64 |  | 61 | 62 | 0.10222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3379-6_0_3_line_65 |  | 61 | 63 | 0.018623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3379-6_0_3_line_66 |  | 62 | 65 | 0.061703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3379-6_0_3_line_67 |  | 63 | 66 | 0.019533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3379-6_0_3_line_68 |  | 64 | 67 | 0.03737 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3379-6_0_3_line_69 |  | 65 | 68 | 0.0044923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3379-6_0_3_line_70 |  | 66 | 69 | 0.03294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3379-6_0_3_line_71 |  | 66 | 70 | 0.007672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3379-6_0_3_line_72 |  | 67 | 87 | 0.051003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3379-6_0_3_line_73 |  | 67 | 88 | 0.015206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3379-6_0_3_line_74 |  | 68 | 99 | 0.046235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_3379-6_0_3_line_75 |  | 69 | 80 | 0.010434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_3379-6_0_3_line_76 |  | 70 | 79 | 0.021662 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_3379-6_0_3_line_77 |  | 70 | 76 | 0.016992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_3379-6_0_3_line_78 |  | 71 | 72 | 0.01948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_3379-6_0_3_line_79 |  | 71 | 73 | 0.0061276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_3379-6_0_3_line_80 |  | 72 | 74 | 0.01906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_3379-6_0_3_line_81 |  | 73 | 75 | 0.0128 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_3379-6_0_3_line_82 |  | 74 | 76 | 0.018965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_3379-6_0_3_line_83 |  | 75 | 77 | 0.019132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_3379-6_0_3_line_84 |  | 77 | 78 | 0.080865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_3379-6_0_3_line_85 |  | 80 | 85 | 0.057813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_3379-6_0_3_line_86 |  | 81 | 82 | 0.018322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_3379-6_0_3_line_87 |  | 83 | 84 | 0.029195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_3379-6_0_3_line_88 |  | 83 | 85 | 0.00844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_3379-6_0_3_line_89 |  | 84 | 86 | 0.029062 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_3379-6_0_3_line_90 |  | 87 | 89 | 0.037068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_3379-6_0_3_line_91 |  | 88 | 90 | 0.02333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_3379-6_0_3_line_92 |  | 89 | 91 | 0.14254 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_3379-6_0_3_line_93 |  | 90 | 99 | 0.01336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_3379-6_0_3_line_94 |  | 91 | 92 | 0.13294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_3379-6_0_3_line_95 |  | 92 | 95 | 0.13519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_3379-6_0_3_line_96 |  | 93 | 94 | 0.038606 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_3379-6_0_3_line_97 |  | 94 | 95 | 0.11708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_3379-6_0_3_line_98 |  | 95 | 96 | 0.052586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_3379-6_0_3_line_99 |  | 96 | 97 | 0.033337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_3379-6_0_3_line_100 |  | 97 | 98 | 0.37819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_3379-6_0_3_line_101 |  | 98 | 100 | 0.24195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_3379-6_0_3_line_102 |  | 101 | 102 | 0.012209 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_3379-6_0_3_line_103 |  | 102 | 103 | 0.017108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_3379-6_0_3_line_104 |  | 102 | 104 | 0.05992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_3379-6_0_3_line_105 |  | 104 | 105 | 0.030264 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_3379-6_0_3_line_106 |  | 105 | 106 | 0.020733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_3379-6_0_3_line_107 |  | 105 | 107 | 0.002206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_3379-6_0_3_line_108 |  | 106 | 108 | 0.038137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3379-6_0_3_trafo_18 | 0.63 MVA 20/0.4 kV | 110 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16
0 | 2724884.2148 | 1241038.8183 | 2724872.0237 | 1241054.3261
1 | 2724872.0237 | 1241054.3261 | 2725095.6066 | 1241313.1293
2 | 2724884.2148 | 1241038.8183 | 2724880.2126 | 1241034.9197 | 2724880.9961 | 1241029.3203 | 2724886.901 | 1241018.7614
3 | 2724889.7084 | 1241014.4766 | 2724887.7081 | 1241017.3181 | 2724886.901 | 1241018.7614
4 | 2724855.0845 | 1240964.5764 | 2724859.8119 | 1240964.9317 | 2724896.2045 | 1240987.7498 | 2724896.425 | 1241004.9355 | 2724889.7084 | 1241014.4766
5 | 2724855.0845 | 1240964.5764 | 2724862.9165 | 1240982.0114 | 2724861.2966 | 1240989.617 | 2724859.5809 | 1240995.3277
6 | 2724826.7144 | 1240993.9823 | 2724829.6497 | 1240988.5617 | 2724832.1119 | 1240977.5931 | 2724831.0268 | 1240967.6953 | 2724827.5839 | 1240959.4938 | 2724839.7002 | 1240959.1705 | 2724855.0845 | 1240964.5764
7 | 2724844.6357 | 1241028.3213 | 2724854.2448 | 1241013.0884 | 2724859.5809 | 1240995.3277
8 | 2724826.7144 | 1240993.9823 | 2724824.0213 | 1240990.7674 | 2724827.7372 | 1240982.761 | 2724828.305 | 1240975.1888 | 2724828.0003 | 1240972.3471
9 | 2724826.7144 | 1240993.9823 | 2724821.45 | 1241003.6908 | 2724819.6889 | 1241006.0849
10 | 2724778.2884 | 1240994.8649 | 2724782.2679 | 1240993.7365 | 2724782.4014 | 1240982.7189 | 2724783.2211 | 1240972.5165 | 2724785.8792 | 1240966.6118 | 2724791.1032 | 1240959.5379 | 2724798.6988 | 1240955.1495 | 2724807.1528 | 1240953.815 | 2724815.1296 | 1240955.3951 | 2724822.6354 | 1240960.3015 | 2724827.4578 | 1240967.2866 | 2724828.0003 | 1240972.3471
11 | 2724778.2884 | 1240994.8649 | 2724777.9204 | 1240984.6708 | 2724778.6265 | 1240978.7918 | 2724781.8481 | 1240966.5938 | 2724783.0955 | 1240932.4691 | 2724785.3179 | 1240930.0137 | 2724821.8241 | 1240926.6117 | 2724838.4338 | 1240931.2983 | 2724841.0345 | 1240926.6824 | 2724841.6496 | 1240921.5355 | 2724829.982 | 1240904.131 | 2724826.8522 | 1240901.8967 | 2724829.6547 | 1240895.9617 | 2724845.0545 | 1240886.6222 | 2724856.7592 | 1240862.3813 | 2724859.322 | 1240859.9331 | 2724862.9565 | 1240850.0457
12 | 2724862.9565 | 1240850.0457 | 2724857.9506 | 1240850.3407 | 2724847.1549 | 1240849.1919
13 | 2724862.9565 | 1240850.0457 | 2724865.0298 | 1240849.2887 | 2724866.9154 | 1240846.6706 | 2724871.639 | 1240836.6883
14 | 2724862.9565 | 1240850.0457 | 2724871.8843 | 1240861.7878 | 2724879.3655 | 1240869.6629 | 2724889.5872 | 1240875.7176
15 | 2724839.9738 | 1240848.4277 | 2724839.9738 | 1240848.4277 | 2724847.1549 | 1240849.1919
16 | 2724871.639 | 1240836.6883 | 2724872.1597 | 1240835.5879
17 | 2724901.0981 | 1240888.0755 | 2724903.7297 | 1240881.4632 | 2724892.4466 | 1240877.4113 | 2724889.5872 | 1240875.7176
18 | 2724839.9738 | 1240848.4277 | 2724835.6365 | 1240848.581 | 2724830.889 | 1240849.8934 | 2724826.4916 | 1240851.8248 | 2724822.8687 | 1240852.2871
19 | 2724904.5893 | 1240778.8617 | 2724895.8241 | 1240791.0098 | 2724886.5177 | 1240806.2267 | 2724880.7867 | 1240815.8142 | 2724876.9609 | 1240825.4419 | 2724872.1597 | 1240835.5879
20 | 2724736.3107 | 1240854.5648 | 2724732.0944 | 1240842.4883
21 | 2724736.3107 | 1240854.5648 | 2724746.8389 | 1240849.2038 | 2724752.9395 | 1240844.3755
22 | 2724752.9395 | 1240844.3755 | 2724760.6766 | 1240838.2521 | 2724768.1991 | 1240832.3052 | 2724770.7382 | 1240828.9874
23 | 2724822.8687 | 1240852.2871 | 2724822.0776 | 1240852.388 | 2724818.9144 | 1240851.0267
24 | 2724816.2907 | 1240849.8976 | 2724818.9144 | 1240851.0267
25 | 2724816.2907 | 1240849.8976 | 2724816.2907 | 1240849.8976 | 2724813.7021 | 1240847.4633 | 2724811.6403 | 1240834.3756 | 2724811.4356 | 1240827.2098 | 2724812.2589 | 1240811.4472 | 2724809.2672 | 1240799.0516 | 2724806.5738 | 1240792.3206
26 | 2724793.4356 | 1240777.5007 | 2724801.1529 | 1240782.4337 | 2724804.7257 | 1240787.7022 | 2724806.5738 | 1240792.3206
27 | 2724681.7794 | 1240815.8757 | 2724684.8417 | 1240808.367 | 2724686.6245 | 1240803.0778
28 | 2724681.7794 | 1240815.8757 | 2724677.5482 | 1240818.1776 | 2724669.2399 | 1240816.524 | 2724690.3291 | 1240743.7947
29 | 2724690.3291 | 1240743.7947 | 2724712.0114 | 1240743.2246
30 | 2724739.4464 | 1240742.5033 | 2724712.0114 | 1240743.2246
31 | 2724787.3404 | 1240755.3667 | 2724785.5169 | 1240763.8005 | 2724783.4349 | 1240789.7786 | 2724781.1493 | 1240810.6925 | 2724776.1557 | 1240821.9081 | 2724770.7382 | 1240828.9874
32 | 2724904.5893 | 1240778.8617 | 2724906.126 | 1240776.2919
33 | 2724906.126 | 1240776.2919 | 2724877.6459 | 1240746.5567
34 | 2724906.126 | 1240776.2919 | 2724912.4465 | 1240780.5538
35 | 2724877.6459 | 1240746.5567 | 2724870.8071 | 1240739.4179 | 2724878.7079 | 1240729.8872 | 2724879.6215 | 1240727.4488 | 2724879.9162 | 1240723.1514 | 2724878.5929 | 1240709.1229 | 2724879.16 | 1240705.8988 | 2724880.2528 | 1240702.4967
36 | 2724877.6459 | 1240746.5567 | 2724899.4264 | 1240739.5534 | 2724903.8488 | 1240738.7814
37 | 2724927.1502 | 1240790.4684 | 2724912.4465 | 1240780.5538
38 | 2724927.1502 | 1240790.4684 | 2724926.4967 | 1240792.0449 | 2724926.433 | 1240793.6338
39 | 2724926.433 | 1240793.6338 | 2724926.769 | 1240795.9984 | 2724929.6487 | 1240800.4072 | 2724931.0094 | 1240802.0765
40 | 2724927.1502 | 1240790.4684 | 2724941.4043 | 1240800.5835
41 | 2724880.2528 | 1240702.4967 | 2724883.12 | 1240701.7564 | 2724885.0748 | 1240701.2415 | 2724889.4406 | 1240700.0991 | 2724892.6121 | 1240699.2762 | 2724895.799 | 1240698.4426 | 2724898.3166 | 1240697.7839 | 2724899.2444 | 1240697.5476 | 2724905.8016 | 1240702.2562 | 2724908.9161 | 1240704.5014 | 2724910.1291 | 1240705.37
42 | 2724910.1291 | 1240705.37 | 2724910.4362 | 1240705.5899 | 2724911.455 | 1240705.3444 | 2724916.3892 | 1240704.1473 | 2724919.4989 | 1240703.3898 | 2724923.9543 | 1240702.3049 | 2724924.3831 | 1240702.2013
43 | 2724964.3606 | 1240816.8738 | 2724941.4043 | 1240800.5835
44 | 2724993.3822 | 1240824.102 | 2724986.9566 | 1240826.0795 | 2724981.7173 | 1240826.6808 | 2724979.9278 | 1240826.4883
45 | 2724991.654 | 1240821.7636 | 2724993.3822 | 1240824.102
46 | 2724997.4944 | 1240831.7617 | 2724995.752 | 1240827.944 | 2724993.3822 | 1240824.102
47 | 2724993.3822 | 1240824.102 | 2724997.3519 | 1240820.9385 | 2725000.3908 | 1240816.3542 | 2725002.3117 | 1240812.4218
48 | 2724793.4356 | 1240777.5007 | 2724791.73 | 1240757.8547
49 | 2724790.3182 | 1240741.5939 | 2724791.73 | 1240757.8547
50 | 2724790.3182 | 1240741.5939 | 2724787.3404 | 1240755.3667
51 | 2724762.3789 | 1240742.2183 | 2724790.3182 | 1240741.5939
52 | 2724961.0177 | 1240873.1431 | 2724957.6399 | 1240875.2258 | 2724954.4188 | 1240879.8397 | 2724953.6435 | 1240882.4253
53 | 2724961.0177 | 1240873.1431 | 2724964.9143 | 1240870.7406
54 | 2724953.6435 | 1240882.4253 | 2724953.0602 | 1240884.3705 | 2724953.7947 | 1240889.0009 | 2724957.1219 | 1240893.7083 | 2724962.6605 | 1240897.9284 | 2724963.2718 | 1240898.3167
55 | 2724985.1316 | 1240857.3421 | 2724979.1433 | 1240861.9674 | 2724964.9143 | 1240870.7406
56 | 2724974.5953 | 1240905.5082 | 2724963.2718 | 1240898.3167
57 | 2724997.4944 | 1240831.7617 | 2724998.1143 | 1240835.3667 | 2724997.457 | 1240840.357 | 2724995.3957 | 1240845.2066 | 2724991.9666 | 1240850.3609 | 2724986.6555 | 1240856.1651 | 2724985.1316 | 1240857.3421
58 | 2724974.5953 | 1240905.5082 | 2724979.2396 | 1240898.3222
59 | 2724974.5953 | 1240905.5082 | 2724986.8293 | 1240914.233
60 | 2725032.8517 | 1240831.5839 | 2725028.52 | 1240830.0358 | 2725026.7078 | 1240830.9651 | 2725019.4847 | 1240836.6845 | 2725017.0361 | 1240836.5884 | 2725012.1116 | 1240834.0937 | 2725003.155 | 1240832.348 | 2724997.4944 | 1240831.7617
61 | 2725093.702 | 1240714.1858 | 2725092.9233 | 1240726.8948 | 2725093.221 | 1240736.4535 | 2725094.6761 | 1240744.5688 | 2725094.6761 | 1240744.5688
62 | 2725104.6779 | 1240760.6041 | 2725097.9596 | 1240752.4223 | 2725094.6761 | 1240744.5688
63 | 2725104.6779 | 1240760.6041 | 2725104.6779 | 1240760.6041 | 2725130.1267 | 1240780.815
64 | 2725006.8754 | 1240690.9853 | 2725008.2704 | 1240685.8104 | 2725010.3042 | 1240685.4974 | 2725013.735 | 1240683.8571 | 2725053.2351 | 1240660.5139 | 2725060.3952 | 1240657.4288 | 2725067.1659 | 1240656.3149 | 2725072.6402 | 1240656.7751 | 2725078.8348 | 1240658.5849 | 2725085.3036 | 1240662.102 | 2725089.7913 | 1240665.9442 | 2725093.2499 | 1240670.1651
65 | 2725006.8754 | 1240690.9853 | 2725003.7728 | 1240696.7916 | 2725002.082 | 1240702.7276 | 2725001.6485 | 1240708.579
66 | 2725093.2499 | 1240670.1651 | 2725096.2102 | 1240676.4883 | 2725097.4784 | 1240681.2746 | 2725097.3822 | 1240688.3452 | 2725095.8141 | 1240724.3202 | 2725095.8628 | 1240731.0095
67 | 2725003.9479 | 1240727.9659 | 2725002.5184 | 1240718.6279 | 2725001.6485 | 1240708.579
68 | 2725153.6895 | 1240808.4219 | 2725151.7092 | 1240801.1851 | 2725147.5221 | 1240795.2919 | 2725139.546 | 1240788.2957 | 2725130.1267 | 1240780.815
69 | 2725095.8955 | 1240735.5017 | 2725095.8628 | 1240731.0095
70 | 2725003.9479 | 1240727.9659 | 2725002.3231 | 1240732.2019 | 2724999.8953 | 1240736.4988 | 2724987.3228 | 1240752.7033 | 2724985.6822 | 1240755.165
71 | 2725003.9479 | 1240727.9659 | 2725011.6425 | 1240727.8723
72 | 2725153.6895 | 1240808.4219 | 2725152.6824 | 1240819.5878 | 2725146.8929 | 1240843.3969 | 2725147.9551 | 1240851.1258 | 2725150.9112 | 1240858.005
73 | 2725153.6895 | 1240808.4219 | 2725154.8835 | 1240802.0194 | 2725154.2101 | 1240800.2371 | 2725151.7035 | 1240796.4366 | 2725150.1179 | 1240794.8618
74 | 2725121.6095 | 1240771.8022 | 2725119.9452 | 1240770.4898 | 2725105.6069 | 1240757.7991 | 2725101.164 | 1240751.8338 | 2725097.7904 | 1240746.1024 | 2725096.3031 | 1240742.0231 | 2725095.9053 | 1240736.8549 | 2725095.8955 | 1240735.5017
75 | 2724981.344 | 1240764.5452 | 2724981.3563 | 1240764.1206 | 2724983.4564 | 1240758.5045 | 2724985.6822 | 1240755.165
76 | 2725011.6425 | 1240727.8723 | 2725012.3154 | 1240733.6246 | 2725011.6351 | 1240737.9139 | 2725007.9406 | 1240748.8342
77 | 2725011.6425 | 1240727.8723 | 2725028.5062 | 1240729.9535
78 | 2725048.7595 | 1240776.2818 | 2725045.6188 | 1240771.3466 | 2725044.1919 | 1240764.3996 | 2725043.6637 | 1240757.883
79 | 2725048.7595 | 1240776.2818 | 2725048.8109 | 1240776.3625 | 2725053.0102 | 1240780.6926
80 | 2725043.6637 | 1240757.883 | 2725043.6637 | 1240757.883 | 2725044.1203 | 1240744.1144 | 2725043.611 | 1240738.8548
81 | 2725053.0102 | 1240780.6926 | 2725054.3928 | 1240782.1183 | 2725062.6838 | 1240789.0607
82 | 2725028.5062 | 1240729.9535 | 2725033.7023 | 1240730.5947 | 2725038.8116 | 1240732.2148 | 2725042.068 | 1240735.2637 | 2725043.611 | 1240738.8548 | 2725043.611 | 1240738.8548
83 | 2725073.6575 | 1240804.3873 | 2725073.6575 | 1240804.3873 | 2725070.9187 | 1240798.3245 | 2725066.3818 | 1240792.1571 | 2725062.6838 | 1240789.0607
84 | 2725073.6575 | 1240804.3873 | 2725075.1108 | 1240811.157 | 2725075.1267 | 1240817.5738 | 2725074.1689 | 1240824.2592 | 2725072.0358 | 1240829.641 | 2725068.8114 | 1240835.845 | 2725062.5791 | 1240845.1549 | 2725045.2893 | 1240863.039 | 2725037.2675 | 1240871.8441 | 2725037.2675 | 1240871.8441
85 | 2724997.3504 | 1240815.6035 | 2724998.201 | 1240814.3842 | 2725000.2965 | 1240809.7022 | 2725001.1211 | 1240805.7495 | 2725000.6692 | 1240800.9916 | 2724999.0641 | 1240796.3983 | 2724995.7918 | 1240791.2362 | 2724983.5912 | 1240775.7997 | 2724981.1894 | 1240769.8886 | 2724981.344 | 1240764.5452
86 | 2725002.3117 | 1240812.4218 | 2725003.8374 | 1240809.2986 | 2725004.6617 | 1240806.4358 | 2725004.6652 | 1240803.7558 | 2725003.7753 | 1240800.4009 | 2725002.1821 | 1240796.3195 | 2725001.5097 | 1240795.1668
87 | 2724991.654 | 1240821.7636 | 2724987.1414 | 1240823.4145 | 2724982.1312 | 1240823.9094 | 2724977.548 | 1240823.5237 | 2724971.2754 | 1240821.1118 | 2724964.3606 | 1240816.8738
88 | 2724991.654 | 1240821.7636 | 2724995.4868 | 1240818.2747 | 2724997.3504 | 1240815.6035
89 | 2724977.0388 | 1240793.4877 | 2724979.2423 | 1240795.1689 | 2724964.3606 | 1240816.8738
90 | 2725180.8163 | 1240879.8246 | 2725156.3966 | 1240862.947 | 2725150.9112 | 1240858.005
91 | 2725132.1001 | 1240780.0745 | 2725147.2879 | 1240792.0509 | 2725150.1179 | 1240794.8618
92 | 2725305.3097 | 1240940.476 | 2725297.9913 | 1240942.4676 | 2725290.7228 | 1240943.1703 | 2725281.2384 | 1240940.6347 | 2725271.9881 | 1240933.4668 | 2725259.1311 | 1240925.878 | 2725235.6285 | 1240915.9404 | 2725220.1449 | 1240907.0063 | 2725180.8163 | 1240879.8246
93 | 2725132.1001 | 1240780.0745 | 2725121.6095 | 1240771.8022
94 | 2725305.3097 | 1240940.476 | 2725434.9757 | 1240969.7836
95 | 2725434.9757 | 1240969.7836 | 2725471.7834 | 1240976.4559 | 2725515.1973 | 1240985.4813 | 2725541.6571 | 1240992.1798 | 2725568.1853 | 1240992.7859
96 | 2725486.4797 | 1240923.1884 | 2725490.911 | 1240920.7355 | 2725500.5353 | 1240911.6536 | 2725504.8174 | 1240905.5278 | 2725506.3199 | 1240901.723 | 2725506.2889 | 1240898.1861 | 2725504.7071 | 1240893.2262
97 | 2725486.4797 | 1240923.1884 | 2725491.1324 | 1240928.1465 | 2725523.7758 | 1240943.2493 | 2725547.9724 | 1240955.0376 | 2725561.3197 | 1240962.6708 | 2725565.4838 | 1240968.9086 | 2725569.1408 | 1240976.5924 | 2725568.1853 | 1240992.7859
98 | 2725568.1853 | 1240992.7859 | 2725565.2243 | 1241017.9667 | 2725562.8574 | 1241045.0951
99 | 2725562.8574 | 1241045.0951 | 2725563.8435 | 1241056.0363 | 2725567.2192 | 1241064.5037 | 2725572.7455 | 1241076.5307
100 | 2725572.7455 | 1241076.5307 | 2725635.1375 | 1241449.5435
101 | 2725635.1375 | 1241449.5435 | 2725637.5461 | 1241448.3046 | 2725638.1609 | 1241446.0602 | 2725636.4456 | 1241439.5628 | 2725635.7325 | 1241431.0961 | 2725636.986 | 1241424.05 | 2725641.6529 | 1241416.8872 | 2725650.0173 | 1241405.8438 | 2725659.8901 | 1241383.9343 | 2725666.3517 | 1241377.0319 | 2725704.6448 | 1241357.0259 | 2725736.7786 | 1241352.8585 | 2725741.9439 | 1241358.228 | 2725727.8089 | 1241393.514 | 2725731.0638 | 1241431.2036
102 | 2724742.4965 | 1240819.3875 | 2724730.8269 | 1240815.7987
103 | 2724742.4965 | 1240819.3875 | 2724758.8472 | 1240824.4216
104 | 2724742.4965 | 1240819.3875 | 2724752.6151 | 1240791.0652 | 2724737.9256 | 1240785.6854 | 2724734.491 | 1240778.1624 | 2724735.6642 | 1240772.3491
105 | 2724741.6513 | 1240742.6831 | 2724735.6642 | 1240772.3491
106 | 2724741.6513 | 1240742.6831 | 2724750.0589 | 1240742.493 | 2724762.3789 | 1240742.2183
107 | 2724741.6513 | 1240742.6831 | 2724739.4464 | 1240742.5033
108 | 2724762.3789 | 1240742.2183 | 2724762.435 | 1240756.8095 | 2724765.5614 | 1240775.035 | 2724764.8258 | 1240780.0354

## bus_geodata
| x | y | coords
0 | 2724872.0237 | 1241054.3261
1 | 2724884.2148 | 1241038.8183
2 | 2725095.6066 | 1241313.1293
3 | 2724886.901 | 1241018.7614
4 | 2724889.7084 | 1241014.4766
5 | 2724855.0845 | 1240964.5764
6 | 2724859.5809 | 1240995.3277
7 | 2724826.7144 | 1240993.9823
8 | 2724844.6357 | 1241028.3213
9 | 2724828.0003 | 1240972.3471
10 | 2724819.6889 | 1241006.0849
11 | 2724862.9565 | 1240850.0457
12 | 2724778.2884 | 1240994.8649
13 | 2724847.1549 | 1240849.1919
14 | 2724871.639 | 1240836.6883
15 | 2724889.5872 | 1240875.7176
16 | 2724839.9738 | 1240848.4277
17 | 2724872.1597 | 1240835.5879
18 | 2724901.0981 | 1240888.0755
19 | 2724736.3107 | 1240854.5648
20 | 2724732.0944 | 1240842.4883
21 | 2724752.9395 | 1240844.3755
22 | 2724822.8687 | 1240852.2871
23 | 2724818.9144 | 1240851.0267
24 | 2724816.2907 | 1240849.8976
25 | 2724806.5738 | 1240792.3206
26 | 2724681.7794 | 1240815.8757
27 | 2724686.6245 | 1240803.0778
28 | 2724690.3291 | 1240743.7947
29 | 2724712.0114 | 1240743.2246
30 | 2724770.7382 | 1240828.9874
31 | 2724904.5893 | 1240778.8617
32 | 2724906.126 | 1240776.2919
33 | 2724877.6459 | 1240746.5567
34 | 2724912.4465 | 1240780.5538
35 | 2724926.433 | 1240793.6338
36 | 2724927.1502 | 1240790.4684
37 | 2724931.0094 | 1240802.0765
38 | 2724880.2528 | 1240702.4967
39 | 2724903.8488 | 1240738.7814
40 | 2724910.1291 | 1240705.37
41 | 2724941.4043 | 1240800.5835
42 | 2724979.9278 | 1240826.4883
43 | 2724993.3822 | 1240824.102
44 | 2724924.3831 | 1240702.2013
45 | 2724793.4356 | 1240777.5007
46 | 2724791.73 | 1240757.8547
47 | 2724790.3182 | 1240741.5939
48 | 2724961.0177 | 1240873.1431
49 | 2724953.6435 | 1240882.4253
50 | 2724964.9143 | 1240870.7406
51 | 2724963.2718 | 1240898.3167
52 | 2724985.1316 | 1240857.3421
53 | 2724974.5953 | 1240905.5082
54 | 2724997.4944 | 1240831.7617
55 | 2724979.2396 | 1240898.3222
56 | 2724986.8293 | 1240914.233
57 | 2725032.8517 | 1240831.5839
58 | 2725093.702 | 1240714.1858
59 | 2725094.6761 | 1240744.5688
60 | 2725104.6779 | 1240760.6041
61 | 2725006.8754 | 1240690.9853
62 | 2725093.2499 | 1240670.1651
63 | 2725001.6485 | 1240708.579
64 | 2725130.1267 | 1240780.815
65 | 2725095.8628 | 1240731.0095
66 | 2725003.9479 | 1240727.9659
67 | 2725153.6895 | 1240808.4219
68 | 2725095.8955 | 1240735.5017
69 | 2724985.6822 | 1240755.165
70 | 2725011.6425 | 1240727.8723
71 | 2725048.7595 | 1240776.2818
72 | 2725043.6637 | 1240757.883
73 | 2725053.0102 | 1240780.6926
74 | 2725043.611 | 1240738.8548
75 | 2725062.6838 | 1240789.0607
76 | 2725028.5062 | 1240729.9535
77 | 2725073.6575 | 1240804.3873
78 | 2725037.2675 | 1240871.8441
79 | 2725007.9406 | 1240748.8342
80 | 2724981.344 | 1240764.5452
81 | 2725001.5097 | 1240795.1668
82 | 2725002.3117 | 1240812.4218
83 | 2724991.654 | 1240821.7636
84 | 2724964.3606 | 1240816.8738
85 | 2724997.3504 | 1240815.6035
86 | 2724977.0388 | 1240793.4877
87 | 2725150.9112 | 1240858.005
88 | 2725150.1179 | 1240794.8618
89 | 2725180.8163 | 1240879.8246
90 | 2725132.1001 | 1240780.0745
91 | 2725305.3097 | 1240940.476
92 | 2725434.9757 | 1240969.7836
93 | 2725504.7071 | 1240893.2262
94 | 2725486.4797 | 1240923.1884
95 | 2725568.1853 | 1240992.7859
96 | 2725562.8574 | 1241045.0951
97 | 2725572.7455 | 1241076.5307
98 | 2725635.1375 | 1241449.5435
99 | 2725121.6095 | 1240771.8022
100 | 2725731.0638 | 1241431.2036
101 | 2724730.8269 | 1240815.7987
102 | 2724742.4965 | 1240819.3875
103 | 2724758.8472 | 1240824.4216
104 | 2724735.6642 | 1240772.3491
105 | 2724741.6513 | 1240742.6831
106 | 2724762.3789 | 1240742.2183
107 | 2724739.4464 | 1240742.5033
108 | 2724764.8258 | 1240780.0354
109 | 2724787.3404 | 1240755.3667
110 | 2724862.9565 | 1240850.0457

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9913 | -0.16755 | 0.0033132 | 0.00083038
1 | 0.99137 | -0.1662 | 0 | 0
2 | 0.99113 | -0.17088 | 0.00054319 | 0.00013614
3 | 0.99145 | -0.1646 | 0.0023271 | 0.00058321
4 | 0.99148 | -0.16403 | 0.0009823 | 0.00024619
5 | 0.99198 | -0.15429 | 0 | 0
6 | 0.99178 | -0.15819 | 0.0048038 | 0.0012039
7 | 0.9928 | -0.13839 | 0 | 0
8 | 0.99171 | -0.15942 | 0.0018986 | 0.00047582
9 | 0.99313 | -0.13192 | 0.004439 | 0.0011125
10 | 0.99278 | -0.13882 | 0.001728 | 0.00043307
11 | 0.9988 | -0.022768 | 0 | 0
12 | 0.99476 | -0.10054 | 0 | 0
13 | 0.99709 | -0.055385 | 0.0026294 | 0.000659
14 | 0.99991 | -0.0017208 | 0.01579 | 0.0039573
15 | 0.9985 | -0.028597 | 0.0072294 | 0.0018119
16 | 0.99633 | -0.06993 | 0.021001 | 0.0052634
17 | 1 | 0 | -0.25186 | -0.063661
18 | 0.99847 | -0.02925 | 0.0016647 | 0.0004172
19 | 0.98444 | -0.29938 | 0 | 0
20 | 0.98433 | -0.30166 | 0.0099236 | 0.0024871
21 | 0.98462 | -0.29588 | 0.0053297 | 0.0013357
22 | 0.99481 | -0.099158 | 0.0068887 | 0.0017265
23 | 0.99447 | -0.10565 | 0.0035479 | 0.00088919
24 | 0.99425 | -0.10985 | 0.011527 | 0.0028891
25 | 0.99029 | -0.18583 | 0.0037442 | 0.00093839
26 | 0.98362 | -0.31537 | 0 | 0
27 | 0.98351 | -0.31765 | 0.0092827 | 0.0023265
28 | 0.98438 | -0.30049 | 0 | 0
29 | 0.98457 | -0.29687 | 0.0054793 | 0.0013732
30 | 0.98495 | -0.2894 | 0.0061 | 0.0015288
31 | 0.99483 | -0.098326 | 0 | 0
32 | 0.9946 | -0.10284 | 0 | 0
33 | 0.99433 | -0.10792 | 0 | 0
34 | 0.99405 | -0.1134 | 0.0021858 | 0.00054782
35 | 0.99279 | -0.13742 | 0 | 0
36 | 0.9928 | -0.13732 | 0 | 0
37 | 0.99278 | -0.13772 | 0.0017132 | 0.00042936
38 | 0.9941 | -0.11252 | 0 | 0
39 | 0.99429 | -0.10879 | 0.0018021 | 0.00045164
40 | 0.99394 | -0.11555 | 0.0026275 | 0.00065852
41 | 0.99159 | -0.16043 | 0.0027334 | 0.00068507
42 | 0.98776 | -0.23455 | 0.0029614 | 0.00074221
43 | 0.98779 | -0.23382 | 0 | 0
44 | 0.99391 | -0.11622 | 0.0025767 | 0.00064579
45 | 0.98901 | -0.21067 | 0 | 0
46 | 0.98777 | -0.23462 | 0.0022471 | 0.00056319
47 | 0.98678 | -0.25384 | 0 | 0
48 | 0.98693 | -0.25056 | 0.0020747 | 0.00051996
49 | 0.98684 | -0.25241 | 0.001406 | 0.00035238
50 | 0.98698 | -0.24971 | 0.0025341 | 0.00063511
51 | 0.98671 | -0.25494 | 0.0019157 | 0.00048013
52 | 0.98727 | -0.24405 | 0.0013761 | 0.00034489
53 | 0.98665 | -0.25616 | 0 | 0
54 | 0.98766 | -0.23635 | 0 | 0
55 | 0.98662 | -0.25663 | 0.0030821 | 0.00077245
56 | 0.98662 | -0.2567 | 0.0019986 | 0.0005009
57 | 0.9876 | -0.23764 | 0.0018697 | 0.00046859
58 | 0.97778 | -0.42936 | 0.0023269 | 0.00058316
59 | 0.97784 | -0.42807 | 0.0019589 | 0.00049094
60 | 0.97792 | -0.42657 | 0.0018549 | 0.00046489
61 | 0.98278 | -0.33126 | 0 | 0
62 | 0.98102 | -0.36567 | 0 | 0
63 | 0.9831 | -0.32501 | 0.0021981 | 0.00055091
64 | 0.9781 | -0.42294 | 0.00051651 | 0.00012945
65 | 0.97996 | -0.3865 | 0.00042925 | 0.00010758
66 | 0.98348 | -0.31767 | 0 | 0
67 | 0.97834 | -0.4184 | 0 | 0
68 | 0.97988 | -0.38798 | 0.00056726 | 0.00014217
69 | 0.9847 | -0.29387 | 0.0018373 | 0.00046046
70 | 0.98334 | -0.32035 | 0 | 0
71 | 0.98238 | -0.33922 | 0.0022593 | 0.00056624
72 | 0.98258 | -0.33531 | 0.0019246 | 0.00048235
73 | 0.98233 | -0.34019 | 0.0016393 | 0.00041085
74 | 0.9828 | -0.33083 | 0.0022631 | 0.00056719
75 | 0.98224 | -0.34186 | 0.0024046 | 0.00060265
76 | 0.98307 | -0.3256 | 0.0018502 | 0.00046371
77 | 0.98216 | -0.34352 | 0.0013774 | 0.00034522
78 | 0.9819 | -0.34852 | 0.003418 | 0.00085664
79 | 0.9833 | -0.3212 | 0.0021798 | 0.00054631
80 | 0.9851 | -0.286 | 0.0027706 | 0.00069438
81 | 0.98772 | -0.23529 | 0.001354 | 0.00033934
82 | 0.98774 | -0.23485 | 0.0024884 | 0.00062366
83 | 0.98785 | -0.23262 | 0 | 0
84 | 0.98973 | -0.19639 | 0 | 0
85 | 0.98749 | -0.23964 | 0.0017845 | 0.00044723
86 | 0.98967 | -0.1976 | 0.002329 | 0.00058369
87 | 0.9779 | -0.42701 | 0.0021964 | 0.00055047
88 | 0.97856 | -0.41399 | 0.00066848 | 0.00016754
89 | 0.97766 | -0.43179 | 0.0029366 | 0.00073598
90 | 0.97892 | -0.40694 | 0.00053636 | 0.00013443
91 | 0.97712 | -0.44254 | 0 | 0
92 | 0.97661 | -0.45256 | 0.00016601 | 4.1607e-05
93 | 0.97608 | -0.46313 | 0.00027382 | 6.8626e-05
94 | 0.97609 | -0.46294 | 0 | 0
95 | 0.97612 | -0.46234 | 0 | 0
96 | 0.97594 | -0.46588 | 0.00047487 | 0.00011901
97 | 0.97584 | -0.46783 | 0.00074487 | 0.00018668
98 | 0.97499 | -0.48479 | 0 | 0
99 | 0.97913 | -0.40278 | 0.00048138 | 0.00012065
100 | 0.97444 | -0.49561 | 0.002434 | 0.00061003
101 | 0.98322 | -0.32315 | 0.0081559 | 0.0020441
102 | 0.98332 | -0.32136 | 0 | 0
103 | 0.98316 | -0.32439 | 0.009838 | 0.0024656
104 | 0.98431 | -0.30194 | 0.0057883 | 0.0014507
105 | 0.98497 | -0.289 | 0 | 0
106 | 0.98571 | -0.27465 | 0 | 0
107 | 0.98494 | -0.28958 | 0 | 0
108 | 0.9856 | -0.27679 | 0.003123 | 0.0007827
109 | 0.98647 | -0.25993 | 0.0027984 | 0.00070135
110 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.0038565 | -0.00096216 | 0.0038568 | 0.00096206 | 2.4776e-07 | -9.5759e-08 | 0.0057874 | 0.0057873 | 0.0057874 | 0.9913 | -0.16755 | 0.99137 | -0.1662 | 1.5899
1 | 0.00054327 | 0.00013178 | -0.00054319 | -0.00013614 | 8.5132e-08 | -4.3539e-06 | 0.00081397 | 0.00081551 | 0.00081551 | 0.9913 | -0.16755 | 0.99113 | -0.17088 | 0.22404
2 | -0.0038568 | -0.00096206 | 0.0038571 | 0.00096195 | 2.9313e-07 | -1.1335e-07 | 0.0057873 | 0.0057872 | 0.0057873 | 0.99137 | -0.1662 | 0.99145 | -0.1646 | 1.5899
3 | -0.0061841 | -0.0015452 | 0.0061843 | 0.0015452 | 1.6562e-07 | 3.9854e-08 | 0.0092797 | 0.0092797 | 0.0092797 | 0.99145 | -0.1646 | 0.99148 | -0.16403 | 2.5494
4 | -0.0071666 | -0.0017914 | 0.0071699 | 0.0017925 | 3.3197e-06 | 1.1369e-06 | 0.010754 | 0.010754 | 0.010754 | 0.99148 | -0.16403 | 0.99198 | -0.15429 | 2.9544
5 | 0.0067037 | 0.0016797 | -0.0067025 | -0.0016794 | 1.2458e-06 | 3.7326e-07 | 0.010056 | 0.010056 | 0.010056 | 0.99198 | -0.15429 | 0.99178 | -0.15819 | 2.7626
6 | -0.013874 | -0.0034723 | 0.013884 | 0.0034782 | 1.0504e-05 | 5.8867e-06 | 0.020809 | 0.020809 | 0.020809 | 0.99198 | -0.15429 | 0.9928 | -0.13839 | 5.7169
7 | 0.0018987 | 0.00047542 | -0.0018986 | -0.00047582 | 1.1124e-07 | -4.0051e-07 | 0.0028485 | 0.0028487 | 0.0028487 | 0.99178 | -0.15819 | 0.99171 | -0.15942 | 0.78261
8 | -0.015612 | -0.0039111 | 0.015617 | 0.0039139 | 4.8192e-06 | 2.7807e-06 | 0.023399 | 0.023399 | 0.023399 | 0.9928 | -0.13839 | 0.99313 | -0.13192 | 6.4283
9 | 0.001728 | 0.00043292 | -0.001728 | -0.00043307 | 3.5256e-08 | -1.5867e-07 | 0.0025899 | 0.00259 | 0.00259 | 0.9928 | -0.13839 | 0.99278 | -0.13882 | 0.71153
10 | -0.020056 | -0.0050264 | 0.020086 | 0.0050444 | 3.0024e-05 | 1.8066e-05 | 0.03005 | 0.030049 | 0.03005 | 0.99313 | -0.13192 | 0.99476 | -0.10054 | 8.2555
11 | 0.020161 | 0.0050894 | -0.020086 | -0.0050444 | 7.4822e-05 | 4.5005e-05 | 0.030048 | 0.030049 | 0.030049 | 0.9988 | -0.022768 | 0.99476 | -0.10054 | 8.2553
12 | 0.11849 | 0.030113 | -0.11831 | -0.029994 | 0.00018579 | 0.0001187 | 0.17668 | 0.17668 | 0.17668 | 0.9988 | -0.022768 | 0.99709 | -0.055385 | 48.5383
13 | -0.14755 | -0.037432 | 0.1477 | 0.037527 | 0.0001495 | 9.5251e-05 | 0.21998 | 0.21998 | 0.21998 | 0.9988 | -0.022768 | 0.99991 | -0.0017208 | 30.2173
14 | 0.0088966 | 0.0022299 | -0.0088941 | -0.0022288 | 2.47e-06 | 1.0902e-06 | 0.013254 | 0.013254 | 0.013254 | 0.9988 | -0.022768 | 0.9985 | -0.028597 | 3.6413
15 | 0.11568 | 0.029335 | -0.1156 | -0.029284 | 8.0823e-05 | 5.1632e-05 | 0.17276 | 0.17276 | 0.17276 | 0.99709 | -0.055385 | 0.99633 | -0.06993 | 47.4602
16 | -0.16349 | -0.041485 | 0.1635 | 0.041493 | 1.3532e-05 | 8.6284e-06 | 0.24348 | 0.24348 | 0.24348 | 0.99991 | -0.0017208 | 1 | 0 | 33.445
17 | 0.0016647 | 0.00041694 | -0.0016647 | -0.0004172 | 5.1763e-08 | -2.6023e-07 | 0.0024807 | 0.0024808 | 0.0024808 | 0.9985 | -0.028597 | 0.99847 | -0.02925 | 0.68155
18 | 0.094597 | 0.02402 | -0.094464 | -0.023935 | 0.00013285 | 8.4791e-05 | 0.14139 | 0.14139 | 0.14139 | 0.99633 | -0.06993 | 0.99481 | -0.099158 | 38.8434
19 | 0.086709 | 0.022167 | -0.086299 | -0.021905 | 0.00041033 | 0.00026176 | 0.12918 | 0.12918 | 0.12918 | 1 | 0 | 0.99483 | -0.098326 | 35.4888
20 | 0.0099247 | 0.0024876 | -0.0099236 | -0.0024871 | 1.0792e-06 | 5.2813e-07 | 0.015002 | 0.015002 | 0.015002 | 0.98444 | -0.29938 | 0.98433 | -0.30166 | 4.1213
21 | -0.0099247 | -0.0024876 | 0.0099264 | 0.0024884 | 1.6536e-06 | 8.0915e-07 | 0.015002 | 0.015002 | 0.015002 | 0.98444 | -0.29938 | 0.98462 | -0.29588 | 4.1213
22 | -0.015256 | -0.0038242 | 0.015261 | 0.0038269 | 4.7113e-06 | 2.7145e-06 | 0.023056 | 0.023056 | 0.023056 | 0.98462 | -0.29588 | 0.98495 | -0.2894 | 6.3341
23 | 0.087575 | 0.022209 | -0.087548 | -0.022191 | 2.733e-05 | 1.7436e-05 | 0.13109 | 0.13109 | 0.13109 | 0.99481 | -0.099158 | 0.99447 | -0.10565 | 36.0127
24 | 0.084 | 0.021302 | -0.083983 | -0.021291 | 1.6945e-05 | 1.0808e-05 | 0.12578 | 0.12578 | 0.12578 | 0.99447 | -0.10565 | 0.99425 | -0.10985 | 34.5542
25 | 0.072456 | 0.018402 | -0.072192 | -0.018234 | 0.00026392 | 0.00016814 | 0.10853 | 0.10853 | 0.10853 | 0.99425 | -0.10985 | 0.99029 | -0.18583 | 29.8147
26 | 0.068447 | 0.017296 | -0.068366 | -0.017244 | 8.1395e-05 | 5.1829e-05 | 0.1029 | 0.1029 | 0.1029 | 0.99029 | -0.18583 | 0.98901 | -0.21067 | 28.2691
27 | 0.0092837 | 0.0023269 | -0.0092827 | -0.0023265 | 1.0125e-06 | 4.7426e-07 | 0.014044 | 0.014044 | 0.014044 | 0.98362 | -0.31537 | 0.98351 | -0.31765 | 3.8584
28 | -0.0092837 | -0.0023269 | 0.0092903 | 0.00233 | 6.5839e-06 | 3.0829e-06 | 0.014044 | 0.014044 | 0.014044 | 0.98362 | -0.31537 | 0.98438 | -0.30049 | 3.8584
29 | -0.0092903 | -0.00233 | 0.0092919 | 0.0023308 | 1.6042e-06 | 7.5092e-07 | 0.014044 | 0.014044 | 0.014044 | 0.98438 | -0.30049 | 0.98457 | -0.29687 | 3.8582
30 | -0.014771 | -0.003704 | 0.014776 | 0.003707 | 5.1294e-06 | 2.9337e-06 | 0.022325 | 0.022325 | 0.022325 | 0.98457 | -0.29687 | 0.98494 | -0.28958 | 6.1332
31 | -0.021361 | -0.0053557 | 0.021391 | 0.0053739 | 3.004e-05 | 1.8245e-05 | 0.032271 | 0.032271 | 0.032271 | 0.98495 | -0.2894 | 0.98647 | -0.25993 | 8.8658
32 | 0.086299 | 0.021905 | -0.08628 | -0.021893 | 1.8723e-05 | 1.1944e-05 | 0.12918 | 0.12918 | 0.12918 | 0.99483 | -0.098326 | 0.9946 | -0.10284 | 35.4888
33 | 0.0070101 | 0.0017562 | -0.0070084 | -0.0017556 | 1.6959e-06 | 5.5191e-07 | 0.010488 | 0.010488 | 0.010488 | 0.9946 | -0.10284 | 0.99433 | -0.10792 | 2.8812
34 | 0.07927 | 0.020137 | -0.07923 | -0.020112 | 4.0273e-05 | 2.5676e-05 | 0.11869 | 0.11869 | 0.11869 | 0.9946 | -0.10284 | 0.99405 | -0.1134 | 32.6077
35 | 0.0052062 | 0.0013043 | -0.0052051 | -0.0013042 | 1.1407e-06 | 8.0186e-08 | 0.0077909 | 0.0077911 | 0.0077911 | 0.99433 | -0.10792 | 0.9941 | -0.11252 | 2.1404
36 | 0.0018022 | 0.00045134 | -0.0018021 | -0.00045164 | 7.4644e-08 | -3.072e-07 | 0.0026968 | 0.0026969 | 0.0026969 | 0.99433 | -0.10792 | 0.99429 | -0.10879 | 0.74092
37 | 0.077044 | 0.019564 | -0.076955 | -0.019507 | 8.8593e-05 | 5.647e-05 | 0.11542 | 0.11542 | 0.11542 | 0.99405 | -0.1134 | 0.9928 | -0.13732 | 31.7088
38 | -0.0017132 | -0.00042925 | 0.0017132 | 0.00042921 | 8.1492e-09 | -3.7405e-08 | 0.0025677 | 0.0025677 | 0.0025677 | 0.99279 | -0.13742 | 0.9928 | -0.13732 | 0.70542
39 | 0.0017132 | 0.00042925 | -0.0017132 | -0.00042936 | 2.425e-08 | -1.113e-07 | 0.0025677 | 0.0025678 | 0.0025678 | 0.99279 | -0.13742 | 0.99278 | -0.13772 | 0.70543
40 | 0.075242 | 0.019078 | -0.075159 | -0.019025 | 8.3475e-05 | 5.3198e-05 | 0.11285 | 0.11285 | 0.11285 | 0.9928 | -0.13732 | 0.99159 | -0.16043 | 31.0034
41 | 0.0052051 | 0.0013042 | -0.0052043 | -0.0013042 | 7.5188e-07 | 5.3043e-08 | 0.0077911 | 0.0077913 | 0.0077913 | 0.9941 | -0.11252 | 0.99394 | -0.11555 | 2.1405
42 | 0.0025768 | 0.00064565 | -0.0025767 | -0.00064579 | 8.2204e-08 | -1.383e-07 | 0.0038576 | 0.0038577 | 0.0038577 | 0.99394 | -0.11555 | 0.99391 | -0.11622 | 1.0598
43 | 0.072425 | 0.01834 | -0.0723 | -0.01826 | 0.00012484 | 7.9536e-05 | 0.10875 | 0.10875 | 0.10875 | 0.99159 | -0.16043 | 0.98973 | -0.19639 | 29.8766
44 | -0.0029614 | -0.00074221 | 0.0029616 | 0.0007421 | 1.0297e-07 | -1.107e-07 | 0.0044613 | 0.0044612 | 0.0044613 | 0.98776 | -0.23455 | 0.98779 | -0.23382 | 1.2256
45 | -0.023075 | -0.0057855 | 0.023076 | 0.0057863 | 1.3163e-06 | 8.0523e-07 | 0.03476 | 0.03476 | 0.03476 | 0.98779 | -0.23382 | 0.98785 | -0.23262 | 9.5496
46 | 0.01627 | 0.0040807 | -0.016268 | -0.0040795 | 1.9614e-06 | 1.1439e-06 | 0.024511 | 0.024511 | 0.024511 | 0.98779 | -0.23382 | 0.98766 | -0.23635 | 6.7337
47 | 0.0038426 | 0.00096271 | -0.0038424 | -0.00096278 | 1.8788e-07 | -7.1156e-08 | 0.0057884 | 0.0057885 | 0.0057885 | 0.98779 | -0.23382 | 0.98774 | -0.23485 | 1.5902
48 | 0.068366 | 0.017244 | -0.068288 | -0.017194 | 7.83e-05 | 4.9859e-05 | 0.1029 | 0.1029 | 0.1029 | 0.98901 | -0.21067 | 0.98777 | -0.23462 | 28.2691
49 | 0.066041 | 0.016631 | -0.06598 | -0.016592 | 6.0614e-05 | 3.8585e-05 | 0.099514 | 0.099515 | 0.099515 | 0.98777 | -0.23462 | 0.98678 | -0.25384 | 27.3392
50 | 0.024196 | 0.0060796 | -0.024189 | -0.0060753 | 7.0368e-06 | 4.3236e-06 | 0.036492 | 0.036492 | 0.036492 | 0.98678 | -0.25384 | 0.98647 | -0.25993 | 10.0253
51 | 0.041784 | 0.010513 | -0.041742 | -0.010487 | 4.1502e-05 | 2.6205e-05 | 0.063022 | 0.063022 | 0.063022 | 0.98678 | -0.25384 | 0.98571 | -0.27465 | 17.3139
52 | 0.0084044 | 0.0021062 | -0.0084037 | -0.0021059 | 7.4029e-07 | 3.1669e-07 | 0.012671 | 0.012671 | 0.012671 | 0.98693 | -0.25056 | 0.98684 | -0.25241 | 3.4812
53 | -0.010479 | -0.0026262 | 0.010479 | 0.0026264 | 4.2851e-07 | 2.1575e-07 | 0.015799 | 0.015799 | 0.015799 | 0.98693 | -0.25056 | 0.98698 | -0.24971 | 4.3405
54 | 0.0069977 | 0.0017535 | -0.0069968 | -0.0017533 | 8.4214e-07 | 2.813e-07 | 0.010551 | 0.010552 | 0.010552 | 0.98684 | -0.25241 | 0.98671 | -0.25494 | 2.8988
55 | -0.013014 | -0.0032615 | 0.013017 | 0.0032635 | 3.5053e-06 | 1.933e-06 | 0.01962 | 0.01962 | 0.01962 | 0.98698 | -0.24971 | 0.98727 | -0.24405 | 5.3901
56 | 0.0050811 | 0.0012731 | -0.0050808 | -0.0012731 | 2.9535e-07 | 1.7699e-08 | 0.0076625 | 0.0076626 | 0.0076626 | 0.98671 | -0.25494 | 0.98665 | -0.25616 | 2.1051
57 | -0.014393 | -0.0036083 | 0.014399 | 0.0036113 | 5.2847e-06 | 2.9992e-06 | 0.021694 | 0.021694 | 0.021694 | 0.98727 | -0.24405 | 0.98766 | -0.23635 | 5.9599
58 | 0.0030822 | 0.00077238 | -0.0030821 | -0.00077245 | 6.9279e-08 | -6.4853e-08 | 0.0046484 | 0.0046484 | 0.0046484 | 0.98665 | -0.25616 | 0.98662 | -0.25663 | 1.277
59 | 0.0019987 | 0.00050074 | -0.0019986 | -0.0005009 | 5.1197e-08 | -1.5913e-07 | 0.0030142 | 0.0030143 | 0.0030143 | 0.98665 | -0.25616 | 0.98662 | -0.2567 | 0.8281
60 | 0.0018698 | 0.00046817 | -0.0018697 | -0.00046859 | 1.1469e-07 | -4.198e-07 | 0.0028169 | 0.0028171 | 0.0028171 | 0.98766 | -0.23635 | 0.9876 | -0.23764 | 0.77393
61 | -0.0023269 | -0.00058316 | 0.002327 | 0.00058287 | 1.436e-07 | -2.9118e-07 | 0.0035411 | 0.0035409 | 0.0035411 | 0.97778 | -0.42936 | 0.97784 | -0.42807 | 0.97283
62 | -0.0042859 | -0.0010738 | 0.0042862 | 0.0010738 | 3.0463e-07 | -4.4639e-08 | 0.0065218 | 0.0065217 | 0.0065218 | 0.97784 | -0.42807 | 0.97792 | -0.42657 | 1.7917
63 | -0.0061411 | -0.0015387 | 0.0061422 | 0.0015389 | 1.0641e-06 | 2.732e-07 | 0.0093443 | 0.0093441 | 0.0093443 | 0.97792 | -0.42657 | 0.9781 | -0.42294 | 2.5671
64 | 0.01866 | 0.0046911 | -0.018629 | -0.0046728 | 3.0609e-05 | 1.8297e-05 | 0.028258 | 0.028258 | 0.028258 | 0.98278 | -0.33126 | 0.98102 | -0.36567 | 7.7633
65 | -0.01866 | -0.0046911 | 0.018665 | 0.0046944 | 5.5764e-06 | 3.3328e-06 | 0.028258 | 0.028258 | 0.028258 | 0.98278 | -0.33126 | 0.9831 | -0.32501 | 7.7632
66 | 0.018629 | 0.0046728 | -0.018611 | -0.0046617 | 1.8477e-05 | 1.1047e-05 | 0.028258 | 0.028259 | 0.028259 | 0.98102 | -0.36567 | 0.97996 | -0.3865 | 7.7634
67 | -0.020864 | -0.0052453 | 0.020871 | 0.0052498 | 7.3074e-06 | 4.429e-06 | 0.031585 | 0.031585 | 0.031585 | 0.9831 | -0.32501 | 0.98348 | -0.31767 | 8.6772
68 | -0.0066587 | -0.0016684 | 0.0066601 | 0.0016688 | 1.438e-06 | 4.5117e-07 | 0.01013 | 0.01013 | 0.01013 | 0.9781 | -0.42294 | 0.97834 | -0.4184 | 2.7829
69 | 0.018182 | 0.0045542 | -0.01818 | -0.0045534 | 1.2839e-06 | 7.651e-07 | 0.027607 | 0.027607 | 0.027607 | 0.97996 | -0.3865 | 0.97988 | -0.38798 | 7.5843
70 | -0.040205 | -0.010099 | 0.040251 | 0.010128 | 4.5722e-05 | 2.8843e-05 | 0.060839 | 0.060839 | 0.060839 | 0.98348 | -0.31767 | 0.9847 | -0.29387 | 16.714
71 | 0.019334 | 0.0048496 | -0.019332 | -0.0048482 | 2.4622e-06 | 1.4784e-06 | 0.029254 | 0.029254 | 0.029254 | 0.98348 | -0.31767 | 0.98334 | -0.32035 | 8.0369
72 | 0.009242 | 0.0023052 | -0.0092382 | -0.0023034 | 3.7771e-06 | 1.7772e-06 | 0.014053 | 0.014053 | 0.014053 | 0.97834 | -0.4184 | 0.9779 | -0.42701 | 3.8607
73 | -0.015902 | -0.0039741 | 0.015905 | 0.003976 | 3.3345e-06 | 1.9431e-06 | 0.024182 | 0.024182 | 0.024182 | 0.97834 | -0.4184 | 0.97856 | -0.41399 | 6.6435
74 | 0.017613 | 0.0044112 | -0.017601 | -0.0044039 | 1.2402e-05 | 7.3555e-06 | 0.026745 | 0.026746 | 0.026746 | 0.97988 | -0.38798 | 0.97913 | -0.40278 | 7.3477
75 | -0.042088 | -0.010589 | 0.042104 | 0.010599 | 1.5834e-05 | 1.0001e-05 | 0.063615 | 0.063615 | 0.063615 | 0.9847 | -0.29387 | 0.9851 | -0.286 | 17.4767
76 | 0.0021799 | 0.00054609 | -0.0021798 | -0.00054631 | 8.8389e-08 | -2.1822e-07 | 0.0032986 | 0.0032987 | 0.0032987 | 0.98334 | -0.32035 | 0.9833 | -0.3212 | 0.90623
77 | 0.017152 | 0.0043021 | -0.017147 | -0.0042995 | 4.2927e-06 | 2.5318e-06 | 0.025956 | 0.025956 | 0.025956 | 0.98334 | -0.32035 | 0.98307 | -0.3256 | 7.1307
78 | -0.011101 | -0.0027815 | 0.011103 | 0.0027826 | 2.0653e-06 | 1.0751e-06 | 0.016814 | 0.016814 | 0.016814 | 0.98238 | -0.33922 | 0.98258 | -0.33531 | 4.6193
79 | 0.0088415 | 0.0022152 | -0.0088411 | -0.0022151 | 4.1212e-07 | 1.8618e-07 | 0.013392 | 0.013392 | 0.013392 | 0.98238 | -0.33922 | 0.98233 | -0.34019 | 3.6792
80 | -0.013028 | -0.0032649 | 0.01303 | 0.0032664 | 2.7821e-06 | 1.539e-06 | 0.019729 | 0.019729 | 0.019729 | 0.98258 | -0.33531 | 0.9828 | -0.33083 | 5.42
81 | 0.0072018 | 0.0018042 | -0.0072013 | -0.001804 | 5.7122e-07 | 2.0356e-07 | 0.010909 | 0.010909 | 0.010909 | 0.98233 | -0.34019 | 0.98224 | -0.34186 | 2.997
82 | -0.015293 | -0.0038336 | 0.015297 | 0.0038358 | 3.8131e-06 | 2.2e-06 | 0.023155 | 0.023155 | 0.023155 | 0.9828 | -0.33083 | 0.98307 | -0.3256 | 6.3613
83 | 0.0047967 | 0.0012014 | -0.0047963 | -0.0012014 | 3.7881e-07 | 2.9582e-10 | 0.0072663 | 0.0072664 | 0.0072664 | 0.98224 | -0.34186 | 0.98216 | -0.34352 | 1.9963
84 | 0.0034188 | 0.00085613 | -0.003418 | -0.00085664 | 8.1356e-07 | -5.0242e-07 | 0.0051795 | 0.0051798 | 0.0051798 | 0.98216 | -0.34352 | 0.9819 | -0.34852 | 1.423
85 | -0.044874 | -0.011293 | 0.044974 | 0.011356 | 9.9659e-05 | 6.3044e-05 | 0.0678 | 0.0678 | 0.0678 | 0.9851 | -0.286 | 0.98749 | -0.23964 | 18.6264
86 | -0.001354 | -0.00033934 | 0.001354 | 0.00033912 | 2.8586e-08 | -2.1621e-07 | 0.0020398 | 0.0020397 | 0.0020398 | 0.98772 | -0.23529 | 0.98774 | -0.23485 | 0.56038
87 | -0.06985 | -0.0176 | 0.069971 | 0.017677 | 0.00012128 | 7.7243e-05 | 0.10525 | 0.10525 | 0.10525 | 0.98785 | -0.23262 | 0.98973 | -0.19639 | 28.9146
88 | 0.046774 | 0.011813 | -0.046759 | -0.011803 | 1.5726e-05 | 9.9566e-06 | 0.070489 | 0.070489 | 0.070489 | 0.98785 | -0.23262 | 0.98749 | -0.23964 | 19.3651
89 | 0.0023291 | 0.00058341 | -0.002329 | -0.00058369 | 1.3363e-07 | -2.8793e-07 | 0.0035016 | 0.0035017 | 0.0035017 | 0.98973 | -0.19639 | 0.98967 | -0.1976 | 0.96201
90 | 0.0070418 | 0.001753 | -0.0070402 | -0.0017524 | 1.5947e-06 | 5.5568e-07 | 0.010711 | 0.010711 | 0.010711 | 0.9779 | -0.42701 | 0.97766 | -0.43179 | 2.9426
91 | -0.016574 | -0.0041435 | 0.016579 | 0.0041468 | 5.5554e-06 | 3.2623e-06 | 0.025199 | 0.025199 | 0.025199 | 0.97856 | -0.41399 | 0.97892 | -0.40694 | 6.9228
92 | 0.0041036 | 0.0010164 | -0.0041015 | -0.0010169 | 2.0825e-06 | -4.536e-07 | 0.0062415 | 0.0062421 | 0.0062421 | 0.97766 | -0.43179 | 0.97712 | -0.44254 | 1.7149
93 | -0.017116 | -0.0042812 | 0.017119 | 0.0042832 | 3.3904e-06 | 2.0019e-06 | 0.026014 | 0.026014 | 0.026014 | 0.97892 | -0.40694 | 0.97913 | -0.40278 | 7.1467
94 | 0.0041015 | 0.0010169 | -0.0040996 | -0.0010173 | 1.9426e-06 | -4.2102e-07 | 0.0062421 | 0.0062427 | 0.0062427 | 0.97712 | -0.44254 | 0.97661 | -0.45256 | 1.715
95 | 0.0039335 | 0.00097571 | -0.0039317 | -0.00097624 | 1.819e-06 | -5.2658e-07 | 0.0059897 | 0.0059903 | 0.0059903 | 0.97661 | -0.45256 | 0.97612 | -0.46234 | 1.6457
96 | -0.00027382 | -6.8626e-05 | 0.00027382 | 6.8145e-05 | 2.5216e-09 | -4.8093e-07 | 0.00041744 | 0.00041726 | 0.00041744 | 0.97608 | -0.46313 | 0.97609 | -0.46294 | 0.11468
97 | -0.00027382 | -6.8145e-05 | 0.00027383 | 6.6686e-05 | 7.6349e-09 | -1.4586e-06 | 0.00041726 | 0.00041675 | 0.00041726 | 0.97609 | -0.46294 | 0.97612 | -0.46234 | 0.11463
98 | 0.0036579 | 0.00090955 | -0.0036573 | -0.00090981 | 6.1262e-07 | -2.6513e-07 | 0.0055736 | 0.0055738 | 0.0055738 | 0.97612 | -0.46234 | 0.97594 | -0.46588 | 1.5313
99 | 0.0031824 | 0.0007908 | -0.0031821 | -0.00079103 | 2.9405e-07 | -2.2833e-07 | 0.0048498 | 0.00485 | 0.00485 | 0.97594 | -0.46588 | 0.97584 | -0.46783 | 1.3324
100 | 0.0024373 | 0.00060435 | -0.0024353 | -0.00060781 | 1.9573e-06 | -3.468e-06 | 0.0037141 | 0.0037158 | 0.0037158 | 0.97584 | -0.46783 | 0.97499 | -0.48479 | 1.0208
101 | 0.0024353 | 0.00060781 | -0.002434 | -0.00061003 | 1.2531e-06 | -2.2137e-06 | 0.0037158 | 0.0037169 | 0.0037169 | 0.97499 | -0.48479 | 0.97444 | -0.49561 | 1.0211
102 | -0.0081559 | -0.0020441 | 0.0081566 | 0.0020444 | 6.9753e-07 | 2.9156e-07 | 0.012343 | 0.012343 | 0.012343 | 0.98322 | -0.32315 | 0.98332 | -0.32136 | 3.391
103 | 0.0098394 | 0.0024663 | -0.009838 | -0.0024656 | 1.4224e-06 | 6.9333e-07 | 0.01489 | 0.01489 | 0.01489 | 0.98332 | -0.32136 | 0.98316 | -0.32439 | 4.0906
104 | -0.017996 | -0.0045107 | 0.018013 | 0.0045206 | 1.6664e-05 | 9.9042e-06 | 0.027233 | 0.027233 | 0.027233 | 0.98332 | -0.32136 | 0.98431 | -0.30194 | 7.4816
105 | -0.023801 | -0.0059713 | 0.023816 | 0.0059803 | 1.4694e-05 | 9.0195e-06 | 0.035983 | 0.035983 | 0.035983 | 0.98431 | -0.30194 | 0.98497 | -0.289 | 9.8854
106 | -0.038592 | -0.0096875 | 0.038619 | 0.0097041 | 2.6433e-05 | 1.6653e-05 | 0.058308 | 0.058308 | 0.058308 | 0.98497 | -0.289 | 0.98571 | -0.27465 | 16.0186
107 | 0.014777 | 0.0037072 | -0.014776 | -0.003707 | 4.123e-07 | 2.358e-07 | 0.022325 | 0.022325 | 0.022325 | 0.98497 | -0.289 | 0.98494 | -0.28958 | 6.1332
108 | 0.0031233 | 0.00078242 | -0.003123 | -0.0007827 | 3.1792e-07 | -2.8261e-07 | 0.0047148 | 0.004715 | 0.004715 | 0.98571 | -0.27465 | 0.9856 | -0.27679 | 1.2953

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.29551 | 0.074598

## res_load
| p_mw | q_mvar
0 | 0.0033132 | 0.00083038
1 | 0.00054319 | 0.00013614
2 | 0.0023271 | 0.00058321
3 | 0.0009823 | 0.00024619
4 | 0.0048038 | 0.0012039
5 | 0.0018986 | 0.00047582
6 | 0.004439 | 0.0011125
7 | 0.001728 | 0.00043307
8 | 0.0026294 | 0.000659
9 | 0.01579 | 0.0039573
10 | 0.0072294 | 0.0018119
11 | 0.021001 | 0.0052634
12 | 0.043641 | 0.010938
13 | 0.0016647 | 0.0004172
14 | 0.0099236 | 0.0024871
15 | 0.0053297 | 0.0013357
16 | 0.0068887 | 0.0017265
17 | 0.0035479 | 0.00088919
18 | 0.011527 | 0.0028891
19 | 0.0037442 | 0.00093839
20 | 0.0092827 | 0.0023265
21 | 0.0054793 | 0.0013732
22 | 0.0061 | 0.0015288
23 | 0.0021858 | 0.00054782
24 | 0.0017132 | 0.00042936
25 | 0.0018021 | 0.00045164
26 | 0.0026275 | 0.00065852
27 | 0.0027334 | 0.00068507
28 | 0.0029614 | 0.00074221
29 | 0.0025767 | 0.00064579
30 | 0.0022471 | 0.00056319
31 | 0.0020747 | 0.00051996
32 | 0.001406 | 0.00035238
33 | 0.0025341 | 0.00063511
34 | 0.0019157 | 0.00048013
35 | 0.0013761 | 0.00034489
36 | 0.0030821 | 0.00077245
37 | 0.0019986 | 0.0005009
38 | 0.0018697 | 0.00046859
39 | 0.0023269 | 0.00058316
40 | 0.0019589 | 0.00049094
41 | 0.0018549 | 0.00046489
42 | 0.0021981 | 0.00055091
43 | 0.00051651 | 0.00012945
44 | 0.00042925 | 0.00010758
45 | 0.00056726 | 0.00014217
46 | 0.0018373 | 0.00046046
47 | 0.0022593 | 0.00056624
48 | 0.0019246 | 0.00048235
49 | 0.0016393 | 0.00041085
50 | 0.0022631 | 0.00056719
51 | 0.0024046 | 0.00060265
52 | 0.0018502 | 0.00046371
53 | 0.0013774 | 0.00034522
54 | 0.003418 | 0.00085664
55 | 0.0021798 | 0.00054631
56 | 0.0027706 | 0.00069438
57 | 0.001354 | 0.00033934
58 | 0.0024884 | 0.00062366
59 | 0.0017845 | 0.00044723
60 | 0.002329 | 0.00058369
61 | 0.0021964 | 0.00055047
62 | 0.00066848 | 0.00016754
63 | 0.0029366 | 0.00073598
64 | 0.00053636 | 0.00013443
65 | 0.00016601 | 4.1607e-05
66 | 0.00027382 | 6.8626e-05
67 | 0.00047487 | 0.00011901
68 | 0.00074487 | 0.00018668
69 | 0.00048138 | 0.00012065
70 | 0.002434 | 0.00061003
71 | 0.0081559 | 0.0020441
72 | 0.009838 | 0.0024656
73 | 0.0057883 | 0.0014507
74 | 0.003123 | 0.0007827
75 | 0.0027984 | 0.00070135

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1