## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3379-7_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3379-7_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3379-7_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3379-7_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3379-7_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_3379-7_0_4_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_3379-7_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_3379-7_0_4_node_16 | 0.4 | n |  | TRUE
8 | bus_LV_3379-7_0_4_node_17 | 0.4 | n |  | TRUE
9 | bus_LV_3379-7_0_4_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_3379-7_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_3379-7_0_4_node_8 | 0.4 | n |  | TRUE
12 | bus_LV_3379-7_0_4_node_21 | 0.4 | n |  | TRUE
13 | bus_LV_3379-7_0_4_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_3379-7_0_4_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_3379-7_0_4_node_25 | 0.4 | n |  | TRUE
16 | bus_LV_3379-7_0_4_node_23 | 0.4 | n |  | TRUE
17 | bus_LV_3379-7_0_4_node_37 | 0.4 | n |  | TRUE
18 | bus_LV_3379-7_0_4_node_18 | 0.4 | n |  | TRUE
19 | bus_LV_3379-7_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_3379-7_0_4_node_19 | 0.4 | n |  | TRUE
21 | bus_LV_3379-7_0_4_node_20 | 0.4 | n |  | TRUE
22 | bus_LV_3379-7_0_4_node_15 | 0.4 | n |  | TRUE
23 | bus_LV_3379-7_0_4_node_26 | 0.4 | n |  | TRUE
24 | bus_LV_3379-7_0_4_node_24 | 0.4 | n |  | TRUE
25 | bus_LV_3379-7_0_4_node_22 | 0.4 | n |  | TRUE
26 | bus_LV_3379-7_0_4_node_29 | 0.4 | n |  | TRUE
27 | bus_LV_3379-7_0_4_node_35 | 0.4 | n |  | TRUE
28 | bus_LV_3379-7_0_4_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_3379-7_0_4_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_3379-7_0_4_node_30 | 0.4 | n |  | TRUE
31 | bus_LV_3379-7_0_4_node_31 | 0.4 | n |  | TRUE
32 | bus_LV_3379-7_0_4_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_3379-7_0_4_node_33 | 0.4 | n |  | TRUE
34 | bus_LV_3379-7_0_4_node_34 | 0.4 | n |  | TRUE
35 | bus_MV_153_0_node_109 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3379-7_0_4_load_0 | 0 | 0.0060639 | 0.0015198 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3379-7_0_4_load_1 | 1 | 0.0044537 | 0.0011162 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3379-7_0_4_load_3 | 3 | 0.0012042 | 0.0003018 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3379-7_0_4_load_16 | 7 | 0.0018137 | 0.00045456 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3379-7_0_4_load_17 | 8 | 0.0020375 | 0.00051064 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3379-7_0_4_load_21 | 12 | 0.02582 | 0.0064711 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3379-7_0_4_load_38 | 13 | 0.055241 | 0.013845 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3379-7_0_4_load_25 | 15 | 0.015103 | 0.0037851 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3379-7_0_4_load_23 | 16 | 0.015761 | 0.0039501 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3379-7_0_4_load_37 | 17 | 0.0028764 | 0.00072088 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3379-7_0_4_load_18 | 18 | 0.0014444 | 0.00036199 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3379-7_0_4_load_19 | 20 | 0.012523 | 0.0031386 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3379-7_0_4_load_20 | 21 | 0.07445 | 0.018659 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3379-7_0_4_load_26 | 23 | 0.013772 | 0.0034515 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3379-7_0_4_load_24 | 24 | 0.0075172 | 0.001884 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3379-7_0_4_load_22 | 25 | 0.081538 | 0.020435 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3379-7_0_4_load_35 | 27 | 0.0069027 | 0.00173 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3379-7_0_4_load_28 | 28 | 0.0047671 | 0.0011947 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3379-7_0_4_load_27 | 29 | 0.0075417 | 0.0018901 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3379-7_0_4_load_30 | 30 | 0.033551 | 0.0084086 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3379-7_0_4_load_31 | 31 | 0.01692 | 0.0042405 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3379-7_0_4_load_32 | 32 | 0.032725 | 0.0082017 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3379-7_0_4_load_33 | 33 | 0.0048536 | 0.0012164 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3379-7_0_4_load_34 | 34 | 0.014269 | 0.0035761 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 30 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3379-7_0_4_line_0 |  | 0 | 1 | 0.034654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3379-7_0_4_line_1 |  | 0 | 2 | 0.098759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3379-7_0_4_line_2 |  | 1 | 3 | 0.021105 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3379-7_0_4_line_3 |  | 2 | 4 | 0.084017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_3379-7_0_4_line_4 |  | 2 | 5 | 0.062937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_3379-7_0_4_line_5 |  | 4 | 6 | 0.03122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3379-7_0_4_line_6 |  | 4 | 7 | 0.029104 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_3379-7_0_4_line_7 |  | 5 | 17 | 0.033794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_3379-7_0_4_line_8 |  | 6 | 8 | 0.029188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3379-7_0_4_line_9 |  | 9 | 10 | 0.00735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_3379-7_0_4_line_10 |  | 9 | 11 | 0.082754 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_3379-7_0_4_line_11 |  | 9 | 12 | 0.011901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_3379-7_0_4_line_12 |  | 10 | 15 | 0.024011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_3379-7_0_4_line_13 |  | 10 | 16 | 0.014422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_3379-7_0_4_line_14 |  | 11 | 13 | 0.015089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3379-7_0_4_line_15 |  | 11 | 14 | 0.055028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_3379-7_0_4_line_16 |  | 12 | 25 | 0.013578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3379-7_0_4_line_17 |  | 14 | 18 | 0.025226 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_3379-7_0_4_line_18 |  | 15 | 26 | 0.011276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_3379-7_0_4_line_19 |  | 16 | 24 | 0.028797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3379-7_0_4_line_20 |  | 17 | 20 | 0.016191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3379-7_0_4_line_21 |  | 18 | 19 | 0.025761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3379-7_0_4_line_22 |  | 19 | 20 | 0.028184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3379-7_0_4_line_23 |  | 19 | 21 | 0.043646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3379-7_0_4_line_24 |  | 22 | 23 | 0.018712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3379-7_0_4_line_25 |  | 22 | 24 | 0.011044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3379-7_0_4_line_26 |  | 23 | 29 | 0.015508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3379-7_0_4_line_27 |  | 26 | 30 | 0.024736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_3379-7_0_4_line_28 |  | 26 | 31 | 0.017256 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3379-7_0_4_line_29 |  | 27 | 28 | 0.023273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3379-7_0_4_line_30 |  | 28 | 29 | 0.018313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3379-7_0_4_line_31 |  | 30 | 32 | 0.0051352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3379-7_0_4_line_32 |  | 31 | 33 | 0.0084785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3379-7_0_4_line_33 |  | 33 | 34 | 0.024535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3379-7_0_4_trafo_30 | 0.63 MVA 20/0.4 kV | 35 | 30 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7
0 | 2724585.7501 | 1240602.7674 | 2724576.6575 | 1240569.3277
1 | 2724544.1994 | 1240661.358 | 2724548.4104 | 1240660.3789 | 2724576.3776 | 1240654.483 | 2724590.7474 | 1240651.3375 | 2724593.844 | 1240648.678 | 2724594.955 | 1240644.0419 | 2724587.0037 | 1240607.3776 | 2724585.7501 | 1240602.7674
2 | 2724576.6575 | 1240569.3277 | 2724576.5482 | 1240568.9259 | 2724571.4803 | 1240548.8674
3 | 2724504.7629 | 1240606.8184 | 2724511.6198 | 1240636.1869 | 2724513.4057 | 1240648.4012 | 2724514.3614 | 1240656.2056 | 2724516.9985 | 1240661.0205 | 2724521.2022 | 1240663.6331 | 2724529.0103 | 1240663.8971 | 2724544.1994 | 1240661.358
4 | 2724544.1994 | 1240661.358 | 2724544.8321 | 1240664.0069 | 2724549.011 | 1240663.116 | 2724570.0419 | 1240658.6647 | 2724599.6121 | 1240654.9599 | 2724604.2519 | 1240654.8127
5 | 2724504.7629 | 1240606.8184 | 2724496.4233 | 1240576.7294
6 | 2724504.7629 | 1240606.8184 | 2724527.0014 | 1240602.1365 | 2724526.9365 | 1240595.8632 | 2724526.9106 | 1240595.7621
7 | 2724604.2519 | 1240654.8127 | 2724601.8439 | 1240644.498 | 2724597.7208 | 1240621.6655
8 | 2724496.4233 | 1240576.7294 | 2724518.7204 | 1240571.4259 | 2724521.0274 | 1240567.8269 | 2724520.4055 | 1240565.9326
9 | 2724672.2521 | 1240547.973 | 2724670.1003 | 1240540.9441
10 | 2724623.3407 | 1240508.424 | 2724656.1755 | 1240495.547 | 2724670.1003 | 1240540.9441
11 | 2724670.1003 | 1240540.9441 | 2724658.5359 | 1240543.7527
12 | 2724672.2521 | 1240547.973 | 2724673.3281 | 1240571.9596
13 | 2724672.2521 | 1240547.973 | 2724685.7508 | 1240553.0493
14 | 2724623.3407 | 1240508.424 | 2724627.301 | 1240522.986
15 | 2724623.3407 | 1240508.424 | 2724582.7002 | 1240525.5965 | 2724572.4549 | 1240529.7183
16 | 2724645.8291 | 1240542.9917 | 2724650.8418 | 1240545.6214 | 2724658.5359 | 1240543.7527
17 | 2724572.4549 | 1240529.7183 | 2724578.9037 | 1240554.1062
18 | 2724673.8334 | 1240583.2246 | 2724673.3281 | 1240571.9596
19 | 2724685.7508 | 1240553.0493 | 2724712.7052 | 1240563.1857
20 | 2724597.7208 | 1240621.6655 | 2724597.6631 | 1240621.3464 | 2724593.2782 | 1240606.0976
21 | 2724585.4891 | 1240579.0109 | 2724578.9037 | 1240554.1062
22 | 2724585.4891 | 1240579.0109 | 2724593.2782 | 1240606.0976
23 | 2724620.6063 | 1240563.3237 | 2724621.5837 | 1240569.7274 | 2724585.4891 | 1240579.0109
24 | 2724723.3284 | 1240566.1944 | 2724718.4187 | 1240584.2504
25 | 2724723.3284 | 1240566.1944 | 2724713.4089 | 1240563.4504 | 2724712.7052 | 1240563.1857
26 | 2724718.4187 | 1240584.2504 | 2724716.0403 | 1240592.9971 | 2724714.4644 | 1240599.2449
27 | 2724673.8334 | 1240583.2246 | 2724649.185 | 1240585.3086
28 | 2724673.8334 | 1240583.2246 | 2724677.5056 | 1240600.0858
29 | 2724709.9853 | 1240617.0019 | 2724707.516 | 1240626.7909 | 2724704.5468 | 1240639.6299
30 | 2724714.4644 | 1240599.2449 | 2724709.9853 | 1240617.0019
31 | 2724649.185 | 1240585.3086 | 2724644.0681 | 1240585.7413
32 | 2724677.5056 | 1240600.0858 | 2724679.3099 | 1240608.3701
33 | 2724679.3099 | 1240608.3701 | 2724684.5309 | 1240632.3427

## bus_geodata
| x | y | coords
0 | 2724585.7501 | 1240602.7674
1 | 2724576.6575 | 1240569.3277
2 | 2724544.1994 | 1240661.358
3 | 2724571.4803 | 1240548.8674
4 | 2724504.7629 | 1240606.8184
5 | 2724604.2519 | 1240654.8127
6 | 2724496.4233 | 1240576.7294
7 | 2724526.9106 | 1240595.7621
8 | 2724520.4055 | 1240565.9326
9 | 2724670.1003 | 1240540.9441
10 | 2724672.2521 | 1240547.973
11 | 2724623.3407 | 1240508.424
12 | 2724658.5359 | 1240543.7527
13 | 2724627.301 | 1240522.986
14 | 2724572.4549 | 1240529.7183
15 | 2724673.3281 | 1240571.9596
16 | 2724685.7508 | 1240553.0493
17 | 2724597.7208 | 1240621.6655
18 | 2724578.9037 | 1240554.1062
19 | 2724585.4891 | 1240579.0109
20 | 2724593.2782 | 1240606.0976
21 | 2724620.6063 | 1240563.3237
22 | 2724723.3284 | 1240566.1944
23 | 2724718.4187 | 1240584.2504
24 | 2724712.7052 | 1240563.1857
25 | 2724645.8291 | 1240542.9917
26 | 2724673.8334 | 1240583.2246
27 | 2724704.5468 | 1240639.6299
28 | 2724709.9853 | 1240617.0019
29 | 2724714.4644 | 1240599.2449
30 | 2724649.1851 | 1240585.3086
31 | 2724677.5056 | 1240600.0858
32 | 2724644.0681 | 1240585.7413
33 | 2724679.3099 | 1240608.3701
34 | 2724684.5309 | 1240632.3427
35 | 2724634.119 | 1240586.5824

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97262 | -0.52856 | 0.0060639 | 0.0015198
1 | 0.97244 | -0.53217 | 0.0044537 | 0.0011162
2 | 0.9737 | -0.50725 | 0 | 0
3 | 0.97241 | -0.53264 | 0.0012042 | 0.0003018
4 | 0.9734 | -0.5132 | 0 | 0
5 | 0.97461 | -0.48923 | 0 | 0
6 | 0.97334 | -0.51437 | 0 | 0
7 | 0.97335 | -0.51417 | 0.0018137 | 0.00045456
8 | 0.97328 | -0.51547 | 0.0020375 | 0.00051064
9 | 0.99295 | -0.1344 | 0 | 0
10 | 0.99355 | -0.12273 | 0 | 0
11 | 0.98672 | -0.25374 | 0 | 0
12 | 0.99178 | -0.15701 | 0.02582 | 0.0064711
13 | 0.98595 | -0.26867 | 0.055241 | 0.013845
14 | 0.98123 | -0.35962 | 0 | 0
15 | 0.99596 | -0.076809 | 0.015103 | 0.0037851
16 | 0.99281 | -0.13707 | 0.015761 | 0.0039501
17 | 0.9751 | -0.47957 | 0.0028764 | 0.00072088
18 | 0.97872 | -0.40856 | 0.0014444 | 0.00036199
19 | 0.97619 | -0.45811 | 0 | 0
20 | 0.97538 | -0.47409 | 0.012523 | 0.0031386
21 | 0.97316 | -0.51772 | 0.07445 | 0.018659
22 | 0.99141 | -0.16417 | 0 | 0
23 | 0.99085 | -0.17513 | 0.013772 | 0.0034515
24 | 0.99175 | -0.15772 | 0.0075172 | 0.001884
25 | 0.99076 | -0.17665 | 0.081538 | 0.020435
26 | 0.99714 | -0.054322 | 0 | 0
27 | 0.99023 | -0.18707 | 0.0069027 | 0.00173
28 | 0.99038 | -0.18421 | 0.0047671 | 0.0011947
29 | 0.99057 | -0.18042 | 0.0075417 | 0.0018901
30 | 1 | 0 | -0.41615 | -0.10578
31 | 0.99657 | -0.065232 | 0.01692 | 0.0042405
32 | 0.99985 | -0.0029295 | 0.032725 | 0.0082017
33 | 0.99643 | -0.068077 | 0.0048536 | 0.0012164
34 | 0.99611 | -0.074225 | 0.014269 | 0.0035761
35 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0056589 | 0.001418 | -0.0056579 | -0.0014178 | 9.7404e-07 | 1.9339e-07 | 0.0086575 | 0.0086577 | 0.0086577 | 0.97262 | -0.52856 | 0.97244 | -0.53217 | 2.3785
1 | -0.011723 | -0.0029377 | 0.011735 | 0.0029441 | 1.1912e-05 | 6.3967e-06 | 0.017935 | 0.017934 | 0.017935 | 0.97262 | -0.52856 | 0.9737 | -0.50725 | 4.9271
2 | 0.0012042 | 0.00030155 | -0.0012042 | -0.0003018 | 2.6872e-08 | -2.4463e-07 | 0.0018426 | 0.0018427 | 0.0018427 | 0.97244 | -0.53217 | 0.97241 | -0.53264 | 0.50623
3 | 0.0038526 | 0.00096394 | -0.0038515 | -0.00096428 | 1.092e-06 | -3.4583e-07 | 0.005887 | 0.0058874 | 0.0058874 | 0.9737 | -0.50725 | 0.9734 | -0.5132 | 1.6174
4 | -0.015587 | -0.003908 | 0.015601 | 0.0039158 | 1.3392e-05 | 7.7876e-06 | 0.023821 | 0.023821 | 0.023821 | 0.9737 | -0.50725 | 0.97461 | -0.48923 | 6.5443
5 | 0.0020377 | 0.00051003 | -0.0020376 | -0.00051034 | 1.1359e-07 | -3.1536e-07 | 0.0031147 | 0.0031149 | 0.0031149 | 0.9734 | -0.5132 | 0.97334 | -0.51437 | 0.85574
6 | 0.0018138 | 0.00045425 | -0.0018137 | -0.00045456 | 8.3905e-08 | -3.0806e-07 | 0.0027726 | 0.0027728 | 0.0027728 | 0.9734 | -0.5132 | 0.97335 | -0.51417 | 0.76175
7 | -0.015601 | -0.0039158 | 0.015608 | 0.00392 | 7.191e-06 | 4.1809e-06 | 0.023821 | 0.023821 | 0.023821 | 0.97461 | -0.48923 | 0.9751 | -0.47957 | 6.5442
8 | 0.0020376 | 0.00051034 | -0.0020375 | -0.00051064 | 1.062e-07 | -2.9479e-07 | 0.0031149 | 0.003115 | 0.003115 | 0.97334 | -0.51437 | 0.97328 | -0.51547 | 0.85577
9 | -0.27197 | -0.069128 | 0.27212 | 0.069225 | 0.00015288 | 9.7556e-05 | 0.40792 | 0.40792 | 0.40792 | 0.99295 | -0.1344 | 0.99355 | -0.12273 | 37.3551
10 | 0.16442 | 0.042099 | -0.16348 | -0.041496 | 0.00094449 | 0.00060234 | 0.24672 | 0.24672 | 0.24672 | 0.99295 | -0.1344 | 0.98672 | -0.25374 | 33.89
11 | 0.10755 | 0.027029 | -0.10743 | -0.026955 | 0.00011597 | 7.4064e-05 | 0.1612 | 0.1612 | 0.1612 | 0.99295 | -0.1344 | 0.99178 | -0.15701 | 44.2857
12 | -0.3285 | -0.083397 | 0.32923 | 0.083862 | 0.00072759 | 0.00046472 | 0.49236 | 0.49236 | 0.49236 | 0.99355 | -0.12273 | 0.99596 | -0.076809 | 45.0882
13 | 0.056375 | 0.014172 | -0.056337 | -0.014147 | 3.8566e-05 | 2.4496e-05 | 0.084446 | 0.084446 | 0.084446 | 0.99355 | -0.12273 | 0.99281 | -0.13707 | 23.1996
14 | 0.055281 | 0.01387 | -0.055241 | -0.013845 | 3.933e-05 | 2.4979e-05 | 0.083371 | 0.083371 | 0.083371 | 0.98672 | -0.25374 | 0.98595 | -0.26867 | 22.9042
15 | 0.1082 | 0.027627 | -0.10765 | -0.027275 | 0.00055061 | 0.00035169 | 0.16335 | 0.16335 | 0.16335 | 0.98672 | -0.25374 | 0.98123 | -0.35962 | 44.876
16 | 0.081614 | 0.020484 | -0.081538 | -0.020435 | 7.6362e-05 | 4.8697e-05 | 0.12246 | 0.12246 | 0.12246 | 0.99178 | -0.15701 | 0.99076 | -0.17665 | 33.6431
17 | 0.10765 | 0.027275 | -0.10739 | -0.027114 | 0.00025241 | 0.00016123 | 0.16335 | 0.16335 | 0.16335 | 0.98123 | -0.35962 | 0.97872 | -0.40856 | 44.876
18 | -0.34433 | -0.087647 | 0.3447 | 0.087885 | 0.00037374 | 0.00023875 | 0.51493 | 0.51493 | 0.51493 | 0.99596 | -0.076809 | 0.99714 | -0.054322 | 47.1545
19 | 0.040576 | 0.010197 | -0.040536 | -0.010172 | 3.9952e-05 | 2.5197e-05 | 0.060824 | 0.060824 | 0.060824 | 0.99281 | -0.13707 | 0.99175 | -0.15772 | 16.7099
20 | -0.018484 | -0.0046409 | 0.018489 | 0.0046438 | 4.8319e-06 | 2.8904e-06 | 0.02821 | 0.02821 | 0.02821 | 0.9751 | -0.47957 | 0.97538 | -0.47409 | 7.7501
21 | 0.10595 | 0.026752 | -0.1057 | -0.026591 | 0.00025088 | 0.00016024 | 0.16115 | 0.16115 | 0.16115 | 0.97872 | -0.40856 | 0.97619 | -0.45811 | 44.2728
22 | 0.031036 | 0.0077971 | -0.031012 | -0.0077824 | 2.3661e-05 | 1.4791e-05 | 0.047315 | 0.047315 | 0.047315 | 0.97619 | -0.45811 | 0.97538 | -0.47409 | 12.9986
23 | 0.074662 | 0.018794 | -0.07445 | -0.018659 | 0.00021211 | 0.0001352 | 0.11384 | 0.11384 | 0.11384 | 0.97619 | -0.45811 | 0.97316 | -0.51772 | 31.2743
24 | 0.033008 | 0.0082814 | -0.032991 | -0.0082707 | 1.7225e-05 | 1.0783e-05 | 0.049545 | 0.049545 | 0.049545 | 0.99141 | -0.16417 | 0.99085 | -0.17513 | 13.6114
25 | -0.033008 | -0.0082814 | 0.033018 | 0.0082878 | 1.0166e-05 | 6.364e-06 | 0.049545 | 0.049545 | 0.049545 | 0.99141 | -0.16417 | 0.99175 | -0.15772 | 13.6114
26 | 0.019219 | 0.0048192 | -0.019215 | -0.0048163 | 4.8449e-06 | 2.9011e-06 | 0.028864 | 0.028864 | 0.028864 | 0.99085 | -0.17513 | 0.99057 | -0.18042 | 7.9296
27 | -0.38077 | -0.096934 | 0.38177 | 0.097573 | 0.0010002 | 0.00063916 | 0.56875 | 0.56875 | 0.56875 | 0.99714 | -0.054322 | 1 | 0 | 52.0836
28 | 0.036068 | 0.0090487 | -0.036049 | -0.0090369 | 1.8749e-05 | 1.1774e-05 | 0.053826 | 0.053827 | 0.053827 | 0.99714 | -0.054322 | 0.99657 | -0.065232 | 14.7875
29 | -0.0069027 | -0.00173 | 0.0069036 | 0.0017303 | 9.39e-07 | 3.0152e-07 | 0.010373 | 0.010372 | 0.010373 | 0.99023 | -0.18707 | 0.99038 | -0.18421 | 2.8496
30 | -0.011671 | -0.002925 | 0.011673 | 0.0029261 | 2.1115e-06 | 1.1157e-06 | 0.017535 | 0.017535 | 0.017535 | 0.99038 | -0.18421 | 0.99057 | -0.18042 | 4.8173
31 | 0.03273 | 0.0082046 | -0.032725 | -0.0082017 | 4.5678e-06 | 2.856e-06 | 0.048703 | 0.048703 | 0.048703 | 1 | 0 | 0.99985 | -0.0029295 | 13.38
32 | 0.019129 | 0.0047964 | -0.019126 | -0.0047949 | 2.5939e-06 | 1.5497e-06 | 0.028563 | 0.028563 | 0.028563 | 0.99657 | -0.065232 | 0.99643 | -0.068077 | 7.847
33 | 0.014273 | 0.0035784 | -0.014269 | -0.0035761 | 4.18e-06 | 2.3557e-06 | 0.021315 | 0.021315 | 0.021315 | 0.99643 | -0.068077 | 0.99611 | -0.074225 | 5.8558

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.4497 | 0.11419

## res_load
| p_mw | q_mvar
0 | 0.0060639 | 0.0015198
1 | 0.0044537 | 0.0011162
2 | 0.0012042 | 0.0003018
3 | 0.0018137 | 0.00045456
4 | 0.0020375 | 0.00051064
5 | 0.02582 | 0.0064711
6 | 0.055241 | 0.013845
7 | 0.015103 | 0.0037851
8 | 0.015761 | 0.0039501
9 | 0.0028764 | 0.00072088
10 | 0.0014444 | 0.00036199
11 | 0.012523 | 0.0031386
12 | 0.07445 | 0.018659
13 | 0.013772 | 0.0034515
14 | 0.0075172 | 0.001884
15 | 0.081538 | 0.020435
16 | 0.0069027 | 0.00173
17 | 0.0047671 | 0.0011947
18 | 0.0075417 | 0.0018901
19 | 0.033551 | 0.0084086
20 | 0.01692 | 0.0042405
21 | 0.032725 | 0.0082017
22 | 0.0048536 | 0.0012164
23 | 0.014269 | 0.0035761

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1