## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_3901-102_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_3901-102_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_3901-102_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_3901-102_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_3901-102_0_5_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_3901-102_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_3901-102_0_5_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_3901-102_0_5_node_10 | 0.4 | n |  | TRUE
8 | bus_LV_3901-102_0_5_node_4 | 0.4 | n |  | TRUE
9 | bus_LV_3901-102_0_5_node_6 | 0.4 | n |  | TRUE
10 | bus_LV_3901-102_0_5_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_3901-102_0_5_node_32 | 0.4 | n |  | TRUE
12 | bus_LV_3901-102_0_5_node_51 | 0.4 | n |  | TRUE
13 | bus_LV_3901-102_0_5_node_57 | 0.4 | n |  | TRUE
14 | bus_LV_3901-102_0_5_node_8 | 0.4 | n |  | TRUE
15 | bus_LV_3901-102_0_5_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_3901-102_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_3901-102_0_5_node_13 | 0.4 | n |  | TRUE
18 | bus_LV_3901-102_0_5_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_3901-102_0_5_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_3901-102_0_5_node_14 | 0.4 | n |  | TRUE
21 | bus_LV_3901-102_0_5_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_3901-102_0_5_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_3901-102_0_5_node_16 | 0.4 | n |  | TRUE
24 | bus_LV_3901-102_0_5_node_17 | 0.4 | n |  | TRUE
25 | bus_LV_3901-102_0_5_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_3901-102_0_5_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_3901-102_0_5_node_33 | 0.4 | n |  | TRUE
28 | bus_LV_3901-102_0_5_node_34 | 0.4 | n |  | TRUE
29 | bus_LV_3901-102_0_5_node_20 | 0.4 | n |  | TRUE
30 | bus_LV_3901-102_0_5_node_21 | 0.4 | n |  | TRUE
31 | bus_LV_3901-102_0_5_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_3901-102_0_5_node_29 | 0.4 | n |  | TRUE
33 | bus_LV_3901-102_0_5_node_30 | 0.4 | n |  | TRUE
34 | bus_LV_3901-102_0_5_node_27 | 0.4 | n |  | TRUE
35 | bus_LV_3901-102_0_5_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_3901-102_0_5_node_49 | 0.4 | n |  | TRUE
37 | bus_LV_3901-102_0_5_node_55 | 0.4 | n |  | TRUE
38 | bus_LV_3901-102_0_5_node_56 | 0.4 | n |  | TRUE
39 | bus_LV_3901-102_0_5_node_54 | 0.4 | n |  | TRUE
40 | bus_LV_3901-102_0_5_node_35 | 0.4 | n |  | TRUE
41 | bus_LV_3901-102_0_5_node_36 | 0.4 | n |  | TRUE
42 | bus_LV_3901-102_0_5_node_37 | 0.4 | n |  | TRUE
43 | bus_LV_3901-102_0_5_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_3901-102_0_5_node_38 | 0.4 | n |  | TRUE
45 | bus_LV_3901-102_0_5_node_53 | 0.4 | n |  | TRUE
46 | bus_LV_3901-102_0_5_node_41 | 0.4 | n |  | TRUE
47 | bus_LV_3901-102_0_5_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_3901-102_0_5_node_77 | 0.4 | n |  | TRUE
49 | bus_LV_3901-102_0_5_node_39 | 0.4 | n |  | TRUE
50 | bus_LV_3901-102_0_5_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_3901-102_0_5_node_76 | 0.4 | n |  | TRUE
52 | bus_LV_3901-102_0_5_node_75 | 0.4 | n |  | TRUE
53 | bus_LV_3901-102_0_5_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_3901-102_0_5_node_78 | 0.4 | n |  | TRUE
55 | bus_LV_3901-102_0_5_node_43 | 0.4 | n |  | TRUE
56 | bus_LV_3901-102_0_5_node_44 | 0.4 | n |  | TRUE
57 | bus_LV_3901-102_0_5_node_47 | 0.4 | n |  | TRUE
58 | bus_LV_3901-102_0_5_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_3901-102_0_5_node_58 | 0.4 | n |  | TRUE
60 | bus_LV_3901-102_0_5_node_48 | 0.4 | n |  | TRUE
61 | bus_LV_3901-102_0_5_node_50 | 0.4 | n |  | TRUE
62 | bus_LV_3901-102_0_5_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_3901-102_0_5_node_60 | 0.4 | n |  | TRUE
64 | bus_LV_3901-102_0_5_node_61 | 0.4 | n |  | TRUE
65 | bus_LV_3901-102_0_5_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_3901-102_0_5_node_63 | 0.4 | n |  | TRUE
67 | bus_LV_3901-102_0_5_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_3901-102_0_5_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_3901-102_0_5_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_3901-102_0_5_node_65 | 0.4 | n |  | TRUE
71 | bus_LV_3901-102_0_5_node_66 | 0.4 | n |  | TRUE
72 | bus_LV_3901-102_0_5_node_67 | 0.4 | n |  | TRUE
73 | bus_LV_3901-102_0_5_node_71 | 0.4 | n |  | TRUE
74 | bus_LV_3901-102_0_5_node_73 | 0.4 | n |  | TRUE
75 | bus_LV_3901-102_0_5_node_74 | 0.4 | n |  | TRUE
76 | bus_MV_151_1_node_5 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_3901-102_0_5_load_0 | 0 | 0.00036346 | 9.109e-05 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_3901-102_0_5_load_2 | 2 | 0.00039039 | 9.7841e-05 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_3901-102_0_5_load_5 | 5 | 0.048471 | 0.012148 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_3901-102_0_5_load_26 | 6 | 0.00048279 | 0.000121 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_3901-102_0_5_load_4 | 8 | 0.0019996 | 0.00050114 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_3901-102_0_5_load_6 | 9 | 0.027307 | 0.0068438 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_3901-102_0_5_load_7 | 10 | 0.0051812 | 0.0012985 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_3901-102_0_5_load_8 | 14 | 0.0071215 | 0.0017848 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_3901-102_0_5_load_9 | 15 | 0.010609 | 0.0026589 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_3901-102_0_5_load_13 | 17 | 0.00014556 | 3.6482e-05 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_3901-102_0_5_load_15 | 18 | 0.014524 | 0.0036401 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_3901-102_0_5_load_24 | 19 | 0.00034424 | 8.6274e-05 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_3901-102_0_5_load_14 | 20 | 0.0063488 | 0.0015912 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_3901-102_0_5_load_25 | 21 | 0.0017238 | 0.00043202 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_3901-102_0_5_load_22 | 22 | 0.00047738 | 0.00011964 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_3901-102_0_5_load_16 | 23 | 0.0018827 | 0.00047186 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_3901-102_0_5_load_17 | 24 | 0.01743 | 0.0043683 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_3901-102_0_5_load_18 | 25 | 0.011834 | 0.0029659 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_3901-102_0_5_load_19 | 26 | 0.0064905 | 0.0016267 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_3901-102_0_5_load_33 | 27 | 0.0034622 | 0.0008677 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_3901-102_0_5_load_34 | 28 | 0.0047261 | 0.0011845 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_3901-102_0_5_load_20 | 29 | 0.0043092 | 0.00108 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_3901-102_0_5_load_21 | 30 | 0.00058799 | 0.00014736 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_3901-102_0_5_load_23 | 31 | 0.00047739 | 0.00011965 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_3901-102_0_5_load_29 | 32 | 0.00047745 | 0.00011966 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_3901-102_0_5_load_30 | 33 | 0.0008438 | 0.00021148 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_3901-102_0_5_load_27 | 34 | 0.0003898 | 9.7694e-05 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_3901-102_0_5_load_31 | 35 | 0.0004774 | 0.00011965 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_3901-102_0_5_load_49 | 36 | 0.007865 | 0.0019712 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_3901-102_0_5_load_56 | 38 | 0.0073356 | 0.0018385 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_3901-102_0_5_load_54 | 39 | 0.0036532 | 0.00091557 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_3901-102_0_5_load_35 | 40 | 0.0031887 | 0.00079916 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_3901-102_0_5_load_36 | 41 | 0.0078759 | 0.0019739 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_3901-102_0_5_load_42 | 43 | 0.0058268 | 0.0014603 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_3901-102_0_5_load_38 | 44 | 0.0031536 | 0.00079037 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_3901-102_0_5_load_53 | 45 | 0.0069203 | 0.0017344 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_3901-102_0_5_load_46 | 47 | 0.029241 | 0.0073286 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_3901-102_0_5_load_77 | 48 | 0.016561 | 0.0041505 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_3901-102_0_5_load_40 | 50 | 0.029784 | 0.0074645 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_3901-102_0_5_load_76 | 51 | 0.0065631 | 0.0016449 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_3901-102_0_5_load_75 | 52 | 0.015685 | 0.003931 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_3901-102_0_5_load_78 | 54 | 0.0063074 | 0.0015808 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_3901-102_0_5_load_43 | 55 | 0.0016448 | 0.00041223 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_3901-102_0_5_load_44 | 56 | 0.0014842 | 0.00037198 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_3901-102_0_5_load_47 | 57 | 0.0058356 | 0.0014625 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_3901-102_0_5_load_58 | 59 | 0.0068803 | 0.0017244 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_3901-102_0_5_load_48 | 60 | 0.0063071 | 0.0015807 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_3901-102_0_5_load_50 | 61 | 0.012124 | 0.0030385 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_3901-102_0_5_load_60 | 63 | 0.0061393 | 0.0015386 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_3901-102_0_5_load_62 | 65 | 0.0060215 | 0.0015091 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_3901-102_0_5_load_63 | 66 | 0.0073383 | 0.0018392 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_3901-102_0_5_load_68 | 67 | 0.021901 | 0.0054889 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_3901-102_0_5_load_69 | 68 | 0.019498 | 0.0048866 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_3901-102_0_5_load_64 | 69 | 0.001205 | 0.000302 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_3901-102_0_5_load_65 | 70 | 0.0063415 | 0.0015893 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_3901-102_0_5_load_66 | 71 | 0.0029574 | 0.0007412 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_3901-102_0_5_load_67 | 72 | 0.025646 | 0.0064275 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_3901-102_0_5_load_71 | 73 | 0.036143 | 0.0090582 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_3901-102_0_5_load_73 | 74 | 0.023542 | 0.0059002 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_3901-102_0_5_load_74 | 75 | 0.01654 | 0.0041453 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 40 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_3901-102_0_5_line_0 |  | 0 | 1 | 0.02265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_3901-102_0_5_line_1 |  | 0 | 2 | 0.017363 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_3901-102_0_5_line_2 |  | 1 | 3 | 0.031131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_3901-102_0_5_line_3 |  | 3 | 4 | 0.01632 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_3901-102_0_5_line_4 |  | 3 | 5 | 0.057779 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
5 | LV_3901-102_0_5_line_5 |  | 4 | 6 | 0.026868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_3901-102_0_5_line_6 |  | 4 | 7 | 0.043776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_3901-102_0_5_line_7 |  | 5 | 8 | 0.035409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_3901-102_0_5_line_8 |  | 6 | 21 | 0.012461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_3901-102_0_5_line_9 |  | 7 | 17 | 0.04809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_3901-102_0_5_line_10 |  | 7 | 14 | 0.021339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_3901-102_0_5_line_11 |  | 8 | 9 | 0.044821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_3901-102_0_5_line_12 |  | 9 | 10 | 0.053703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
13 | LV_3901-102_0_5_line_13 |  | 10 | 11 | 0.056802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
14 | LV_3901-102_0_5_line_14 |  | 11 | 12 | 0.041165 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_3901-102_0_5_line_15 |  | 11 | 13 | 0.024499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
16 | LV_3901-102_0_5_line_16 |  | 12 | 36 | 0.027169 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_3901-102_0_5_line_17 |  | 13 | 38 | 0.0088159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
18 | LV_3901-102_0_5_line_18 |  | 14 | 15 | 0.037821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
19 | LV_3901-102_0_5_line_19 |  | 15 | 16 | 0.027082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_3901-102_0_5_line_20 |  | 16 | 18 | 0.038404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_3901-102_0_5_line_21 |  | 17 | 19 | 0.019738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_3901-102_0_5_line_22 |  | 18 | 20 | 0.0091513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_3901-102_0_5_line_23 |  | 19 | 22 | 0.010315 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_3901-102_0_5_line_24 |  | 20 | 23 | 0.014924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_3901-102_0_5_line_25 |  | 21 | 34 | 0.12343 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_3901-102_0_5_line_26 |  | 22 | 29 | 0.0024399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_3901-102_0_5_line_27 |  | 23 | 24 | 0.019555 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_3901-102_0_5_line_28 |  | 25 | 26 | 0.010122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_3901-102_0_5_line_29 |  | 26 | 27 | 0.00067202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_3901-102_0_5_line_30 |  | 27 | 28 | 0.01452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_3901-102_0_5_line_31 |  | 28 | 40 | 0.0057803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_3901-102_0_5_line_32 |  | 29 | 30 | 0.016803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_3901-102_0_5_line_33 |  | 30 | 31 | 0.00038905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_3901-102_0_5_line_34 |  | 31 | 32 | 0.01905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_3901-102_0_5_line_35 |  | 32 | 33 | 0.013636 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_3901-102_0_5_line_36 |  | 33 | 35 | 0.0053245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_3901-102_0_5_line_37 |  | 36 | 60 | 0.0020552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_3901-102_0_5_line_38 |  | 37 | 38 | 0.0033393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
39 | LV_3901-102_0_5_line_39 |  | 37 | 39 | 0.026461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
40 | LV_3901-102_0_5_line_40 |  | 39 | 45 | 0.006802 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
41 | LV_3901-102_0_5_line_41 |  | 40 | 41 | 0.031871 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
42 | LV_3901-102_0_5_line_42 |  | 41 | 42 | 0.040705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
43 | LV_3901-102_0_5_line_43 |  | 42 | 43 | 0.01805 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
44 | LV_3901-102_0_5_line_44 |  | 42 | 44 | 0.014821 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
45 | LV_3901-102_0_5_line_45 |  | 43 | 45 | 0.068678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_3901-102_0_5_line_46 |  | 44 | 49 | 0.015723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_3901-102_0_5_line_47 |  | 46 | 47 | 0.027192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_3901-102_0_5_line_48 |  | 46 | 48 | 0.020374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_3901-102_0_5_line_49 |  | 46 | 49 | 0.058845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_3901-102_0_5_line_50 |  | 47 | 53 | 0.061133 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_3901-102_0_5_line_51 |  | 48 | 54 | 0.0077844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_3901-102_0_5_line_52 |  | 49 | 50 | 0.056813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_3901-102_0_5_line_53 |  | 50 | 51 | 0.012014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_3901-102_0_5_line_54 |  | 51 | 52 | 0.011373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_3901-102_0_5_line_55 |  | 52 | 75 | 0.032087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
56 | LV_3901-102_0_5_line_56 |  | 53 | 56 | 0.019541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_3901-102_0_5_line_57 |  | 55 | 56 | 0.0045869 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_3901-102_0_5_line_58 |  | 57 | 58 | 0.036567 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_3901-102_0_5_line_59 |  | 58 | 59 | 0.03576 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_3901-102_0_5_line_60 |  | 59 | 62 | 0.011284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_3901-102_0_5_line_61 |  | 60 | 61 | 0.017164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_3901-102_0_5_line_62 |  | 61 | 62 | 0.037972 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_3901-102_0_5_line_63 |  | 63 | 64 | 0.013917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_3901-102_0_5_line_64 |  | 64 | 65 | 0.0016818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_3901-102_0_5_line_65 |  | 65 | 66 | 0.015858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_3901-102_0_5_line_66 |  | 66 | 69 | 0.0068829 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_3901-102_0_5_line_67 |  | 67 | 68 | 0.03443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_3901-102_0_5_line_68 |  | 68 | 73 | 0.013149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_3901-102_0_5_line_69 |  | 68 | 72 | 0.086824 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_3901-102_0_5_line_70 |  | 69 | 70 | 0.005084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_3901-102_0_5_line_71 |  | 70 | 71 | 0.010884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_3901-102_0_5_line_72 |  | 71 | 72 | 0.006844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_3901-102_0_5_line_73 |  | 73 | 74 | 0.0013848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_3901-102_0_5_line_74 |  | 74 | 75 | 0.0012079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_3901-102_0_5_trafo_35 | 0.63 MVA 20/0.4 kV | 76 | 40 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2759517.9998 | 1193236.3904 | 2759540.187 | 1193231.833
1 | 2759557.1945 | 1193228.3394 | 2759540.187 | 1193231.833
2 | 2759517.9998 | 1193236.3904 | 2759507.9255 | 1193206.9293
3 | 2759504.5227 | 1193190.9691 | 2759507.9255 | 1193206.9293
4 | 2759507.9255 | 1193206.9293 | 2759565.3771 | 1193200.7907
5 | 2759504.5227 | 1193190.9691 | 2759490.8199 | 1193193.7396 | 2759479.1139 | 1193199.1323
6 | 2759504.5227 | 1193190.9691 | 2759495.4069 | 1193148.1551
7 | 2759599.8457 | 1193208.3115 | 2759567.7214 | 1193200.5402 | 2759565.3771 | 1193200.7907
8 | 2759473.5992 | 1193210.3063 | 2759479.1139 | 1193199.1323 | 2759479.1139 | 1193199.1323
9 | 2759495.4069 | 1193148.1551 | 2759469.6465 | 1193143.7647 | 2759452.7155 | 1193129.782
10 | 2759495.4069 | 1193148.1551 | 2759492.5071 | 1193127.0138
11 | 2759643.7153 | 1193216.8559 | 2759631.9504 | 1193216.078 | 2759599.8457 | 1193208.3115
12 | 2759643.7153 | 1193216.8559 | 2759681.6116 | 1193219.3615 | 2759696.7843 | 1193215.2331
13 | 2759752.7924 | 1193212.1884 | 2759716.5593 | 1193209.8525 | 2759696.7843 | 1193215.2331
14 | 2759752.7924 | 1193212.1884 | 2759754.8898 | 1193171.0861
15 | 2759743.1602 | 1193193.3369 | 2759742.8262 | 1193203.8373 | 2759746.0987 | 1193203.8135 | 2759752.7924 | 1193212.1884
16 | 2759754.8898 | 1193171.0861 | 2759781.5066 | 1193165.6371
17 | 2759743.1602 | 1193193.3369 | 2759743.3423 | 1193184.5229
18 | 2759492.5071 | 1193127.0138 | 2759487.3676 | 1193089.5436
19 | 2759492.3292 | 1193064.5441 | 2759487.0699 | 1193070.9985 | 2759485.8231 | 1193078.2828 | 2759487.3676 | 1193089.5436
20 | 2759492.3292 | 1193064.5441 | 2759530.2186 | 1193058.28
21 | 2759437.4969 | 1193117.2133 | 2759452.7155 | 1193129.782
22 | 2759539.2473 | 1193056.7874 | 2759530.2186 | 1193058.28
23 | 2759437.4969 | 1193117.2133 | 2759429.5436 | 1193110.645
24 | 2759539.2473 | 1193056.7874 | 2759552.565 | 1193054.5856 | 2759553.9721 | 1193054.3543
25 | 2759473.5992 | 1193210.3063 | 2759369.1433 | 1193276.0682
26 | 2759427.6623 | 1193109.0913 | 2759429.5436 | 1193110.645
27 | 2759572.9119 | 1193049.7775 | 2759564.906 | 1193052.5573 | 2759553.9721 | 1193054.3543
28 | 2759653.7659 | 1193046.2208 | 2759643.9645 | 1193043.6947
29 | 2759654.4167 | 1193046.3885 | 2759653.7659 | 1193046.2208
30 | 2759668.4773 | 1193050.0124 | 2759654.4167 | 1193046.3885
31 | 2759674.0972 | 1193051.3602 | 2759671.6295 | 1193050.8248 | 2759668.4773 | 1193050.0124
32 | 2759427.6623 | 1193109.0913 | 2759414.7068 | 1193098.3917
33 | 2759414.4069 | 1193098.144 | 2759414.7068 | 1193098.3917
34 | 2759399.7188 | 1193086.0135 | 2759414.4069 | 1193098.144
35 | 2759389.2053 | 1193077.3307 | 2759399.7188 | 1193086.0135
36 | 2759389.2053 | 1193077.3307 | 2759385.0998 | 1193073.9401
37 | 2759783.5201 | 1193165.225 | 2759781.5066 | 1193165.6371
38 | 2759746.6804 | 1193184.6121 | 2759743.3423 | 1193184.5229
39 | 2759746.6804 | 1193184.6121 | 2759746.979 | 1193174.5779 | 2759747.5507 | 1193164.8847 | 2759747.31 | 1193158.1764
40 | 2759747.066 | 1193151.3788 | 2759747.31 | 1193158.1764
41 | 2759674.0972 | 1193051.3602 | 2759705.2432 | 1193058.1176
42 | 2759745.3701 | 1193064.6717 | 2759723.5954 | 1193062.0993 | 2759705.2432 | 1193058.1176
43 | 2759745.3701 | 1193064.6717 | 2759745.5485 | 1193082.7208
44 | 2759745.3701 | 1193064.6717 | 2759745.2702 | 1193049.8512
45 | 2759745.5485 | 1193082.7208 | 2759745.8047 | 1193108.6331 | 2759747.0086 | 1193149.7792 | 2759747.066 | 1193151.3788
46 | 2759745.1641 | 1193034.1282 | 2759745.2702 | 1193049.8512
47 | 2759752.3892 | 1192979.8067 | 2759778.8094 | 1192986.2408
48 | 2759752.3892 | 1192979.8067 | 2759753.2999 | 1192959.4531
49 | 2759745.1641 | 1193034.1282 | 2759749.9708 | 1193033.7785 | 2759752.3892 | 1192979.8067
50 | 2759838.2061 | 1193000.7056 | 2759778.8094 | 1192986.2408
51 | 2759753.2999 | 1192959.4531 | 2759753.6479 | 1192951.6765
52 | 2759745.1641 | 1193034.1282 | 2759744.2863 | 1192986.4852 | 2759744.9846 | 1192977.3497
53 | 2759744.9846 | 1192977.3497 | 2759745.8575 | 1192965.9313 | 2759745.8788 | 1192965.3692
54 | 2759746.3094 | 1192954.0048 | 2759745.8788 | 1192965.3692
55 | 2759746.3094 | 1192954.0048 | 2759746.8919 | 1192938.6349 | 2759747.8957 | 1192921.9595
56 | 2759838.2061 | 1193000.7056 | 2759842.9496 | 1193001.8666 | 2759849.4696 | 1193009.8923 | 2759849.7361 | 1193014.201
57 | 2759850.0193 | 1193018.7791 | 2759849.7361 | 1193014.201
58 | 2759837.4433 | 1193107.1232 | 2759837.3716 | 1193072.1461 | 2759837.3902 | 1193070.5564
59 | 2759837.4433 | 1193107.1232 | 2759837.5134 | 1193142.8836
60 | 2759837.5355 | 1193154.1671 | 2759837.5134 | 1193142.8836
61 | 2759783.5201 | 1193165.225 | 2759800.3349 | 1193161.7827
62 | 2759837.5355 | 1193154.1671 | 2759800.3349 | 1193161.7827
63 | 2759661.5325 | 1192844.007 | 2759661.0045 | 1192830.0998
64 | 2759661.5325 | 1192844.007 | 2759661.5965 | 1192845.6876
65 | 2759661.5965 | 1192845.6876 | 2759662.2001 | 1192861.5338
66 | 2759662.2001 | 1192861.5338 | 2759662.4621 | 1192868.4118
67 | 2759750.9106 | 1192871.879 | 2759748.8417 | 1192906.2463
68 | 2759748.0515 | 1192919.3715 | 2759748.8417 | 1192906.2463
69 | 2759748.8417 | 1192906.2463 | 2759663.3305 | 1192891.2076
70 | 2759662.6557 | 1192873.4921 | 2759662.4621 | 1192868.4118
71 | 2759662.6557 | 1192873.4921 | 2759663.07 | 1192884.3686
72 | 2759663.3305 | 1192891.2076 | 2759663.07 | 1192884.3686
73 | 2759747.9683 | 1192920.7538 | 2759748.0515 | 1192919.3715
74 | 2759747.9683 | 1192920.7538 | 2759747.8957 | 1192921.9595

## bus_geodata
| x | y | coords
0 | 2759540.187 | 1193231.833
1 | 2759517.9998 | 1193236.3904
2 | 2759557.1945 | 1193228.3394
3 | 2759507.9255 | 1193206.9293
4 | 2759504.5227 | 1193190.9691
5 | 2759565.3771 | 1193200.7907
6 | 2759479.1139 | 1193199.1323
7 | 2759495.4069 | 1193148.1551
8 | 2759599.8457 | 1193208.3115
9 | 2759643.7153 | 1193216.8559
10 | 2759696.7843 | 1193215.2331
11 | 2759752.7924 | 1193212.1884
12 | 2759754.8898 | 1193171.0861
13 | 2759743.1602 | 1193193.3369
14 | 2759492.5071 | 1193127.0138
15 | 2759487.3676 | 1193089.5436
16 | 2759492.3292 | 1193064.5441
17 | 2759452.7155 | 1193129.782
18 | 2759530.2186 | 1193058.28
19 | 2759437.4969 | 1193117.2133
20 | 2759539.2473 | 1193056.7874
21 | 2759473.5992 | 1193210.3063
22 | 2759429.5436 | 1193110.645
23 | 2759553.9721 | 1193054.3543
24 | 2759572.9119 | 1193049.7775
25 | 2759643.9645 | 1193043.6947
26 | 2759653.7659 | 1193046.2208
27 | 2759654.4167 | 1193046.3885
28 | 2759668.4773 | 1193050.0124
29 | 2759427.6623 | 1193109.0913
30 | 2759414.7068 | 1193098.3917
31 | 2759414.4069 | 1193098.144
32 | 2759399.7188 | 1193086.0135
33 | 2759389.2053 | 1193077.3307
34 | 2759369.1433 | 1193276.0682
35 | 2759385.0998 | 1193073.9401
36 | 2759781.5066 | 1193165.6371
37 | 2759746.6804 | 1193184.6121
38 | 2759743.3423 | 1193184.5229
39 | 2759747.31 | 1193158.1764
40 | 2759674.0972 | 1193051.3602
41 | 2759705.2432 | 1193058.1176
42 | 2759745.3701 | 1193064.6717
43 | 2759745.5485 | 1193082.7208
44 | 2759745.2702 | 1193049.8512
45 | 2759747.066 | 1193151.3788
46 | 2759752.3892 | 1192979.8067
47 | 2759778.8094 | 1192986.2408
48 | 2759753.2999 | 1192959.4531
49 | 2759745.1641 | 1193034.1282
50 | 2759744.9846 | 1192977.3497
51 | 2759745.8788 | 1192965.3692
52 | 2759746.3094 | 1192954.0048
53 | 2759838.2061 | 1193000.7056
54 | 2759753.6479 | 1192951.6765
55 | 2759850.0193 | 1193018.7791
56 | 2759849.7361 | 1193014.201
57 | 2759837.3902 | 1193070.5564
58 | 2759837.4433 | 1193107.1232
59 | 2759837.5134 | 1193142.8836
60 | 2759783.5201 | 1193165.225
61 | 2759800.3349 | 1193161.7827
62 | 2759837.5355 | 1193154.1671
63 | 2759661.0045 | 1192830.0998
64 | 2759661.5325 | 1192844.007
65 | 2759661.5965 | 1192845.6876
66 | 2759662.2001 | 1192861.5338
67 | 2759750.9106 | 1192871.879
68 | 2759748.8417 | 1192906.2463
69 | 2759662.4621 | 1192868.4118
70 | 2759662.6557 | 1192873.4921
71 | 2759663.07 | 1192884.3686
72 | 2759663.3305 | 1192891.2076
73 | 2759748.0515 | 1192919.3715
74 | 2759747.9683 | 1192920.7538
75 | 2759747.8957 | 1192921.9595
76 | 2759745.3701 | 1193064.6717

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1