## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5002-91_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5002-91_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5002-91_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5002-91_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5002-91_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5002-91_0_4_node_49 | 0.4 | n |  | TRUE
6 | bus_LV_5002-91_0_4_node_48 | 0.4 | n |  | TRUE
7 | bus_LV_5002-91_0_4_node_50 | 0.4 | n |  | TRUE
8 | bus_LV_5002-91_0_4_node_47 | 0.4 | n |  | TRUE
9 | bus_LV_5002-91_0_4_node_5 | 0.4 | n |  | TRUE
10 | bus_LV_5002-91_0_4_node_6 | 0.4 | n |  | TRUE
11 | bus_LV_5002-91_0_4_node_7 | 0.4 | n |  | TRUE
12 | bus_LV_5002-91_0_4_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_5002-91_0_4_node_58 | 0.4 | n |  | TRUE
14 | bus_LV_5002-91_0_4_node_57 | 0.4 | n |  | TRUE
15 | bus_LV_5002-91_0_4_node_9 | 0.4 | n |  | TRUE
16 | bus_LV_5002-91_0_4_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_5002-91_0_4_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_5002-91_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_5002-91_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_5002-91_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_5002-91_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_5002-91_0_4_node_24 | 0.4 | n |  | TRUE
23 | bus_LV_5002-91_0_4_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_5002-91_0_4_node_35 | 0.4 | n |  | TRUE
25 | bus_LV_5002-91_0_4_node_32 | 0.4 | n |  | TRUE
26 | bus_LV_5002-91_0_4_node_16 | 0.4 | n |  | TRUE
27 | bus_LV_5002-91_0_4_node_53 | 0.4 | n |  | TRUE
28 | bus_LV_5002-91_0_4_node_56 | 0.4 | n |  | TRUE
29 | bus_LV_5002-91_0_4_node_18 | 0.4 | n |  | TRUE
30 | bus_LV_5002-91_0_4_node_25 | 0.4 | n |  | TRUE
31 | bus_LV_5002-91_0_4_node_33 | 0.4 | n |  | TRUE
32 | bus_LV_5002-91_0_4_node_54 | 0.4 | n |  | TRUE
33 | bus_LV_5002-91_0_4_node_19 | 0.4 | n |  | TRUE
34 | bus_LV_5002-91_0_4_node_20 | 0.4 | n |  | TRUE
35 | bus_LV_5002-91_0_4_node_39 | 0.4 | n |  | TRUE
36 | bus_LV_5002-91_0_4_node_22 | 0.4 | n |  | TRUE
37 | bus_LV_5002-91_0_4_node_37 | 0.4 | n |  | TRUE
38 | bus_LV_5002-91_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_5002-91_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_5002-91_0_4_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_5002-91_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_5002-91_0_4_node_30 | 0.4 | n |  | TRUE
43 | bus_LV_5002-91_0_4_node_31 | 0.4 | n |  | TRUE
44 | bus_LV_5002-91_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_5002-91_0_4_node_34 | 0.4 | n |  | TRUE
46 | bus_LV_5002-91_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_5002-91_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_5002-91_0_4_node_41 | 0.4 | n |  | TRUE
49 | bus_LV_5002-91_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_5002-91_0_4_node_43 | 0.4 | n |  | TRUE
51 | bus_LV_5002-91_0_4_node_44 | 0.4 | n |  | TRUE
52 | bus_LV_5002-91_0_4_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_5002-91_0_4_node_46 | 0.4 | n |  | TRUE
54 | bus_LV_5002-91_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_5002-91_0_4_node_65 | 0.4 | n |  | TRUE
56 | bus_LV_5002-91_0_4_node_52 | 0.4 | n |  | TRUE
57 | bus_LV_5002-91_0_4_node_64 | 0.4 | n |  | TRUE
58 | bus_LV_5002-91_0_4_node_59 | 0.4 | n |  | TRUE
59 | bus_LV_5002-91_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_5002-91_0_4_node_60 | 0.4 | n |  | TRUE
61 | bus_LV_5002-91_0_4_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_5002-91_0_4_node_62 | 0.4 | n |  | TRUE
63 | bus_MV_62_0_node_101 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5002-91_0_4_load_0 | 0 | 0.0029856 | 0.00074825 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5002-91_0_4_load_1 | 1 | 0.005511 | 0.0013812 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5002-91_0_4_load_2 | 2 | 0.0024592 | 0.00061634 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5002-91_0_4_load_3 | 3 | 0.0017464 | 0.0004377 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5002-91_0_4_load_4 | 4 | 0.0041364 | 0.0010367 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5002-91_0_4_load_49 | 5 | 0.0058065 | 0.0014552 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5002-91_0_4_load_48 | 6 | 0.011383 | 0.0028528 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5002-91_0_4_load_50 | 7 | 0.0043977 | 0.0011022 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5002-91_0_4_load_47 | 8 | 0.010294 | 0.00258 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5002-91_0_4_load_5 | 9 | 0.0059613 | 0.001494 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5002-91_0_4_load_6 | 10 | 0.0034676 | 0.00086905 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5002-91_0_4_load_7 | 11 | 0.001677 | 0.0004203 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5002-91_0_4_load_58 | 13 | 0.0016069 | 0.00040272 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5002-91_0_4_load_57 | 14 | 0.0039425 | 0.00098808 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5002-91_0_4_load_9 | 15 | 0.008713 | 0.0021837 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5002-91_0_4_load_10 | 16 | 0.0054154 | 0.0013572 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5002-91_0_4_load_14 | 19 | 0.022822 | 0.0057198 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5002-91_0_4_load_21 | 20 | 0.004683 | 0.0011737 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5002-91_0_4_load_17 | 21 | 0.0097565 | 0.0024452 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5002-91_0_4_load_24 | 22 | 0.0090327 | 0.0022638 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5002-91_0_4_load_35 | 24 | 0.0097977 | 0.0024555 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5002-91_0_4_load_32 | 25 | 0.018527 | 0.0046432 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5002-91_0_4_load_53 | 27 | 0.0080257 | 0.0020114 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5002-91_0_4_load_56 | 28 | 0.0035317 | 0.00088513 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5002-91_0_4_load_25 | 30 | 0.0073055 | 0.0018309 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5002-91_0_4_load_33 | 31 | 0.0036705 | 0.0009199 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5002-91_0_4_load_54 | 32 | 0.003998 | 0.001002 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5002-91_0_4_load_20 | 34 | 0.002485 | 0.00062281 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5002-91_0_4_load_22 | 36 | 0.0058164 | 0.0014577 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5002-91_0_4_load_37 | 37 | 0.0035037 | 0.00087811 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5002-91_0_4_load_26 | 38 | 0.0028839 | 0.00072278 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5002-91_0_4_load_27 | 39 | 0.098659 | 0.024726 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5002-91_0_4_load_28 | 40 | 0.0056725 | 0.0014217 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5002-91_0_4_load_29 | 41 | 0.047523 | 0.01191 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5002-91_0_4_load_30 | 42 | 0.0057341 | 0.0014371 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5002-91_0_4_load_31 | 43 | 0.034057 | 0.0085354 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5002-91_0_4_load_36 | 44 | 0.0059523 | 0.0014918 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5002-91_0_4_load_34 | 45 | 0.0068584 | 0.0017189 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5002-91_0_4_load_38 | 46 | 0.0038307 | 0.00096006 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5002-91_0_4_load_40 | 47 | 0.0019499 | 0.00048869 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5002-91_0_4_load_41 | 48 | 0.0041922 | 0.0010507 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5002-91_0_4_load_42 | 49 | 0.0017063 | 0.00042765 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5002-91_0_4_load_43 | 50 | 0.0060963 | 0.0015279 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5002-91_0_4_load_44 | 51 | 0.0012197 | 0.00030568 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5002-91_0_4_load_45 | 52 | 0.0052772 | 0.0013226 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5002-91_0_4_load_46 | 53 | 0.0043518 | 0.0010907 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5002-91_0_4_load_51 | 54 | 0.0047605 | 0.0011931 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5002-91_0_4_load_65 | 55 | 0.003553 | 0.00089046 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5002-91_0_4_load_52 | 56 | 0.001874 | 0.00046967 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5002-91_0_4_load_59 | 58 | 0.0079676 | 0.0019969 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5002-91_0_4_load_55 | 59 | 0.0014168 | 0.00035508 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5002-91_0_4_load_61 | 61 | 0.0012924 | 0.00032391 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5002-91_0_4_load_62 | 62 | 0.00088053 | 0.00022068 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 41 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5002-91_0_4_line_0 |  | 0 | 1 | 0.0094127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5002-91_0_4_line_1 |  | 0 | 2 | 0.0032288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5002-91_0_4_line_2 |  | 1 | 3 | 0.019874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5002-91_0_4_line_3 |  | 2 | 4 | 0.006643 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5002-91_0_4_line_4 |  | 3 | 5 | 0.0017535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5002-91_0_4_line_5 |  | 4 | 6 | 0.022279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5002-91_0_4_line_6 |  | 5 | 7 | 0.039208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5002-91_0_4_line_7 |  | 6 | 8 | 0.0012242 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5002-91_0_4_line_8 |  | 7 | 54 | 0.002003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5002-91_0_4_line_9 |  | 7 | 55 | 0.074585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5002-91_0_4_line_10 |  | 8 | 53 | 0.0016561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5002-91_0_4_line_11 |  | 9 | 10 | 0.0039578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5002-91_0_4_line_12 |  | 9 | 11 | 0.051162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5002-91_0_4_line_13 |  | 11 | 12 | 0.023846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5002-91_0_4_line_14 |  | 12 | 13 | 0.021139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5002-91_0_4_line_15 |  | 13 | 14 | 0.016806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5002-91_0_4_line_16 |  | 14 | 59 | 0.0052727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5002-91_0_4_line_17 |  | 15 | 16 | 0.0071481 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5002-91_0_4_line_18 |  | 15 | 17 | 0.013167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5002-91_0_4_line_19 |  | 17 | 18 | 0.038142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_5002-91_0_4_line_20 |  | 17 | 19 | 0.020146 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_5002-91_0_4_line_21 |  | 18 | 20 | 0.010376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5002-91_0_4_line_22 |  | 18 | 21 | 0.0072883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5002-91_0_4_line_23 |  | 19 | 22 | 0.0031791 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_5002-91_0_4_line_24 |  | 21 | 29 | 0.0090392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5002-91_0_4_line_25 |  | 22 | 30 | 0.023322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_5002-91_0_4_line_26 |  | 23 | 24 | 0.012187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5002-91_0_4_line_27 |  | 23 | 25 | 0.018533 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5002-91_0_4_line_28 |  | 24 | 27 | 0.037024 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5002-91_0_4_line_29 |  | 25 | 31 | 0.013771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5002-91_0_4_line_30 |  | 26 | 27 | 0.017307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5002-91_0_4_line_31 |  | 26 | 28 | 0.039838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5002-91_0_4_line_32 |  | 28 | 32 | 0.018111 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5002-91_0_4_line_33 |  | 29 | 33 | 0.014099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5002-91_0_4_line_34 |  | 29 | 34 | 0.030063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5002-91_0_4_line_35 |  | 30 | 38 | 0.019307 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_5002-91_0_4_line_36 |  | 31 | 45 | 0.0061763 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5002-91_0_4_line_37 |  | 32 | 59 | 0.0012866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5002-91_0_4_line_38 |  | 33 | 35 | 0.020362 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5002-91_0_4_line_39 |  | 34 | 36 | 0.026147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5002-91_0_4_line_40 |  | 35 | 37 | 0.036562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5002-91_0_4_line_41 |  | 37 | 46 | 0.0077444 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5002-91_0_4_line_42 |  | 38 | 39 | 0.026577 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
43 | LV_5002-91_0_4_line_43 |  | 39 | 40 | 0.0055087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_5002-91_0_4_line_44 |  | 40 | 41 | 0.011123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_5002-91_0_4_line_45 |  | 41 | 42 | 0.011145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5002-91_0_4_line_46 |  | 42 | 43 | 0.015005 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5002-91_0_4_line_47 |  | 43 | 44 | 0.0040171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5002-91_0_4_line_48 |  | 44 | 45 | 0.013667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5002-91_0_4_line_49 |  | 46 | 47 | 0.017624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5002-91_0_4_line_50 |  | 47 | 48 | 0.010115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5002-91_0_4_line_51 |  | 48 | 49 | 0.0092015 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5002-91_0_4_line_52 |  | 49 | 50 | 0.011748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5002-91_0_4_line_53 |  | 50 | 51 | 0.0011857 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5002-91_0_4_line_54 |  | 51 | 52 | 0.0025157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5002-91_0_4_line_55 |  | 52 | 53 | 0.015358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5002-91_0_4_line_56 |  | 54 | 56 | 0.0012346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5002-91_0_4_line_57 |  | 55 | 57 | 0.096462 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5002-91_0_4_line_58 |  | 57 | 58 | 0.2047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5002-91_0_4_line_59 |  | 58 | 60 | 0.077543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5002-91_0_4_line_60 |  | 60 | 61 | 0.013491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5002-91_0_4_line_61 |  | 60 | 62 | 0.027233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5002-91_0_4_trafo_29 | 0.63 MVA 20/0.4 kV | 63 | 41 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2719858.3924 | 1115610.1365 | 2719849.553 | 1115606.9019
1 | 2719858.3924 | 1115610.1365 | 2719861.4246 | 1115611.2461
2 | 2719849.553 | 1115606.9019 | 2719830.889 | 1115600.0722
3 | 2719867.663 | 1115613.5289 | 2719861.4246 | 1115611.2461
4 | 2719829.2423 | 1115599.4696 | 2719830.889 | 1115600.0722
5 | 2719867.663 | 1115613.5289 | 2719888.5855 | 1115621.1851
6 | 2719829.2423 | 1115599.4696 | 2719792.4218 | 1115585.9959
7 | 2719888.5855 | 1115621.1851 | 2719889.7352 | 1115621.6058
8 | 2719792.4218 | 1115585.9959 | 2719790.5408 | 1115585.3076
9 | 2719792.4218 | 1115585.9959 | 2719832.8277 | 1115523.3044
10 | 2719891.2904 | 1115622.1749 | 2719889.7352 | 1115621.6058
11 | 2719599.5792 | 1115627.7667 | 2719595.9514 | 1115629.3486
12 | 2719599.5792 | 1115627.7667 | 2719606.601 | 1115624.7049 | 2719646.4218 | 1115607.1922
13 | 2719668.2505 | 1115597.5922 | 2719646.4218 | 1115607.1922
14 | 2719668.2505 | 1115597.5922 | 2719675.7065 | 1115617.3724
15 | 2719675.7065 | 1115617.3724 | 2719681.6342 | 1115633.0984
16 | 2719683.494 | 1115638.0323 | 2719681.6342 | 1115633.0984
17 | 2719947.6427 | 1115738.9671 | 2719944.0323 | 1115745.1364
18 | 2719954.2934 | 1115727.6028 | 2719947.6427 | 1115738.9671
19 | 2719973.9698 | 1115694.9588 | 2719968.4363 | 1115702.5545 | 2719954.2934 | 1115727.6028
20 | 2719954.2934 | 1115727.6028 | 2719935.185 | 1115721.2197
21 | 2719973.9698 | 1115694.9588 | 2719971.2472 | 1115692.8257 | 2719969.3739 | 1115689.92 | 2719968.5601 | 1115686.5571
22 | 2719973.9698 | 1115694.9588 | 2719977.0451 | 1115696.0538 | 2719980.318 | 1115696.1409 | 2719981.037 | 1115695.9279
23 | 2719935.185 | 1115721.2197 | 2719932.1697 | 1115720.2125
24 | 2719988.1166 | 1115690.7694 | 2719986.1346 | 1115693.3541 | 2719983.4488 | 1115695.2133 | 2719981.037 | 1115695.9279
25 | 2719910.049 | 1115712.8232 | 2719932.1697 | 1115720.2125
26 | 2719769.4125 | 1115689.22 | 2719757.2566 | 1115690.0837
27 | 2719769.4125 | 1115689.22 | 2719787.8252 | 1115687.1155
28 | 2719757.2566 | 1115690.0837 | 2719720.3261 | 1115692.7078
29 | 2719787.8252 | 1115687.1155 | 2719801.5072 | 1115685.5518
30 | 2719703.0626 | 1115693.9345 | 2719720.3261 | 1115692.7078
31 | 2719703.0626 | 1115693.9345 | 2719690.3184 | 1115656.1895
32 | 2719683.9478 | 1115639.2362 | 2719690.1486 | 1115655.6866 | 2719690.3184 | 1115656.1895
33 | 2719988.1166 | 1115690.7694 | 2719989.2408 | 1115687.4338 | 2719989.1793 | 1115683.9079 | 2719987.9396 | 1115680.6033 | 2719985.6605 | 1115677.9119
34 | 2719988.1166 | 1115690.7694 | 2720001.0467 | 1115696.5404 | 2720015.1647 | 1115703.8629
35 | 2719910.049 | 1115712.8232 | 2719891.7365 | 1115706.7059
36 | 2719807.6436 | 1115684.8504 | 2719801.5072 | 1115685.5518
37 | 2719683.9478 | 1115639.2362 | 2719683.494 | 1115638.0323
38 | 2719985.6605 | 1115677.9119 | 2719991.3359 | 1115669.3962 | 2719996.5209 | 1115660.6818
39 | 2720015.1647 | 1115703.8629 | 2720038.375 | 1115715.9013
40 | 2719996.5209 | 1115660.6818 | 2719962.1858 | 1115648.1176
41 | 2719962.1858 | 1115648.1176 | 2719954.913 | 1115645.4563
42 | 2719891.7365 | 1115706.7059 | 2719866.5285 | 1115698.2853
43 | 2719861.3036 | 1115696.54 | 2719866.5285 | 1115698.2853
44 | 2719850.5898 | 1115693.6263 | 2719855.7188 | 1115694.6744 | 2719861.3036 | 1115696.54
45 | 2719850.5898 | 1115693.6263 | 2719839.6705 | 1115691.395
46 | 2719824.9693 | 1115688.3909 | 2719839.6705 | 1115691.395
47 | 2719824.9693 | 1115688.3909 | 2719821.0335 | 1115687.5866
48 | 2719807.6436 | 1115684.8504 | 2719807.6436 | 1115684.8504 | 2719821.0335 | 1115687.5866
49 | 2719938.362 | 1115639.3998 | 2719954.913 | 1115645.4563
50 | 2719938.362 | 1115639.3998 | 2719928.8631 | 1115635.9238
51 | 2719920.222 | 1115632.7618 | 2719928.8631 | 1115635.9238
52 | 2719920.222 | 1115632.7618 | 2719909.1893 | 1115628.7246
53 | 2719908.0759 | 1115628.3172 | 2719909.1893 | 1115628.7246
54 | 2719905.7133 | 1115627.4527 | 2719908.0759 | 1115628.3172
55 | 2719905.7133 | 1115627.4527 | 2719891.2904 | 1115622.1749
56 | 2719790.5408 | 1115585.3076 | 2719789.3814 | 1115584.8834
57 | 2719832.8277 | 1115523.3044 | 2719810.9057 | 1115429.3734
58 | 2719810.9057 | 1115429.3734 | 2719695.8713 | 1115260.0546
59 | 2719619.2174 | 1115271.7569 | 2719686.9552 | 1115261.5317 | 2719695.8713 | 1115260.0546
60 | 2719619.2174 | 1115271.7569 | 2719605.9298 | 1115274.0878
61 | 2719619.2174 | 1115271.7569 | 2719614.4385 | 1115244.9468

## bus_geodata
| x | y | coords
0 | 2719858.3924 | 1115610.1365
1 | 2719849.553 | 1115606.9019
2 | 2719861.4246 | 1115611.2461
3 | 2719830.889 | 1115600.0722
4 | 2719867.663 | 1115613.5289
5 | 2719829.2423 | 1115599.4696
6 | 2719888.5855 | 1115621.1851
7 | 2719792.4218 | 1115585.9959
8 | 2719889.7352 | 1115621.6058
9 | 2719599.5792 | 1115627.7667
10 | 2719595.9514 | 1115629.3486
11 | 2719646.4218 | 1115607.1922
12 | 2719668.2505 | 1115597.5922
13 | 2719675.7065 | 1115617.3724
14 | 2719681.6342 | 1115633.0984
15 | 2719947.6427 | 1115738.9671
16 | 2719944.0323 | 1115745.1364
17 | 2719954.2934 | 1115727.6028
18 | 2719973.9698 | 1115694.9588
19 | 2719935.185 | 1115721.2197
20 | 2719968.5601 | 1115686.5571
21 | 2719981.037 | 1115695.9279
22 | 2719932.1697 | 1115720.2125
23 | 2719769.4125 | 1115689.22
24 | 2719757.2566 | 1115690.0837
25 | 2719787.8252 | 1115687.1155
26 | 2719703.0626 | 1115693.9345
27 | 2719720.3261 | 1115692.7078
28 | 2719690.3184 | 1115656.1895
29 | 2719988.1166 | 1115690.7694
30 | 2719910.049 | 1115712.8232
31 | 2719801.5072 | 1115685.5518
32 | 2719683.9478 | 1115639.2362
33 | 2719985.6605 | 1115677.9119
34 | 2720015.1647 | 1115703.8629
35 | 2719996.5209 | 1115660.6818
36 | 2720038.375 | 1115715.9013
37 | 2719962.1858 | 1115648.1176
38 | 2719891.7365 | 1115706.7059
39 | 2719866.5285 | 1115698.2853
40 | 2719861.3036 | 1115696.54
41 | 2719850.5898 | 1115693.6263
42 | 2719839.6705 | 1115691.395
43 | 2719824.9693 | 1115688.3909
44 | 2719821.0335 | 1115687.5866
45 | 2719807.6436 | 1115684.8504
46 | 2719954.913 | 1115645.4563
47 | 2719938.362 | 1115639.3998
48 | 2719928.8631 | 1115635.9238
49 | 2719920.222 | 1115632.7618
50 | 2719909.1893 | 1115628.7246
51 | 2719908.0759 | 1115628.3172
52 | 2719905.7133 | 1115627.4527
53 | 2719891.2904 | 1115622.1749
54 | 2719790.5408 | 1115585.3076
55 | 2719832.8277 | 1115523.3044
56 | 2719789.3814 | 1115584.8834
57 | 2719810.9057 | 1115429.3734
58 | 2719695.8713 | 1115260.0546
59 | 2719683.494 | 1115638.0323
60 | 2719619.2175 | 1115271.7569
61 | 2719605.9298 | 1115274.0878
62 | 2719614.4385 | 1115244.9468
63 | 2719769.4125 | 1115689.22

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1