## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5176-6_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5176-6_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5176-6_0_4_node_3 | 0.4 | n |  | TRUE
3 | bus_LV_5176-6_0_4_node_6 | 0.4 | n |  | TRUE
4 | bus_LV_5176-6_0_4_node_2 | 0.4 | n |  | TRUE
5 | bus_LV_5176-6_0_4_node_7 | 0.4 | n |  | TRUE
6 | bus_LV_5176-6_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_5176-6_0_4_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_5176-6_0_4_node_11 | 0.4 | n |  | TRUE
9 | bus_LV_5176-6_0_4_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_5176-6_0_4_node_15 | 0.4 | n |  | TRUE
11 | bus_LV_5176-6_0_4_node_10 | 0.4 | n |  | TRUE
12 | bus_LV_5176-6_0_4_node_33 | 0.4 | n |  | TRUE
13 | bus_LV_5176-6_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_5176-6_0_4_node_28 | 0.4 | n |  | TRUE
15 | bus_LV_5176-6_0_4_node_26 | 0.4 | n |  | TRUE
16 | bus_LV_5176-6_0_4_node_32 | 0.4 | n |  | TRUE
17 | bus_LV_5176-6_0_4_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_5176-6_0_4_node_35 | 0.4 | n |  | TRUE
19 | bus_LV_5176-6_0_4_node_8 | 0.4 | n |  | TRUE
20 | bus_LV_5176-6_0_4_node_24 | 0.4 | n |  | TRUE
21 | bus_LV_5176-6_0_4_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_5176-6_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_5176-6_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_5176-6_0_4_node_18 | 0.4 | n |  | TRUE
25 | bus_LV_5176-6_0_4_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_5176-6_0_4_node_20 | 0.4 | n |  | TRUE
27 | bus_LV_5176-6_0_4_node_12 | 0.4 | n |  | TRUE
28 | bus_LV_5176-6_0_4_node_13 | 0.4 | n |  | TRUE
29 | bus_LV_5176-6_0_4_node_14 | 0.4 | n |  | TRUE
30 | bus_LV_5176-6_0_4_node_74 | 0.4 | n |  | TRUE
31 | bus_LV_5176-6_0_4_node_73 | 0.4 | n |  | TRUE
32 | bus_LV_5176-6_0_4_node_71 | 0.4 | n |  | TRUE
33 | bus_LV_5176-6_0_4_node_72 | 0.4 | n |  | TRUE
34 | bus_LV_5176-6_0_4_node_21 | 0.4 | n |  | TRUE
35 | bus_LV_5176-6_0_4_node_23 | 0.4 | n |  | TRUE
36 | bus_LV_5176-6_0_4_node_30 | 0.4 | n |  | TRUE
37 | bus_LV_5176-6_0_4_node_31 | 0.4 | n |  | TRUE
38 | bus_LV_5176-6_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_5176-6_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_5176-6_0_4_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_5176-6_0_4_node_68 | 0.4 | n |  | TRUE
42 | bus_LV_5176-6_0_4_node_69 | 0.4 | n |  | TRUE
43 | bus_LV_5176-6_0_4_node_66 | 0.4 | n |  | TRUE
44 | bus_LV_5176-6_0_4_node_70 | 0.4 | n |  | TRUE
45 | bus_LV_5176-6_0_4_node_38 | 0.4 | n |  | TRUE
46 | bus_LV_5176-6_0_4_node_64 | 0.4 | n |  | TRUE
47 | bus_LV_5176-6_0_4_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_5176-6_0_4_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_5176-6_0_4_node_42 | 0.4 | n |  | TRUE
50 | bus_LV_5176-6_0_4_node_40 | 0.4 | n |  | TRUE
51 | bus_LV_5176-6_0_4_node_41 | 0.4 | n |  | TRUE
52 | bus_LV_5176-6_0_4_node_43 | 0.4 | n |  | TRUE
53 | bus_LV_5176-6_0_4_node_45 | 0.4 | n |  | TRUE
54 | bus_LV_5176-6_0_4_node_46 | 0.4 | n |  | TRUE
55 | bus_LV_5176-6_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_5176-6_0_4_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_5176-6_0_4_node_63 | 0.4 | n |  | TRUE
58 | bus_LV_5176-6_0_4_node_56 | 0.4 | n |  | TRUE
59 | bus_LV_5176-6_0_4_node_52 | 0.4 | n |  | TRUE
60 | bus_LV_5176-6_0_4_node_65 | 0.4 | n |  | TRUE
61 | bus_LV_5176-6_0_4_node_62 | 0.4 | n |  | TRUE
62 | bus_LV_5176-6_0_4_node_54 | 0.4 | n |  | TRUE
63 | bus_LV_5176-6_0_4_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_5176-6_0_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_5176-6_0_4_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_5176-6_0_4_node_53 | 0.4 | n |  | TRUE
67 | bus_LV_5176-6_0_4_node_55 | 0.4 | n |  | TRUE
68 | bus_LV_5176-6_0_4_node_57 | 0.4 | n |  | TRUE
69 | bus_LV_5176-6_0_4_node_58 | 0.4 | n |  | TRUE
70 | bus_LV_5176-6_0_4_node_59 | 0.4 | n |  | TRUE
71 | bus_LV_5176-6_0_4_node_60 | 0.4 | n |  | TRUE
72 | bus_LV_5176-6_0_4_node_61 | 0.4 | n |  | TRUE
73 | bus_LV_5176-6_0_4_node_67 | 0.4 | n |  | TRUE
74 | bus_MV_73_1_node_61 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5176-6_0_4_load_0 | 0 | 0.0078263 | 0.0019615 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5176-6_0_4_load_3 | 2 | 0.0029851 | 0.00074814 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5176-6_0_4_load_6 | 3 | 0.0014471 | 0.00036268 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5176-6_0_4_load_7 | 5 | 0.0005747 | 0.00014403 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5176-6_0_4_load_5 | 6 | 0.0011583 | 0.0002903 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5176-6_0_4_load_11 | 8 | 0.00048302 | 0.00012106 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5176-6_0_4_load_9 | 9 | 0.00066132 | 0.00016574 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5176-6_0_4_load_15 | 10 | 0.00098036 | 0.0002457 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5176-6_0_4_load_33 | 12 | 0.002339 | 0.0005862 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5176-6_0_4_load_27 | 13 | 0.0016819 | 0.00042152 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5176-6_0_4_load_28 | 14 | 0.0021827 | 0.00054703 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5176-6_0_4_load_32 | 16 | 0.0026891 | 0.00067395 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5176-6_0_4_load_34 | 17 | 0.0055582 | 0.001393 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5176-6_0_4_load_35 | 18 | 0.0033291 | 0.00083435 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5176-6_0_4_load_8 | 19 | 0.0023531 | 0.00058974 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5176-6_0_4_load_24 | 20 | 0.0026019 | 0.0006521 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5176-6_0_4_load_25 | 21 | 0.0047184 | 0.0011826 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5176-6_0_4_load_22 | 22 | 0.0085065 | 0.0021319 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5176-6_0_4_load_17 | 23 | 0.0044448 | 0.001114 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5176-6_0_4_load_18 | 24 | 0.0036732 | 0.00092059 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5176-6_0_4_load_20 | 26 | 0.0069833 | 0.0017502 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5176-6_0_4_load_12 | 27 | 0.00053354 | 0.00013372 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5176-6_0_4_load_74 | 30 | 0.0011381 | 0.00028524 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5176-6_0_4_load_73 | 31 | 0.0061959 | 0.0015528 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5176-6_0_4_load_71 | 32 | 0.014279 | 0.0035787 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5176-6_0_4_load_72 | 33 | 0.002056 | 0.00051528 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5176-6_0_4_load_21 | 34 | 0.0039839 | 0.00099845 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5176-6_0_4_load_23 | 35 | 0.0083005 | 0.0020803 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5176-6_0_4_load_30 | 36 | 0.0073941 | 0.0018531 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5176-6_0_4_load_31 | 37 | 0.0072906 | 0.0018272 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5176-6_0_4_load_29 | 38 | 0.012872 | 0.0032259 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5176-6_0_4_load_36 | 39 | 0.005206 | 0.0013048 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5176-6_0_4_load_37 | 40 | 0.0051755 | 0.0012971 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5176-6_0_4_load_68 | 41 | 0.0093684 | 0.0023479 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5176-6_0_4_load_66 | 43 | 0.0025451 | 0.00063786 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5176-6_0_4_load_70 | 44 | 0.0034848 | 0.00087337 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5176-6_0_4_load_38 | 45 | 0.0095071 | 0.0023827 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5176-6_0_4_load_64 | 46 | 0.0093911 | 0.0023536 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5176-6_0_4_load_39 | 47 | 0.0014289 | 0.00035811 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5176-6_0_4_load_44 | 48 | 0.0074383 | 0.0018642 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5176-6_0_4_load_42 | 49 | 0.0068057 | 0.0017057 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5176-6_0_4_load_40 | 50 | 0.010534 | 0.0026401 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5176-6_0_4_load_41 | 51 | 0.0064505 | 0.0016166 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5176-6_0_4_load_45 | 53 | 0.0065313 | 0.0016369 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5176-6_0_4_load_46 | 54 | 0.0049849 | 0.0012493 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5176-6_0_4_load_47 | 55 | 0.0065625 | 0.0016447 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5176-6_0_4_load_56 | 58 | 0.0012789 | 0.00032052 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5176-6_0_4_load_65 | 60 | 0.008486 | 0.0021268 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5176-6_0_4_load_62 | 61 | 0.003402 | 0.00085263 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5176-6_0_4_load_54 | 62 | 0.0068322 | 0.0017123 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5176-6_0_4_load_50 | 63 | 0.0048468 | 0.0012147 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5176-6_0_4_load_49 | 64 | 0.0022423 | 0.00056196 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5176-6_0_4_load_51 | 65 | 0.0061926 | 0.001552 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5176-6_0_4_load_53 | 66 | 0.0032068 | 0.00080369 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5176-6_0_4_load_55 | 67 | 0.0036639 | 0.00091826 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5176-6_0_4_load_57 | 68 | 0.013165 | 0.0032994 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5176-6_0_4_load_58 | 69 | 0.0043704 | 0.0010953 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5176-6_0_4_load_60 | 71 | 0.0070697 | 0.0017718 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5176-6_0_4_load_61 | 72 | 0.005169 | 0.0012955 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5176-6_0_4_load_67 | 73 | 0.0058051 | 0.0014549 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5176-6_0_4_line_0 |  | 0 | 1 | 0.029469 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
1 | LV_5176-6_0_4_line_1 |  | 0 | 2 | 0.14677 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_5176-6_0_4_line_2 |  | 1 | 3 | 0.12255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
3 | LV_5176-6_0_4_line_3 |  | 2 | 4 | 0.0077633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5176-6_0_4_line_4 |  | 3 | 5 | 0.0089274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5176-6_0_4_line_5 |  | 3 | 6 | 0.022549 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
6 | LV_5176-6_0_4_line_6 |  | 4 | 7 | 0.025598 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5176-6_0_4_line_7 |  | 5 | 19 | 0.0027068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5176-6_0_4_line_8 |  | 6 | 12 | 0.10181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_5176-6_0_4_line_9 |  | 7 | 8 | 0.035982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5176-6_0_4_line_10 |  | 7 | 9 | 0.045289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5176-6_0_4_line_11 |  | 8 | 10 | 0.012464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5176-6_0_4_line_12 |  | 9 | 11 | 0.017074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5176-6_0_4_line_13 |  | 11 | 27 | 0.012807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5176-6_0_4_line_14 |  | 11 | 28 | 0.043919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5176-6_0_4_line_15 |  | 12 | 14 | 0.010584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_5176-6_0_4_line_16 |  | 12 | 16 | 0.010882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5176-6_0_4_line_17 |  | 13 | 14 | 0.0062902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_5176-6_0_4_line_18 |  | 13 | 15 | 0.012628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_5176-6_0_4_line_19 |  | 15 | 20 | 0.010047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_5176-6_0_4_line_20 |  | 16 | 17 | 0.018753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5176-6_0_4_line_21 |  | 17 | 18 | 0.0018764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5176-6_0_4_line_22 |  | 20 | 21 | 0.00032284 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_5176-6_0_4_line_23 |  | 21 | 22 | 0.027326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_5176-6_0_4_line_24 |  | 22 | 26 | 0.020541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
25 | LV_5176-6_0_4_line_25 |  | 23 | 24 | 0.025384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_5176-6_0_4_line_26 |  | 23 | 25 | 0.033361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
27 | LV_5176-6_0_4_line_27 |  | 24 | 26 | 0.0062953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
28 | LV_5176-6_0_4_line_28 |  | 25 | 34 | 0.016275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_5176-6_0_4_line_29 |  | 28 | 29 | 0.054372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5176-6_0_4_line_30 |  | 29 | 30 | 0.054374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5176-6_0_4_line_31 |  | 29 | 31 | 0.11466 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5176-6_0_4_line_32 |  | 31 | 33 | 0.058925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5176-6_0_4_line_33 |  | 32 | 33 | 0.0078913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5176-6_0_4_line_34 |  | 34 | 35 | 0.016043 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
35 | LV_5176-6_0_4_line_35 |  | 35 | 38 | 0.0023137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
36 | LV_5176-6_0_4_line_36 |  | 36 | 37 | 0.033962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_5176-6_0_4_line_37 |  | 36 | 38 | 0.093193 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_5176-6_0_4_line_38 |  | 37 | 39 | 0.00083663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_5176-6_0_4_line_39 |  | 39 | 40 | 0.040599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_5176-6_0_4_line_40 |  | 40 | 45 | 0.00045772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_5176-6_0_4_line_41 |  | 41 | 42 | 0.022157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5176-6_0_4_line_42 |  | 41 | 43 | 0.0048962 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5176-6_0_4_line_43 |  | 42 | 44 | 0.046957 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5176-6_0_4_line_44 |  | 43 | 46 | 0.040948 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5176-6_0_4_line_45 |  | 45 | 47 | 0.033507 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_5176-6_0_4_line_46 |  | 46 | 57 | 0.018515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5176-6_0_4_line_47 |  | 47 | 48 | 0.0071624 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
48 | LV_5176-6_0_4_line_48 |  | 48 | 49 | 0.025565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
49 | LV_5176-6_0_4_line_49 |  | 49 | 50 | 0.014926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_5176-6_0_4_line_50 |  | 50 | 51 | 0.029409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5176-6_0_4_line_51 |  | 51 | 52 | 0.021136 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5176-6_0_4_line_52 |  | 52 | 53 | 0.019557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5176-6_0_4_line_53 |  | 52 | 54 | 0.016845 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5176-6_0_4_line_54 |  | 53 | 55 | 0.021208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5176-6_0_4_line_55 |  | 54 | 56 | 0.0512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5176-6_0_4_line_56 |  | 55 | 57 | 0.059422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5176-6_0_4_line_57 |  | 56 | 58 | 0.0052116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5176-6_0_4_line_58 |  | 56 | 59 | 0.020155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5176-6_0_4_line_59 |  | 57 | 60 | 0.05707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5176-6_0_4_line_60 |  | 58 | 61 | 0.00092313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5176-6_0_4_line_61 |  | 59 | 62 | 0.061981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5176-6_0_4_line_62 |  | 59 | 63 | 0.021405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5176-6_0_4_line_63 |  | 60 | 73 | 0.040472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5176-6_0_4_line_64 |  | 63 | 64 | 0.0033914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5176-6_0_4_line_65 |  | 64 | 65 | 0.026928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5176-6_0_4_line_66 |  | 65 | 66 | 0.02717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5176-6_0_4_line_67 |  | 66 | 67 | 0.017618 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5176-6_0_4_line_68 |  | 67 | 68 | 0.00041018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5176-6_0_4_line_69 |  | 68 | 69 | 0.01998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5176-6_0_4_line_70 |  | 69 | 70 | 0.0063224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5176-6_0_4_line_71 |  | 70 | 71 | 0.020992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5176-6_0_4_line_72 |  | 70 | 72 | 0.037843 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5176-6_0_4_trafo_40 | 0.63 MVA 20/0.4 kV | 74 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2717531.2265 | 1099781.9028 | 2717549.0625 | 1099786.5399 | 2717560.054 | 1099785.5098
1 | 2717504.5159 | 1099921.3669 | 2717560.054 | 1099785.5098
2 | 2717408.6777 | 1099782.989 | 2717531.2265 | 1099781.9028
3 | 2717505.6756 | 1099929.043 | 2717504.5159 | 1099921.3669
4 | 2717408.6777 | 1099782.989 | 2717408.5396 | 1099774.0627
5 | 2717409.0264 | 1099805.5352 | 2717408.6777 | 1099782.989
6 | 2717500.4211 | 1099954.0919 | 2717505.6756 | 1099929.043
7 | 2717408.4978 | 1099771.3562 | 2717408.5396 | 1099774.0627
8 | 2717409.0264 | 1099805.5352 | 2717308.3249 | 1099820.4914
9 | 2717500.4211 | 1099954.0919 | 2717521.1102 | 1099952.1129 | 2717533.4762 | 1099954.8985 | 2717533.5994 | 1099957.4181
10 | 2717500.4211 | 1099954.0919 | 2717481.9419 | 1099995.4397
11 | 2717534.2085 | 1099969.8674 | 2717533.5994 | 1099957.4181
12 | 2717474.9752 | 1100011.0279 | 2717481.9419 | 1099995.4397
13 | 2717474.9752 | 1100011.0279 | 2717462.6571 | 1100007.5244
14 | 2717474.9752 | 1100011.0279 | 2717469.7078 | 1100023.5458 | 2717457.7079 | 1100046.2738 | 2717456.5139 | 1100050.7538
15 | 2717308.3249 | 1099820.4914 | 2717307.0058 | 1099809.9898
16 | 2717309.6812 | 1099831.2887 | 2717309.6812 | 1099831.2887 | 2717308.3249 | 1099820.4914
17 | 2717307.0058 | 1099809.9898 | 2717306.2218 | 1099803.7487
18 | 2717304.6479 | 1099791.2196 | 2717306.2218 | 1099803.7487
19 | 2717304.6479 | 1099791.2196 | 2717303.3911 | 1099781.2518
20 | 2717309.6812 | 1099831.2887 | 2717313.1174 | 1099849.7237
21 | 2717313.1174 | 1099849.7237 | 2717313.4613 | 1099851.5684
22 | 2717303.3508 | 1099780.9315 | 2717303.3911 | 1099781.2518
23 | 2717299.9324 | 1099753.8198 | 2717303.3508 | 1099780.9315
24 | 2717302.495 | 1099733.5162 | 2717299.659 | 1099751.6516 | 2717299.9324 | 1099753.8198
25 | 2717305.8245 | 1099728.1734 | 2717310.6219 | 1099720.4752 | 2717311.8886 | 1099704.2107
26 | 2717308.1824 | 1099671.1943 | 2717308.4488 | 1099679.4495 | 2717311.6039 | 1099694.0983 | 2717311.8886 | 1099704.2107
27 | 2717302.495 | 1099733.5162 | 2717302.495 | 1099733.5162 | 2717305.8245 | 1099728.1734
28 | 2717308.1824 | 1099671.1943 | 2717291.9524 | 1099669.9801 | 2717291.9524 | 1099669.9801
29 | 2717456.5139 | 1100050.7538 | 2717473.375 | 1100070.1264 | 2717489.9663 | 1100085.8247 | 2717487.7793 | 1100080.4009
30 | 2717487.7793 | 1100080.4009 | 2717491.5285 | 1100083.52 | 2717495.7947 | 1100084.7255 | 2717499.8783 | 1100082.1694 | 2717502.7344 | 1100071.4173 | 2717510.5957 | 1100049.6988 | 2717514.7158 | 1100045.2532
31 | 2717487.7793 | 1100080.4009 | 2717400.0965 | 1100154.2822
32 | 2717349.0626 | 1100183.7391 | 2717359.1349 | 1100177.926 | 2717400.0965 | 1100154.2822
33 | 2717342.2279 | 1100187.6837 | 2717349.0626 | 1100183.7391
34 | 2717277.2366 | 1099663.5899 | 2717291.9524 | 1099669.9801
35 | 2717277.2366 | 1099663.5899 | 2717275.1144 | 1099662.6684
36 | 2717189.239 | 1099698.8669 | 2717182.1579 | 1099719.7514 | 2717182.2753 | 1099731.6609
37 | 2717189.239 | 1099698.8669 | 2717275.1144 | 1099662.6684
38 | 2717182.2836 | 1099732.4975 | 2717182.2753 | 1099731.6609
39 | 2717182.2836 | 1099732.4975 | 2717182.4643 | 1099750.8231 | 2717183.5741 | 1099773.0679
40 | 2717183.5969 | 1099773.525 | 2717183.5741 | 1099773.0679
41 | 2717121.1048 | 1099706.3318 | 2717116.5814 | 1099728.0224
42 | 2717115.5819 | 1099732.8155 | 2717116.5814 | 1099728.0224
43 | 2717121.1048 | 1099706.3318 | 2717074.6171 | 1099712.9504
44 | 2717115.5819 | 1099732.8155 | 2717115.516 | 1099733.1313 | 2717107.2276 | 1099772.9023
45 | 2717183.5969 | 1099773.525 | 2717184.7702 | 1099797.0437 | 2717185.7834 | 1099806.9506
46 | 2717103.4503 | 1099791.0274 | 2717107.2276 | 1099772.9023
47 | 2717186.5121 | 1099814.0759 | 2717185.7834 | 1099806.9506
48 | 2717186.5121 | 1099814.0759 | 2717188.1575 | 1099830.1651 | 2717195.3923 | 1099836.1532
49 | 2717195.3923 | 1099836.1532 | 2717206.891 | 1099845.6704
50 | 2717206.891 | 1099845.6704 | 2717206.891 | 1099845.6704 | 2717199.9333 | 1099853.9196 | 2717182.8485 | 1099861.3173
51 | 2717163.4523 | 1099869.7158 | 2717182.8485 | 1099861.3173
52 | 2717163.4523 | 1099869.7158 | 2717154.7408 | 1099852.2061
53 | 2717163.4523 | 1099869.7158 | 2717147.9965 | 1099876.4146
54 | 2717145.294 | 1099833.2184 | 2717154.7408 | 1099852.2061
55 | 2717100.6607 | 1099895.9233 | 2717139.4568 | 1099880.1158 | 2717147.9965 | 1099876.4146
56 | 2717145.294 | 1099833.2184 | 2717103.4503 | 1099791.0274
57 | 2717100.6607 | 1099895.9233 | 2717098.8746 | 1099891.0273
58 | 2717111.5845 | 1099912.8788 | 2717107.4571 | 1099906.4726 | 2717100.6607 | 1099895.9233
59 | 2717103.4503 | 1099791.0274 | 2717098.213 | 1099793.1835 | 2717092.5684 | 1099805.2163 | 2717088.651 | 1099809.1991 | 2717056.1434 | 1099810.3758
60 | 2717098.8746 | 1099891.0273 | 2717098.5582 | 1099890.1601
61 | 2717163.2981 | 1099944.3196 | 2717144.5599 | 1099935.8858 | 2717131.6906 | 1099924.6633 | 2717124.7872 | 1099916.458 | 2717117.1607 | 1099913.6201 | 2717111.5845 | 1099912.8788
62 | 2717111.5845 | 1099912.8788 | 2717123.184 | 1099930.8689
63 | 2717015.6974 | 1099811.8399 | 2717056.1434 | 1099810.3758
64 | 2717125.0217 | 1099933.7192 | 2717123.184 | 1099930.8689
65 | 2717125.0217 | 1099933.7192 | 2717126.7637 | 1099936.4209 | 2717135.0528 | 1099943.8413 | 2717141.5601 | 1099954.6173
66 | 2717150.7577 | 1099978.6569 | 2717150.7577 | 1099978.6569 | 2717152.2129 | 1099972.2583 | 2717141.5601 | 1099954.6173
67 | 2717150.7577 | 1099978.6569 | 2717142.4234 | 1099986.4237 | 2717138.4009 | 1099991.176
68 | 2717138.4009 | 1099991.176 | 2717138.1359 | 1099991.4891
69 | 2717125.2261 | 1100006.7388 | 2717131.6077 | 1099999.2017 | 2717138.1359 | 1099991.4891
70 | 2717121.1407 | 1100011.564 | 2717125.2261 | 1100006.7388
71 | 2717121.1407 | 1100011.564 | 2717111.7431 | 1100022.6794 | 2717107.5846 | 1100027.5925
72 | 2717121.1407 | 1100011.564 | 2717121.1858 | 1100033.7134 | 2717120.041 | 1100049.3654

## bus_geodata
| x | y | coords
0 | 2717560.054 | 1099785.5098
1 | 2717531.2265 | 1099781.9028
2 | 2717504.5159 | 1099921.3669
3 | 2717408.6777 | 1099782.989
4 | 2717505.6756 | 1099929.043
5 | 2717408.5396 | 1099774.0627
6 | 2717409.0264 | 1099805.5352
7 | 2717500.4211 | 1099954.0919
8 | 2717533.5994 | 1099957.4181
9 | 2717481.9419 | 1099995.4397
10 | 2717534.2085 | 1099969.8674
11 | 2717474.9752 | 1100011.0279
12 | 2717308.3249 | 1099820.4914
13 | 2717306.2218 | 1099803.7487
14 | 2717307.0058 | 1099809.9898
15 | 2717304.6479 | 1099791.2196
16 | 2717309.6812 | 1099831.2887
17 | 2717313.1174 | 1099849.7237
18 | 2717313.4613 | 1099851.5684
19 | 2717408.4978 | 1099771.3562
20 | 2717303.3911 | 1099781.2518
21 | 2717303.3508 | 1099780.9315
22 | 2717299.9324 | 1099753.8198
23 | 2717311.8886 | 1099704.2107
24 | 2717305.8245 | 1099728.1734
25 | 2717308.1824 | 1099671.1943
26 | 2717302.495 | 1099733.5162
27 | 2717462.6571 | 1100007.5244
28 | 2717456.5139 | 1100050.7538
29 | 2717487.7793 | 1100080.4009
30 | 2717514.7158 | 1100045.2532
31 | 2717400.0965 | 1100154.2822
32 | 2717342.2279 | 1100187.6837
33 | 2717349.0626 | 1100183.7391
34 | 2717291.9524 | 1099669.9801
35 | 2717277.2366 | 1099663.5899
36 | 2717189.239 | 1099698.8669
37 | 2717182.2753 | 1099731.6609
38 | 2717275.1144 | 1099662.6684
39 | 2717182.2836 | 1099732.4975
40 | 2717183.5741 | 1099773.0679
41 | 2717116.5814 | 1099728.0224
42 | 2717121.1048 | 1099706.3318
43 | 2717115.5819 | 1099732.8155
44 | 2717074.6171 | 1099712.9504
45 | 2717183.5969 | 1099773.525
46 | 2717107.2276 | 1099772.9023
47 | 2717185.7834 | 1099806.9506
48 | 2717186.5121 | 1099814.0759
49 | 2717195.3923 | 1099836.1532
50 | 2717206.891 | 1099845.6704
51 | 2717182.8485 | 1099861.3173
52 | 2717163.4523 | 1099869.7158
53 | 2717154.7408 | 1099852.2061
54 | 2717147.9965 | 1099876.4146
55 | 2717145.294 | 1099833.2184
56 | 2717100.6607 | 1099895.9233
57 | 2717103.4503 | 1099791.0274
58 | 2717098.8746 | 1099891.0273
59 | 2717111.5845 | 1099912.8788
60 | 2717056.1434 | 1099810.3758
61 | 2717098.5582 | 1099890.1601
62 | 2717163.2981 | 1099944.3196
63 | 2717123.184 | 1099930.8689
64 | 2717125.0217 | 1099933.7192
65 | 2717141.5601 | 1099954.6173
66 | 2717150.7577 | 1099978.6569
67 | 2717138.4009 | 1099991.176
68 | 2717138.1359 | 1099991.4891
69 | 2717125.2261 | 1100006.7388
70 | 2717121.1407 | 1100011.564
71 | 2717107.5846 | 1100027.5925
72 | 2717120.041 | 1100049.3654
73 | 2717015.6974 | 1099811.8399
74 | 2717163.4523 | 1099869.7158

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1