## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5192-155_0_6_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5192-155_0_6_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5192-155_0_6_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5192-155_0_6_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5192-155_0_6_node_5 | 0.4 | n |  | TRUE
5 | bus_LV_5192-155_0_6_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_5192-155_0_6_node_39 | 0.4 | n |  | TRUE
7 | bus_LV_5192-155_0_6_node_49 | 0.4 | n |  | TRUE
8 | bus_LV_5192-155_0_6_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5192-155_0_6_node_14 | 0.4 | n |  | TRUE
10 | bus_LV_5192-155_0_6_node_57 | 0.4 | n |  | TRUE
11 | bus_LV_5192-155_0_6_node_15 | 0.4 | n |  | TRUE
12 | bus_LV_5192-155_0_6_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_5192-155_0_6_node_40 | 0.4 | n |  | TRUE
14 | bus_LV_5192-155_0_6_node_37 | 0.4 | n |  | TRUE
15 | bus_LV_5192-155_0_6_node_38 | 0.4 | n |  | TRUE
16 | bus_LV_5192-155_0_6_node_41 | 0.4 | n |  | TRUE
17 | bus_LV_5192-155_0_6_node_42 | 0.4 | n |  | TRUE
18 | bus_LV_5192-155_0_6_node_43 | 0.4 | n |  | TRUE
19 | bus_LV_5192-155_0_6_node_44 | 0.4 | n |  | TRUE
20 | bus_LV_5192-155_0_6_node_45 | 0.4 | n |  | TRUE
21 | bus_LV_5192-155_0_6_node_46 | 0.4 | n |  | TRUE
22 | bus_LV_5192-155_0_6_node_47 | 0.4 | n |  | TRUE
23 | bus_LV_5192-155_0_6_node_51 | 0.4 | n |  | TRUE
24 | bus_LV_5192-155_0_6_node_48 | 0.4 | n |  | TRUE
25 | bus_LV_5192-155_0_6_node_50 | 0.4 | n |  | TRUE
26 | bus_LV_5192-155_0_6_node_52 | 0.4 | n |  | TRUE
27 | bus_LV_5192-155_0_6_node_58 | 0.4 | n |  | TRUE
28 | bus_LV_5192-155_0_6_node_59 | 0.4 | n |  | TRUE
29 | bus_LV_5192-155_0_6_node_60 | 0.4 | n |  | TRUE
30 | bus_MV_256_0_node_6 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5192-155_0_6_load_0 | 0 | 0.061227 | 0.015345 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5192-155_0_6_load_1 | 1 | 0.023512 | 0.0058926 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5192-155_0_6_load_2 | 2 | 0.0122 | 0.0030576 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5192-155_0_6_load_39 | 6 | 0.0072388 | 0.0018142 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5192-155_0_6_load_14 | 9 | 0.017209 | 0.004313 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5192-155_0_6_load_57 | 10 | 0.0077819 | 0.0019503 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5192-155_0_6_load_37 | 14 | 0.058938 | 0.014771 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5192-155_0_6_load_38 | 15 | 0.0084237 | 0.0021112 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5192-155_0_6_load_41 | 16 | 0.00099422 | 0.00024918 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5192-155_0_6_load_42 | 17 | 0.00096691 | 0.00024233 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5192-155_0_6_load_43 | 18 | 0.042923 | 0.010758 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5192-155_0_6_load_45 | 20 | 0.020888 | 0.005235 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5192-155_0_6_load_47 | 22 | 0.0084359 | 0.0021142 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5192-155_0_6_load_51 | 23 | 0.014066 | 0.0035252 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5192-155_0_6_load_48 | 24 | 0.014505 | 0.0036352 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5192-155_0_6_load_52 | 26 | 0.0058992 | 0.0014785 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5192-155_0_6_load_60 | 29 | 0.003067 | 0.00076867 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 15 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5192-155_0_6_line_0 |  | 0 | 1 | 0.035877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5192-155_0_6_line_1 |  | 0 | 2 | 0.0072082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5192-155_0_6_line_2 |  | 2 | 3 | 0.043003 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5192-155_0_6_line_3 |  | 3 | 4 | 0.10275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5192-155_0_6_line_4 |  | 4 | 8 | 0.053099 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5192-155_0_6_line_5 |  | 4 | 9 | 0.05854 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_5192-155_0_6_line_6 |  | 5 | 6 | 0.024828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_5192-155_0_6_line_7 |  | 5 | 7 | 0.48153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_5192-155_0_6_line_8 |  | 6 | 15 | 0.059504 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
9 | LV_5192-155_0_6_line_9 |  | 7 | 25 | 0.022436 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5192-155_0_6_line_10 |  | 7 | 24 | 0.063009 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_5192-155_0_6_line_11 |  | 8 | 10 | 0.014602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5192-155_0_6_line_12 |  | 9 | 11 | 0.019365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_5192-155_0_6_line_13 |  | 10 | 27 | 0.029648 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5192-155_0_6_line_14 |  | 11 | 12 | 0.069261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_5192-155_0_6_line_15 |  | 12 | 13 | 0.031538 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5192-155_0_6_line_16 |  | 12 | 14 | 0.089262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_5192-155_0_6_line_17 |  | 13 | 16 | 0.071394 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5192-155_0_6_line_18 |  | 14 | 15 | 0.093675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
19 | LV_5192-155_0_6_line_19 |  | 16 | 17 | 0.013502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5192-155_0_6_line_20 |  | 18 | 19 | 0.001439 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5192-155_0_6_line_21 |  | 19 | 20 | 0.019137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5192-155_0_6_line_22 |  | 19 | 21 | 0.19966 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
23 | LV_5192-155_0_6_line_23 |  | 20 | 22 | 0.01634 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5192-155_0_6_line_24 |  | 21 | 23 | 0.056761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5192-155_0_6_line_25 |  | 21 | 24 | 0.025717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
26 | LV_5192-155_0_6_line_26 |  | 25 | 26 | 0.023069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5192-155_0_6_line_27 |  | 27 | 28 | 0.020694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5192-155_0_6_line_28 |  | 28 | 29 | 0.0079058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5192-155_0_6_trafo_38 | 0.63 MVA 20/0.4 kV | 30 | 15 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42 | x43 | y43 | x44 | y44 | x45 | y45 | x46 | y46 | x47 | y47 | x48 | y48 | x49 | y49 | x50 | y50 | x51 | y51 | x52 | y52 | x53 | y53 | x54 | y54
0 | 2715869.5862 | 1093702.948 | 2715901.9324 | 1093718.4673
1 | 2715869.5862 | 1093702.948 | 2715863.0873 | 1093699.83
2 | 2715824.3157 | 1093681.2279 | 2715863.0873 | 1093699.83
3 | 2715789.1523 | 1093760.4128 | 2715807.4832 | 1093763.664 | 2715810.4669 | 1093749.0441 | 2715824.3157 | 1093681.2279
4 | 2715789.1523 | 1093760.4128 | 2715792.8625 | 1093745.084 | 2715797.1197 | 1093727.4863 | 2715797.4793 | 1093723.2569 | 2715797.5241 | 1093718.4655 | 2715796.6037 | 1093712.6663 | 2715795.1542 | 1093708.6025
5 | 2715789.1523 | 1093760.4128 | 2715736.1565 | 1093749.9858 | 2715731.7203 | 1093749.0796
6 | 2715909.4648 | 1093787.89 | 2715885.0832 | 1093783.2041
7 | 2715909.4648 | 1093787.89 | 2715933.5741 | 1093792.5527 | 2715938.4762 | 1093793.9916 | 2715941.4434 | 1093794.4707 | 2715946.4134 | 1093794.7879 | 2715958.6048 | 1093797.6667 | 2715958.8306 | 1093796.8038 | 2715959.1696 | 1093794.8756 | 2715961.3293 | 1093795.4282 | 2715977.4662 | 1093796.6701 | 2716004.9489 | 1093802.0424 | 2716033.5556 | 1093813.0957 | 2716036.7968 | 1093815.4591 | 2716039.2507 | 1093817.6519 | 2716041.1715 | 1093819.7567 | 2716042.7642 | 1093822.4 | 2716043.8363 | 1093825.1112 | 2716046.0985 | 1093836.1286 | 2716046.7481 | 1093837.831 | 2716047.8861 | 1093839.932 | 2716052.8561 | 1093846.7426 | 2716055.4908 | 1093850.0174 | 2716059.2535 | 1093853.8918 | 2716131.0666 | 1093925.99 | 2716143.7511 | 1093938.741 | 2716144.6012 | 1093939.6801 | 2716145.1812 | 1093940.5584 | 2716145.6776 | 1093941.7576 | 2716145.9047 | 1093942.8516 | 2716146.0276 | 1093943.7212 | 2716146.0171 | 1093944.6772 | 2716145.8484 | 1093945.797 | 2716145.4501 | 1093946.7678 | 2716144.9603 | 1093947.6591 | 2716144.3893 | 1093948.3375 | 2716143.7274 | 1093948.9031 | 2716142.8716 | 1093949.476 | 2716141.9878 | 1093949.8928 | 2716140.8442 | 1093950.1155 | 2716139.642 | 1093950.1593 | 2716138.5278 | 1093950.0601 | 2716137.5795 | 1093949.7974 | 2716136.5421 | 1093949.3328 | 2716135.8068 | 1093948.874 | 2716135.1771 | 1093948.1615 | 2716134.5152 | 1093947.1037 | 2716130.3947 | 1093939.6532 | 2716128.9107 | 1093937.4122 | 2716126.6199 | 1093934.8 | 2716124.6174 | 1093932.9161 | 2716113.7182 | 1093924.8913 | 2716106.0185 | 1093920.1967 | 2716057.3358 | 1093897.0849 | 2716016.96 | 1093879.3357 | 2715997.4128 | 1093869.5784
8 | 2715826.5588 | 1093772.4518 | 2715872.3424 | 1093780.7555 | 2715885.0832 | 1093783.2041
9 | 2715982.4776 | 1093854.1163 | 2715993.8051 | 1093861.2372 | 2715997.4128 | 1093869.5784
10 | 2715997.4128 | 1093869.5784 | 2715964.4013 | 1093849.7241 | 2715945.5079 | 1093838.1893 | 2715943.3715 | 1093837.209
11 | 2715795.1542 | 1093708.6025 | 2715786.4447 | 1093696.8817
12 | 2715712.7467 | 1093745.2038 | 2715731.7203 | 1093749.0796
13 | 2715771.8548 | 1093671.1666 | 2715781.6948 | 1093690.4894 | 2715786.4447 | 1093696.8817
14 | 2715650.4063 | 1093729.7185 | 2715652.8097 | 1093725.2056 | 2715667.7733 | 1093734.7522 | 2715675.2528 | 1093738.019 | 2715684.4403 | 1093740.7289 | 2715712.7467 | 1093745.2038
15 | 2715648.5207 | 1093760.3815 | 2715646.2937 | 1093746.2517 | 2715648.196 | 1093733.8571 | 2715650.4063 | 1093729.7185
16 | 2715650.4063 | 1093729.7185 | 2715661.4138 | 1093736.9884 | 2715680.5985 | 1093745.0699 | 2715720.3228 | 1093752.3528 | 2715734.9509 | 1093755.0067
17 | 2715648.5207 | 1093760.3815 | 2715650.7868 | 1093764.3051 | 2715667.8755 | 1093823.0593 | 2715668.7537 | 1093828.6648
18 | 2715734.9509 | 1093755.0067 | 2715754.7651 | 1093758.6014 | 2715769.1008 | 1093764.4783 | 2715802.9484 | 1093768.1696 | 2715826.5588 | 1093772.4518
19 | 2715668.7537 | 1093828.6648 | 2715670.8435 | 1093842.004
20 | 2715828.4405 | 1093830.0198 | 2715827.5291 | 1093828.9063
21 | 2715828.4405 | 1093830.0198 | 2715844.9213 | 1093820.2932
22 | 2715828.4405 | 1093830.0198 | 2715842.2867 | 1093846.9284 | 2715834.3052 | 1093852.5247 | 2715831.7303 | 1093858.7133 | 2715832.1383 | 1093862.9239 | 2715839.8862 | 1093874.0569 | 2715843.1527 | 1093878.7557 | 2715839.3621 | 1093881.6299 | 2715849.0836 | 1093893.312 | 2715853.4632 | 1093898.5768 | 2715880.3704 | 1093899.1565 | 2715887.805 | 1093896.6297 | 2715891.6925 | 1093891.5225 | 2715901.9082 | 1093842.3278 | 2715907.7033 | 1093837.1792 | 2715919.2981 | 1093839.6352
23 | 2715858.9932 | 1093811.9883 | 2715844.9213 | 1093820.2932
24 | 2715919.2981 | 1093839.6352 | 2715917.0148 | 1093842.3157 | 2715915.2909 | 1093845.3294 | 2715913.9213 | 1093849.2727 | 2715913.1907 | 1093852.6277 | 2715913.1081 | 1093856.9624 | 2715914.731 | 1093894.7523
25 | 2715919.2981 | 1093839.6352 | 2715922.5154 | 1093837.1615 | 2715926.5776 | 1093835.4933 | 2715931.0019 | 1093834.7549 | 2715935.3571 | 1093834.7935 | 2715940.1986 | 1093835.7531 | 2715943.3715 | 1093837.209
26 | 2715982.4776 | 1093854.1163 | 2715971.8865 | 1093847.3986 | 2715966.3705 | 1093843.2016 | 2715963.7116 | 1093840.7808
27 | 2715771.8548 | 1093671.1666 | 2715770.0256 | 1093669.1304 | 2715769.0121 | 1093666.5871 | 2715768.887 | 1093664.2053 | 2715769.6269 | 1093661.5732 | 2715771.2273 | 1093659.3465 | 2715773.4891 | 1093657.7996 | 2715776.1529 | 1093657.1165 | 2715778.0205 | 1093657.141
28 | 2715778.0205 | 1093657.141 | 2715778.8133 | 1093649.275

## bus_geodata
| x | y | coords
0 | 2715869.5862 | 1093702.948
1 | 2715901.9324 | 1093718.4673
2 | 2715863.0873 | 1093699.83
3 | 2715824.3157 | 1093681.2279
4 | 2715789.1523 | 1093760.4128
5 | 2715909.4648 | 1093787.89
6 | 2715885.0832 | 1093783.2041
7 | 2715997.4128 | 1093869.5784
8 | 2715795.1542 | 1093708.6025
9 | 2715731.7203 | 1093749.0796
10 | 2715786.4447 | 1093696.8817
11 | 2715712.7467 | 1093745.2038
12 | 2715650.4063 | 1093729.7185
13 | 2715648.5207 | 1093760.3815
14 | 2715734.9509 | 1093755.0067
15 | 2715826.5588 | 1093772.4518
16 | 2715668.7537 | 1093828.6648
17 | 2715670.8435 | 1093842.004
18 | 2715827.5291 | 1093828.9063
19 | 2715828.4405 | 1093830.0198
20 | 2715844.9213 | 1093820.2932
21 | 2715919.2981 | 1093839.6352
22 | 2715858.9932 | 1093811.9883
23 | 2715914.731 | 1093894.7523
24 | 2715943.3715 | 1093837.209
25 | 2715982.4776 | 1093854.1163
26 | 2715963.7116 | 1093840.7808
27 | 2715771.8548 | 1093671.1666
28 | 2715778.0205 | 1093657.141
29 | 2715778.8133 | 1093649.275
30 | 2715909.4648 | 1093787.89

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1