## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5192-181_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5192-181_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5192-181_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5192-181_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5192-181_0_3_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5192-181_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_5192-181_0_3_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_5192-181_0_3_node_48 | 0.4 | n |  | TRUE
8 | bus_LV_5192-181_0_3_node_54 | 0.4 | n |  | TRUE
9 | bus_LV_5192-181_0_3_node_15 | 0.4 | n |  | TRUE
10 | bus_LV_5192-181_0_3_node_56 | 0.4 | n |  | TRUE
11 | bus_LV_5192-181_0_3_node_49 | 0.4 | n |  | TRUE
12 | bus_LV_5192-181_0_3_node_53 | 0.4 | n |  | TRUE
13 | bus_LV_5192-181_0_3_node_52 | 0.4 | n |  | TRUE
14 | bus_LV_5192-181_0_3_node_65 | 0.4 | n |  | TRUE
15 | bus_LV_5192-181_0_3_node_11 | 0.4 | n |  | TRUE
16 | bus_LV_5192-181_0_3_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_5192-181_0_3_node_9 | 0.4 | n |  | TRUE
18 | bus_LV_5192-181_0_3_node_55 | 0.4 | n |  | TRUE
19 | bus_LV_5192-181_0_3_node_7 | 0.4 | n |  | TRUE
20 | bus_LV_5192-181_0_3_node_8 | 0.4 | n |  | TRUE
21 | bus_LV_5192-181_0_3_node_10 | 0.4 | n |  | TRUE
22 | bus_LV_5192-181_0_3_node_13 | 0.4 | n |  | TRUE
23 | bus_LV_5192-181_0_3_node_14 | 0.4 | n |  | TRUE
24 | bus_LV_5192-181_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_5192-181_0_3_node_17 | 0.4 | n |  | TRUE
26 | bus_LV_5192-181_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_5192-181_0_3_node_19 | 0.4 | n |  | TRUE
28 | bus_LV_5192-181_0_3_node_20 | 0.4 | n |  | TRUE
29 | bus_LV_5192-181_0_3_node_21 | 0.4 | n |  | TRUE
30 | bus_LV_5192-181_0_3_node_22 | 0.4 | n |  | TRUE
31 | bus_LV_5192-181_0_3_node_23 | 0.4 | n |  | TRUE
32 | bus_LV_5192-181_0_3_node_24 | 0.4 | n |  | TRUE
33 | bus_LV_5192-181_0_3_node_45 | 0.4 | n |  | TRUE
34 | bus_LV_5192-181_0_3_node_35 | 0.4 | n |  | TRUE
35 | bus_LV_5192-181_0_3_node_51 | 0.4 | n |  | TRUE
36 | bus_LV_5192-181_0_3_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_5192-181_0_3_node_34 | 0.4 | n |  | TRUE
38 | bus_LV_5192-181_0_3_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_5192-181_0_3_node_26 | 0.4 | n |  | TRUE
40 | bus_LV_5192-181_0_3_node_27 | 0.4 | n |  | TRUE
41 | bus_LV_5192-181_0_3_node_28 | 0.4 | n |  | TRUE
42 | bus_LV_5192-181_0_3_node_46 | 0.4 | n |  | TRUE
43 | bus_LV_5192-181_0_3_node_47 | 0.4 | n |  | TRUE
44 | bus_LV_5192-181_0_3_node_29 | 0.4 | n |  | TRUE
45 | bus_LV_5192-181_0_3_node_30 | 0.4 | n |  | TRUE
46 | bus_LV_5192-181_0_3_node_31 | 0.4 | n |  | TRUE
47 | bus_LV_5192-181_0_3_node_32 | 0.4 | n |  | TRUE
48 | bus_LV_5192-181_0_3_node_33 | 0.4 | n |  | TRUE
49 | bus_LV_5192-181_0_3_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_5192-181_0_3_node_38 | 0.4 | n |  | TRUE
51 | bus_LV_5192-181_0_3_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_5192-181_0_3_node_36 | 0.4 | n |  | TRUE
53 | bus_LV_5192-181_0_3_node_37 | 0.4 | n |  | TRUE
54 | bus_LV_5192-181_0_3_node_39 | 0.4 | n |  | TRUE
55 | bus_LV_5192-181_0_3_node_42 | 0.4 | n |  | TRUE
56 | bus_LV_5192-181_0_3_node_43 | 0.4 | n |  | TRUE
57 | bus_LV_5192-181_0_3_node_50 | 0.4 | n |  | TRUE
58 | bus_LV_5192-181_0_3_node_62 | 0.4 | n |  | TRUE
59 | bus_LV_5192-181_0_3_node_63 | 0.4 | n |  | TRUE
60 | bus_LV_5192-181_0_3_node_64 | 0.4 | n |  | TRUE
61 | bus_LV_5192-181_0_3_node_61 | 0.4 | n |  | TRUE
62 | bus_LV_5192-181_0_3_node_59 | 0.4 | n |  | TRUE
63 | bus_LV_5192-181_0_3_node_57 | 0.4 | n |  | TRUE
64 | bus_LV_5192-181_0_3_node_58 | 0.4 | n |  | TRUE
65 | bus_MV_248_0_node_63 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5192-181_0_3_load_0 | 0 | 0.0069145 | 0.0017329 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5192-181_0_3_load_1 | 1 | 0.006911 | 0.0017321 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5192-181_0_3_load_3 | 3 | 0.012333 | 0.0030909 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5192-181_0_3_load_48 | 7 | 0.0062881 | 0.0015759 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5192-181_0_3_load_54 | 8 | 0.0051005 | 0.0012783 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5192-181_0_3_load_56 | 10 | 0.0016887 | 0.00042322 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5192-181_0_3_load_49 | 11 | 0.0033526 | 0.00084025 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5192-181_0_3_load_52 | 13 | 0.011003 | 0.0027576 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5192-181_0_3_load_65 | 14 | 0.014111 | 0.0035366 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5192-181_0_3_load_12 | 16 | 0.0098157 | 0.0024601 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5192-181_0_3_load_55 | 18 | 0.013313 | 0.0033366 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5192-181_0_3_load_7 | 19 | 0.0040073 | 0.0010043 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5192-181_0_3_load_8 | 20 | 0.014264 | 0.0035748 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5192-181_0_3_load_10 | 21 | 0.0037602 | 0.0009424 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5192-181_0_3_load_13 | 22 | 0.0061744 | 0.0015474 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5192-181_0_3_load_14 | 23 | 0.0086458 | 0.0021668 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5192-181_0_3_load_17 | 25 | 0.022257 | 0.0055782 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5192-181_0_3_load_18 | 26 | 0.014043 | 0.0035196 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5192-181_0_3_load_19 | 27 | 0.0081185 | 0.0020347 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5192-181_0_3_load_20 | 28 | 0.0063706 | 0.0015966 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5192-181_0_3_load_22 | 30 | 0.0059614 | 0.0014941 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5192-181_0_3_load_23 | 31 | 0.0056846 | 0.0014247 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5192-181_0_3_load_24 | 32 | 0.0075369 | 0.0018889 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5192-181_0_3_load_45 | 33 | 0.0071104 | 0.001782 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5192-181_0_3_load_35 | 34 | 0.0072082 | 0.0018065 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5192-181_0_3_load_51 | 35 | 0.0038986 | 0.00097707 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5192-181_0_3_load_44 | 36 | 0.0090523 | 0.0022687 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5192-181_0_3_load_34 | 37 | 0.0063005 | 0.0015791 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5192-181_0_3_load_25 | 38 | 0.0065094 | 0.0016314 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5192-181_0_3_load_27 | 40 | 0.0106 | 0.0026566 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5192-181_0_3_load_46 | 42 | 0.0058684 | 0.0014708 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5192-181_0_3_load_29 | 44 | 0.018997 | 0.0047611 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5192-181_0_3_load_30 | 45 | 0.0045019 | 0.0011283 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5192-181_0_3_load_31 | 46 | 0.002512 | 0.00062956 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5192-181_0_3_load_32 | 47 | 0.0018432 | 0.00046196 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5192-181_0_3_load_40 | 51 | 0.0051268 | 0.0012849 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5192-181_0_3_load_36 | 52 | 0.0041766 | 0.0010468 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5192-181_0_3_load_37 | 53 | 0.0042923 | 0.0010757 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5192-181_0_3_load_39 | 54 | 0.0019465 | 0.00048784 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5192-181_0_3_load_42 | 55 | 0.001578 | 0.00039547 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5192-181_0_3_load_43 | 56 | 0.01294 | 0.003243 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5192-181_0_3_load_50 | 57 | 0.0060705 | 0.0015214 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5192-181_0_3_load_62 | 58 | 0.0071351 | 0.0017882 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5192-181_0_3_load_64 | 60 | 0.0032249 | 0.00080824 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5192-181_0_3_load_61 | 61 | 0.0058128 | 0.0014568 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5192-181_0_3_load_59 | 62 | 0.0034205 | 0.00085727 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5192-181_0_3_load_57 | 63 | 0.0028854 | 0.00072316 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5192-181_0_3_load_58 | 64 | 0.0036322 | 0.00091031 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 28 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5192-181_0_3_line_0 |  | 0 | 1 | 1.1143e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
1 | LV_5192-181_0_3_line_1 |  | 0 | 2 | 0.018475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
2 | LV_5192-181_0_3_line_2 |  | 1 | 3 | 0.014671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_5192-181_0_3_line_3 |  | 2 | 4 | 0.026289 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5192-181_0_3_line_4 |  | 2 | 5 | 0.020855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
5 | LV_5192-181_0_3_line_5 |  | 3 | 6 | 0.075365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_5192-181_0_3_line_6 |  | 4 | 7 | 0.022491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5192-181_0_3_line_7 |  | 5 | 8 | 0.013772 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_5192-181_0_3_line_8 |  | 6 | 9 | 0.038357 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_5192-181_0_3_line_9 |  | 6 | 10 | 0.048886 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5192-181_0_3_line_10 |  | 7 | 11 | 0.019387 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5192-181_0_3_line_11 |  | 8 | 12 | 0.01897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_5192-181_0_3_line_12 |  | 9 | 14 | 0.018896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5192-181_0_3_line_13 |  | 9 | 15 | 0.080302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5192-181_0_3_line_14 |  | 10 | 18 | 0.011641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5192-181_0_3_line_15 |  | 11 | 57 | 0.005599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5192-181_0_3_line_16 |  | 12 | 13 | 0.010726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_5192-181_0_3_line_17 |  | 13 | 35 | 0.015093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_5192-181_0_3_line_18 |  | 15 | 16 | 0.028423 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5192-181_0_3_line_19 |  | 15 | 17 | 0.035793 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5192-181_0_3_line_20 |  | 16 | 22 | 0.024112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5192-181_0_3_line_21 |  | 17 | 19 | 0.056376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5192-181_0_3_line_22 |  | 18 | 63 | 0.016541 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5192-181_0_3_line_23 |  | 19 | 20 | 0.0017865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5192-181_0_3_line_24 |  | 20 | 21 | 0.012253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5192-181_0_3_line_25 |  | 22 | 23 | 0.00067547 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5192-181_0_3_line_26 |  | 23 | 24 | 0.019897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5192-181_0_3_line_27 |  | 24 | 25 | 0.009799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5192-181_0_3_line_28 |  | 24 | 26 | 0.0099819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5192-181_0_3_line_29 |  | 27 | 28 | 0.014556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
30 | LV_5192-181_0_3_line_30 |  | 27 | 29 | 0.0018703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
31 | LV_5192-181_0_3_line_31 |  | 28 | 30 | 0.0066844 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5192-181_0_3_line_32 |  | 29 | 31 | 0.016721 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5192-181_0_3_line_33 |  | 29 | 32 | 0.0056163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
34 | LV_5192-181_0_3_line_34 |  | 30 | 33 | 0.013305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5192-181_0_3_line_35 |  | 31 | 34 | 0.0020877 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5192-181_0_3_line_36 |  | 32 | 35 | 0.019197 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
37 | LV_5192-181_0_3_line_37 |  | 33 | 36 | 0.0098815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5192-181_0_3_line_38 |  | 34 | 37 | 0.030218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5192-181_0_3_line_39 |  | 36 | 54 | 0.0060892 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5192-181_0_3_line_40 |  | 38 | 39 | 0.014659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5192-181_0_3_line_41 |  | 39 | 40 | 0.031977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5192-181_0_3_line_42 |  | 39 | 41 | 0.033237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5192-181_0_3_line_43 |  | 41 | 42 | 0.053267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5192-181_0_3_line_44 |  | 42 | 43 | 0.026611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5192-181_0_3_line_45 |  | 43 | 49 | 0.003093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5192-181_0_3_line_46 |  | 44 | 45 | 0.0028236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5192-181_0_3_line_47 |  | 44 | 46 | 0.011864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5192-181_0_3_line_48 |  | 45 | 47 | 0.019093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5192-181_0_3_line_49 |  | 46 | 48 | 0.010355 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5192-181_0_3_line_50 |  | 47 | 49 | 0.028195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5192-181_0_3_line_51 |  | 48 | 50 | 0.007807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5192-181_0_3_line_52 |  | 50 | 51 | 0.025231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5192-181_0_3_line_53 |  | 50 | 52 | 0.014498 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5192-181_0_3_line_54 |  | 51 | 55 | 0.022404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5192-181_0_3_line_55 |  | 52 | 53 | 0.016013 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5192-181_0_3_line_56 |  | 53 | 54 | 0.010834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5192-181_0_3_line_57 |  | 55 | 56 | 0.024942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5192-181_0_3_line_58 |  | 57 | 58 | 0.011401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5192-181_0_3_line_59 |  | 58 | 62 | 0.040938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5192-181_0_3_line_60 |  | 59 | 60 | 0.009194 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5192-181_0_3_line_61 |  | 59 | 61 | 0.026261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5192-181_0_3_line_62 |  | 61 | 62 | 0.0046184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5192-181_0_3_line_63 |  | 62 | 64 | 0.013096 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5192-181_0_3_trafo_20 | 0.63 MVA 20/0.4 kV | 65 | 28 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2719071.8507 | 1098088.5048 | 2719071.8513 | 1098088.5159
1 | 2719072.9158 | 1098106.9592 | 2719072.474 | 1098100.6572 | 2719071.8513 | 1098088.5159
2 | 2719071.8507 | 1098088.5048 | 2719071.0993 | 1098073.8531
3 | 2719072.9158 | 1098106.9592 | 2719099.1988 | 1098104.8616
4 | 2719074.3825 | 1098127.7579 | 2719072.9158 | 1098106.9592
5 | 2719066.4574 | 1097998.6353 | 2719069.1063 | 1098034.9902 | 2719071.0993 | 1098073.8531
6 | 2719099.1988 | 1098104.8616 | 2719103.9429 | 1098100.3181 | 2719107.1063 | 1098084.7136
7 | 2719074.3825 | 1098127.7579 | 2719060.6142 | 1098127.4505
8 | 2719066.4574 | 1097998.6353 | 2719064.5693 | 1097989.0583 | 2719049.7571 | 1097987.6005 | 2719049.1276 | 1097992.8474 | 2719049.9033 | 1097995.5533 | 2719050.9883 | 1097998.6879 | 2719051.471 | 1098000.9322
9 | 2719066.4574 | 1097998.6353 | 2719090.4088 | 1098006.043 | 2719094.0199 | 1098007.1479 | 2719096.9109 | 1098008.2386 | 2719099.7076 | 1098008.6048 | 2719102.3136 | 1098008.0332 | 2719104.5996 | 1098007.978 | 2719106.9821 | 1098008.5362 | 2719108.6105 | 1098010.0247 | 2719108.988 | 1098012.1002 | 2719107.7497 | 1098014.1691
10 | 2719107.1063 | 1098084.7136 | 2719108.3591 | 1098078.5339 | 2719113.1942 | 1098069.3557 | 2719114.1568 | 1098066.8252
11 | 2719043.2014 | 1098134.3627 | 2719058.0234 | 1098127.3927 | 2719060.6142 | 1098127.4505
12 | 2719047.6811 | 1098019.2262 | 2719051.5701 | 1098006.1489 | 2719051.7479 | 1098002.2163 | 2719051.471 | 1098000.9322
13 | 2718983.4895 | 1097981.0539 | 2719049.7571 | 1097987.6005 | 2719049.1276 | 1097992.8474 | 2719049.9033 | 1097995.5533 | 2719050.9883 | 1097998.6879 | 2719051.471 | 1098000.9322
14 | 2719101.3856 | 1098023.7593 | 2719102.0457 | 1098021.693 | 2719104.173 | 1098019.4665 | 2719107.6988 | 1098014.2542 | 2719107.7497 | 1098014.1691
15 | 2719116.1475 | 1098061.592 | 2719114.1568 | 1098066.8252
16 | 2719043.2014 | 1098134.3627 | 2719034.0899 | 1098128.7034
17 | 2719021.0626 | 1098121.0968 | 2719026.7871 | 1098124.1675 | 2719034.0899 | 1098128.7034
18 | 2718983.4895 | 1097981.0539 | 2718982.0843 | 1098003.3641 | 2718981.5785 | 1098009.4114
19 | 2718947.7757 | 1097977.419 | 2718953.2469 | 1097978.071 | 2718983.4895 | 1097981.0539
20 | 2718995.917 | 1098019.5189 | 2718980.83 | 1098018.361 | 2718981.5785 | 1098009.4114
21 | 2718947.7757 | 1097977.419 | 2718945.3536 | 1098016.8545 | 2718943.9324 | 1098019.4173 | 2718941.8458 | 1098021.1555 | 2718930.661 | 1098020.2697
22 | 2719098.0592 | 1098039.7385 | 2719100.9015 | 1098032.6449 | 2719101.3856 | 1098023.7593
23 | 2718930.661 | 1098020.2697 | 2718928.88 | 1098020.1287
24 | 2718916.6651 | 1098019.1614 | 2718928.88 | 1098020.1287
25 | 2718996.5905 | 1098019.5706 | 2718995.917 | 1098019.5189
26 | 2719016.4296 | 1098021.0932 | 2718996.5905 | 1098019.5706
27 | 2719016.4296 | 1098021.0932 | 2719014.985 | 1098030.7828
28 | 2719016.4296 | 1098021.0932 | 2719017.9047 | 1098011.221
29 | 2718997.3736 | 1098108.8595 | 2718983.842 | 1098103.4948
30 | 2718999.1123 | 1098109.5488 | 2718997.3736 | 1098108.8595
31 | 2718977.6281 | 1098101.0313 | 2718983.842 | 1098103.4948
32 | 2718999.1123 | 1098109.5488 | 2718996.1914 | 1098115.9183 | 2718993.952 | 1098125.3706
33 | 2718999.1123 | 1098109.5488 | 2719000.734 | 1098110.1921 | 2719004.1458 | 1098112.0223
34 | 2718965.2597 | 1098096.1277 | 2718977.6281 | 1098101.0313
35 | 2718993.4707 | 1098127.4021 | 2718993.952 | 1098125.3706
36 | 2719021.0626 | 1098121.0968 | 2719004.1458 | 1098112.0223
37 | 2718965.2597 | 1098096.1277 | 2718958.5158 | 1098093.4541 | 2718955.9333 | 1098092.9733
38 | 2718985.9956 | 1098156.6711 | 2718988.7187 | 1098147.4605 | 2718993.4707 | 1098127.4021
39 | 2718955.9333 | 1098092.9733 | 2718949.9469 | 1098091.8588
40 | 2718860.6976 | 1098015.8754 | 2718859.7965 | 1098030.5063
41 | 2718879.111 | 1098000.7362 | 2718876.9258 | 1098015.0256 | 2718876.2519 | 1098016.6135 | 2718874.3309 | 1098017.4098 | 2718872.3296 | 1098017.5596 | 2718860.6976 | 1098015.8754
42 | 2718827.8147 | 1098010.4732 | 2718839.2027 | 1098012.7529 | 2718860.6976 | 1098015.8754
43 | 2718827.8147 | 1098010.4732 | 2718818.4356 | 1098049.628 | 2718818.1812 | 1098062.6296
44 | 2718827.5842 | 1098084.809 | 2718820.4823 | 1098080.8119 | 2718818.0338 | 1098070.1677 | 2718818.1812 | 1098062.6296
45 | 2718830.4745 | 1098085.933 | 2718827.5842 | 1098084.809
46 | 2718879.1559 | 1098085.1198 | 2718876.3324 | 1098085.1044
47 | 2718879.1559 | 1098085.1198 | 2718891.0201 | 1098085.1847
48 | 2718876.3324 | 1098085.1044 | 2718868.2665 | 1098085.0603 | 2718857.4741 | 1098087.3245
49 | 2718901.3752 | 1098085.2414 | 2718891.0201 | 1098085.1847
50 | 2718830.4745 | 1098085.933 | 2718842.2354 | 1098090.5217 | 2718857.4741 | 1098087.3245
51 | 2718901.3752 | 1098085.2414 | 2718909.2051 | 1098085.2835
52 | 2718909.2051 | 1098085.2835 | 2718907.8437 | 1098091.917 | 2718905.9702 | 1098110.2808
53 | 2718909.2051 | 1098085.2835 | 2718914.7967 | 1098085.3151 | 2718923.5529 | 1098086.9452
54 | 2718905.9702 | 1098110.2808 | 2718905.1312 | 1098118.5045 | 2718914.5209 | 1098129.0734
55 | 2718923.5529 | 1098086.9452 | 2718939.2954 | 1098089.8759
56 | 2718939.2954 | 1098089.8759 | 2718949.9469 | 1098091.8588
57 | 2718921.8301 | 1098147.796 | 2718915.2757 | 1098146.3001 | 2718912.8671 | 1098143.5177 | 2718914.5209 | 1098129.0734
58 | 2719120.2011 | 1098050.9358 | 2719116.1475 | 1098061.592
59 | 2719120.2011 | 1098050.9358 | 2719160.5581 | 1098057.8084
60 | 2719163.1244 | 1098088.5811 | 2719153.9318 | 1098089.3013
61 | 2719163.1244 | 1098088.5811 | 2719160.9419 | 1098062.4109
62 | 2719160.5581 | 1098057.8084 | 2719160.9419 | 1098062.4109
63 | 2719162.5163 | 1098045.1462 | 2719162.4328 | 1098045.2708 | 2719161.2422 | 1098047.5268 | 2719160.8917 | 1098049.5991 | 2719161.0399 | 1098052.7042 | 2719160.378 | 1098055.6488 | 2719160.5581 | 1098057.8084

## bus_geodata
| x | y | coords
0 | 2719071.8513 | 1098088.5159
1 | 2719071.8507 | 1098088.5048
2 | 2719072.9158 | 1098106.9592
3 | 2719071.0993 | 1098073.8531
4 | 2719099.1988 | 1098104.8616
5 | 2719074.3825 | 1098127.7579
6 | 2719066.4574 | 1097998.6353
7 | 2719107.1063 | 1098084.7136
8 | 2719060.6142 | 1098127.4505
9 | 2719051.471 | 1098000.9322
10 | 2719107.7497 | 1098014.1691
11 | 2719114.1568 | 1098066.8252
12 | 2719043.2014 | 1098134.3627
13 | 2719034.0899 | 1098128.7034
14 | 2719047.6811 | 1098019.2262
15 | 2718983.4895 | 1097981.0539
16 | 2718981.5785 | 1098009.4114
17 | 2718947.7757 | 1097977.419
18 | 2719101.3856 | 1098023.7593
19 | 2718930.661 | 1098020.2697
20 | 2718928.88 | 1098020.1287
21 | 2718916.6651 | 1098019.1614
22 | 2718995.917 | 1098019.5189
23 | 2718996.5905 | 1098019.5706
24 | 2719016.4296 | 1098021.0932
25 | 2719014.985 | 1098030.7828
26 | 2719017.9047 | 1098011.221
27 | 2718997.3736 | 1098108.8595
28 | 2718983.842 | 1098103.4948
29 | 2718999.1123 | 1098109.5488
30 | 2718977.6281 | 1098101.0313
31 | 2718993.952 | 1098125.3706
32 | 2719004.1458 | 1098112.0223
33 | 2718965.2597 | 1098096.1277
34 | 2718993.4707 | 1098127.4021
35 | 2719021.0626 | 1098121.0968
36 | 2718955.9333 | 1098092.9733
37 | 2718985.9956 | 1098156.6711
38 | 2718859.7965 | 1098030.5063
39 | 2718860.6976 | 1098015.8754
40 | 2718879.111 | 1098000.7362
41 | 2718827.8147 | 1098010.4732
42 | 2718818.1812 | 1098062.6296
43 | 2718827.5842 | 1098084.809
44 | 2718879.1559 | 1098085.1198
45 | 2718876.3324 | 1098085.1044
46 | 2718891.0201 | 1098085.1847
47 | 2718857.4741 | 1098087.3245
48 | 2718901.3752 | 1098085.2414
49 | 2718830.4745 | 1098085.933
50 | 2718909.2051 | 1098085.2835
51 | 2718905.9702 | 1098110.2808
52 | 2718923.5529 | 1098086.9452
53 | 2718939.2954 | 1098089.8759
54 | 2718949.9469 | 1098091.8588
55 | 2718914.5209 | 1098129.0734
56 | 2718921.8301 | 1098147.796
57 | 2719116.1475 | 1098061.592
58 | 2719120.2011 | 1098050.9358
59 | 2719163.1244 | 1098088.5811
60 | 2719153.9318 | 1098089.3013
61 | 2719160.9419 | 1098062.4109
62 | 2719160.5581 | 1098057.8084
63 | 2719098.0592 | 1098039.7385
64 | 2719162.5163 | 1098045.1462
65 | 2718983.842 | 1098103.4948

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1