## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5192-184_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5192-184_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5192-184_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5192-184_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5192-184_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5192-184_0_4_node_54 | 0.4 | n |  | TRUE
6 | bus_LV_5192-184_0_4_node_18 | 0.4 | n |  | TRUE
7 | bus_LV_5192-184_0_4_node_53 | 0.4 | n |  | TRUE
8 | bus_LV_5192-184_0_4_node_37 | 0.4 | n |  | TRUE
9 | bus_LV_5192-184_0_4_node_19 | 0.4 | n |  | TRUE
10 | bus_LV_5192-184_0_4_node_16 | 0.4 | n |  | TRUE
11 | bus_LV_5192-184_0_4_node_25 | 0.4 | n |  | TRUE
12 | bus_LV_5192-184_0_4_node_22 | 0.4 | n |  | TRUE
13 | bus_LV_5192-184_0_4_node_20 | 0.4 | n |  | TRUE
14 | bus_LV_5192-184_0_4_node_5 | 0.4 | n |  | TRUE
15 | bus_LV_5192-184_0_4_node_6 | 0.4 | n |  | TRUE
16 | bus_LV_5192-184_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_5192-184_0_4_node_34 | 0.4 | n |  | TRUE
18 | bus_LV_5192-184_0_4_node_50 | 0.4 | n |  | TRUE
19 | bus_LV_5192-184_0_4_node_48 | 0.4 | n |  | TRUE
20 | bus_LV_5192-184_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_5192-184_0_4_node_13 | 0.4 | n |  | TRUE
22 | bus_LV_5192-184_0_4_node_10 | 0.4 | n |  | TRUE
23 | bus_LV_5192-184_0_4_node_11 | 0.4 | n |  | TRUE
24 | bus_LV_5192-184_0_4_node_12 | 0.4 | n |  | TRUE
25 | bus_LV_5192-184_0_4_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_5192-184_0_4_node_46 | 0.4 | n |  | TRUE
27 | bus_LV_5192-184_0_4_node_39 | 0.4 | n |  | TRUE
28 | bus_LV_5192-184_0_4_node_21 | 0.4 | n |  | TRUE
29 | bus_LV_5192-184_0_4_node_43 | 0.4 | n |  | TRUE
30 | bus_LV_5192-184_0_4_node_23 | 0.4 | n |  | TRUE
31 | bus_LV_5192-184_0_4_node_24 | 0.4 | n |  | TRUE
32 | bus_LV_5192-184_0_4_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_5192-184_0_4_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_5192-184_0_4_node_38 | 0.4 | n |  | TRUE
35 | bus_LV_5192-184_0_4_node_26 | 0.4 | n |  | TRUE
36 | bus_LV_5192-184_0_4_node_27 | 0.4 | n |  | TRUE
37 | bus_LV_5192-184_0_4_node_28 | 0.4 | n |  | TRUE
38 | bus_LV_5192-184_0_4_node_29 | 0.4 | n |  | TRUE
39 | bus_LV_5192-184_0_4_node_30 | 0.4 | n |  | TRUE
40 | bus_LV_5192-184_0_4_node_47 | 0.4 | n |  | TRUE
41 | bus_LV_5192-184_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_5192-184_0_4_node_32 | 0.4 | n |  | TRUE
43 | bus_LV_5192-184_0_4_node_33 | 0.4 | n |  | TRUE
44 | bus_LV_5192-184_0_4_node_58 | 0.4 | n |  | TRUE
45 | bus_LV_5192-184_0_4_node_49 | 0.4 | n |  | TRUE
46 | bus_LV_5192-184_0_4_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_5192-184_0_4_node_41 | 0.4 | n |  | TRUE
48 | bus_LV_5192-184_0_4_node_42 | 0.4 | n |  | TRUE
49 | bus_LV_5192-184_0_4_node_44 | 0.4 | n |  | TRUE
50 | bus_LV_5192-184_0_4_node_45 | 0.4 | n |  | TRUE
51 | bus_LV_5192-184_0_4_node_57 | 0.4 | n |  | TRUE
52 | bus_LV_5192-184_0_4_node_52 | 0.4 | n |  | TRUE
53 | bus_LV_5192-184_0_4_node_56 | 0.4 | n |  | TRUE
54 | bus_LV_5192-184_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_5192-184_0_4_node_55 | 0.4 | n |  | TRUE
56 | bus_MV_250_0_node_45 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5192-184_0_4_load_0 | 0 | 0.0054276 | 0.0013603 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5192-184_0_4_load_1 | 1 | 0.0022442 | 0.00056246 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5192-184_0_4_load_2 | 2 | 0.0068614 | 0.0017196 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5192-184_0_4_load_3 | 3 | 0.0039145 | 0.00098106 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5192-184_0_4_load_54 | 5 | 0.0039752 | 0.00099628 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5192-184_0_4_load_53 | 7 | 0.0050957 | 0.0012771 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5192-184_0_4_load_37 | 8 | 0.007726 | 0.0019363 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5192-184_0_4_load_16 | 10 | 0.011698 | 0.0029317 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5192-184_0_4_load_25 | 11 | 0.014334 | 0.0035924 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5192-184_0_4_load_22 | 12 | 0.011616 | 0.0029112 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5192-184_0_4_load_5 | 14 | 0.0088306 | 0.0022132 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5192-184_0_4_load_6 | 15 | 0.031441 | 0.0078798 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5192-184_0_4_load_50 | 18 | 0.0022552 | 0.00056521 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5192-184_0_4_load_48 | 19 | 0.045971 | 0.011522 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5192-184_0_4_load_15 | 20 | 0.017095 | 0.0042845 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5192-184_0_4_load_13 | 21 | 0.024604 | 0.0061663 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5192-184_0_4_load_10 | 22 | 0.0096426 | 0.0024167 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5192-184_0_4_load_11 | 23 | 0.0063136 | 0.0015823 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5192-184_0_4_load_12 | 24 | 0.009703 | 0.0024318 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5192-184_0_4_load_14 | 25 | 0.0041509 | 0.0010403 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5192-184_0_4_load_46 | 26 | 0.0048212 | 0.0012083 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5192-184_0_4_load_21 | 28 | 0.020307 | 0.0050895 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5192-184_0_4_load_43 | 29 | 0.0022849 | 0.00057266 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5192-184_0_4_load_23 | 30 | 0.0065022 | 0.0016296 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5192-184_0_4_load_24 | 31 | 0.0085789 | 0.0021501 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5192-184_0_4_load_35 | 32 | 0.01248 | 0.0031279 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5192-184_0_4_load_36 | 33 | 0.013039 | 0.0032679 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5192-184_0_4_load_26 | 35 | 0.016737 | 0.0041947 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5192-184_0_4_load_27 | 36 | 0.0076474 | 0.0019166 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5192-184_0_4_load_28 | 37 | 0.018293 | 0.0045847 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5192-184_0_4_load_29 | 38 | 0.012418 | 0.0031122 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5192-184_0_4_load_30 | 39 | 0.005583 | 0.0013992 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5192-184_0_4_load_31 | 41 | 0.026966 | 0.0067582 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5192-184_0_4_load_58 | 44 | 0.018908 | 0.0047389 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5192-184_0_4_load_40 | 46 | 0.0024618 | 0.00061699 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5192-184_0_4_load_44 | 49 | 0.0017029 | 0.00042678 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5192-184_0_4_load_45 | 50 | 0.0017869 | 0.00044784 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5192-184_0_4_load_56 | 53 | 0.0038253 | 0.00095871 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5192-184_0_4_load_51 | 54 | 0.0016224 | 0.00040661 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5192-184_0_4_load_55 | 55 | 0.0054342 | 0.0013619 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 31 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5192-184_0_4_line_0 |  | 0 | 1 | 0.041348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5192-184_0_4_line_1 |  | 0 | 2 | 0.011231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5192-184_0_4_line_2 |  | 1 | 3 | 0.0045953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5192-184_0_4_line_3 |  | 2 | 4 | 0.038911 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5192-184_0_4_line_4 |  | 3 | 5 | 0.0043011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5192-184_0_4_line_5 |  | 4 | 6 | 0.022543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5192-184_0_4_line_6 |  | 4 | 7 | 0.011767 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5192-184_0_4_line_7 |  | 5 | 8 | 0.0037205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5192-184_0_4_line_8 |  | 6 | 9 | 0.04412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
9 | LV_5192-184_0_4_line_9 |  | 6 | 10 | 0.07106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5192-184_0_4_line_10 |  | 7 | 13 | 0.030646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5192-184_0_4_line_11 |  | 8 | 25 | 0.0012039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5192-184_0_4_line_12 |  | 9 | 11 | 0.037282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
13 | LV_5192-184_0_4_line_13 |  | 9 | 12 | 0.015251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_5192-184_0_4_line_14 |  | 11 | 27 | 0.060925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_5192-184_0_4_line_15 |  | 12 | 28 | 0.035421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
16 | LV_5192-184_0_4_line_16 |  | 13 | 26 | 0.011286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5192-184_0_4_line_17 |  | 14 | 15 | 0.047713 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5192-184_0_4_line_18 |  | 15 | 16 | 0.00069345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5192-184_0_4_line_19 |  | 16 | 17 | 0.042752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5192-184_0_4_line_20 |  | 17 | 18 | 0.0050589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
21 | LV_5192-184_0_4_line_21 |  | 17 | 19 | 0.02093 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
22 | LV_5192-184_0_4_line_22 |  | 18 | 40 | 0.0016195 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
23 | LV_5192-184_0_4_line_23 |  | 19 | 45 | 0.043211 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
24 | LV_5192-184_0_4_line_24 |  | 20 | 21 | 0.035661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5192-184_0_4_line_25 |  | 21 | 23 | 0.0072051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5192-184_0_4_line_26 |  | 22 | 23 | 0.024905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5192-184_0_4_line_27 |  | 22 | 24 | 0.017579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5192-184_0_4_line_28 |  | 24 | 25 | 0.016259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5192-184_0_4_line_29 |  | 26 | 29 | 0.023398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5192-184_0_4_line_30 |  | 27 | 34 | 0.006818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_5192-184_0_4_line_31 |  | 28 | 30 | 0.024797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_5192-184_0_4_line_32 |  | 29 | 47 | 0.0017422 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5192-184_0_4_line_33 |  | 30 | 31 | 0.013582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
34 | LV_5192-184_0_4_line_34 |  | 31 | 32 | 0.0091164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5192-184_0_4_line_35 |  | 32 | 33 | 0.012176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5192-184_0_4_line_36 |  | 34 | 38 | 0.055216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
37 | LV_5192-184_0_4_line_37 |  | 35 | 36 | 0.0010889 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
38 | LV_5192-184_0_4_line_38 |  | 35 | 37 | 0.023083 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
39 | LV_5192-184_0_4_line_39 |  | 36 | 38 | 0.023735 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
40 | LV_5192-184_0_4_line_40 |  | 37 | 39 | 0.0051201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
41 | LV_5192-184_0_4_line_41 |  | 39 | 40 | 0.017917 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
42 | LV_5192-184_0_4_line_42 |  | 41 | 42 | 0.091282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5192-184_0_4_line_43 |  | 42 | 43 | 0.085196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
44 | LV_5192-184_0_4_line_44 |  | 43 | 44 | 0.042263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5192-184_0_4_line_45 |  | 43 | 45 | 0.068388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_5192-184_0_4_line_46 |  | 46 | 47 | 0.012401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5192-184_0_4_line_47 |  | 46 | 48 | 0.0080255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5192-184_0_4_line_48 |  | 47 | 49 | 0.016602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5192-184_0_4_line_49 |  | 48 | 50 | 0.018337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5192-184_0_4_line_50 |  | 49 | 51 | 0.01279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5192-184_0_4_line_51 |  | 50 | 52 | 0.0069386 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5192-184_0_4_line_52 |  | 51 | 53 | 0.0021834 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5192-184_0_4_line_53 |  | 52 | 54 | 0.011446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5192-184_0_4_line_54 |  | 53 | 55 | 0.014878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5192-184_0_4_trafo_24 | 0.63 MVA 20/0.4 kV | 56 | 31 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4
0 | 2718560.2744 | 1097411.3322 | 2718546.3904 | 1097395.4408 | 2718532.9975 | 1097380.2585
1 | 2718560.2744 | 1097411.3322 | 2718567.6639 | 1097419.7901
2 | 2718532.9975 | 1097380.2585 | 2718529.9575 | 1097376.8124
3 | 2718601.1311 | 1097438.4495 | 2718593.5848 | 1097436.5343 | 2718579.6948 | 1097429.4362 | 2718570.7811 | 1097423.3581 | 2718567.6639 | 1097419.7901
4 | 2718529.9575 | 1097376.8124 | 2718527.1122 | 1097373.5869
5 | 2718601.1311 | 1097438.4495 | 2718606.4531 | 1097426.534 | 2718613.9383 | 1097432.373
6 | 2718601.1311 | 1097438.4495 | 2718597.3097 | 1097449.579
7 | 2718527.1122 | 1097373.5869 | 2718524.651 | 1097370.7969
8 | 2718613.9383 | 1097432.373 | 2718606.4531 | 1097426.534 | 2718620.505 | 1097403.9259 | 2718625.5378 | 1097397.6976
9 | 2718613.9383 | 1097432.373 | 2718619.7754 | 1097436.9234 | 2718645.0958 | 1097475.9112 | 2718651.2397 | 1097485.3711 | 2718656.5418 | 1097487.9384
10 | 2718587.3573 | 1097478.5641 | 2718597.3097 | 1097449.579
11 | 2718523.8545 | 1097369.894 | 2718524.651 | 1097370.7969
12 | 2718625.5378 | 1097397.6976 | 2718630.3009 | 1097391.7976 | 2718651.4521 | 1097370.9487
13 | 2718625.5378 | 1097397.6976 | 2718611.8677 | 1097390.9367
14 | 2718696.4403 | 1097329.9236 | 2718671.7128 | 1097350.9776 | 2718651.4521 | 1097370.9487
15 | 2718580.1179 | 1097375.2341 | 2718611.8677 | 1097390.9367
16 | 2718587.3573 | 1097478.5641 | 2718576.7524 | 1097474.702
17 | 2718482.2101 | 1097251.8267 | 2718527.3058 | 1097267.4109
18 | 2718527.3058 | 1097267.4109 | 2718527.9612 | 1097267.6374
19 | 2718527.9612 | 1097267.6374 | 2718568.4734 | 1097281.6483
20 | 2718568.4734 | 1097281.6483 | 2718573.2777 | 1097283.2329
21 | 2718568.4734 | 1097281.6483 | 2718577.726 | 1097263.2271 | 2718577.9239 | 1097262.9807
22 | 2718574.8157 | 1097283.7401 | 2718573.2777 | 1097283.2329
23 | 2718604.9826 | 1097229.2909 | 2718577.9239 | 1097262.9807
24 | 2718483.7763 | 1097317.6318 | 2718464.2399 | 1097287.798
25 | 2718483.7763 | 1097317.6318 | 2718487.7235 | 1097323.6595
26 | 2718502.3187 | 1097343.8069 | 2718494.3974 | 1097333.8511 | 2718487.7235 | 1097323.6595
27 | 2718513.2636 | 1097357.563 | 2718502.3187 | 1097343.8069
28 | 2718513.2636 | 1097357.563 | 2718515.901 | 1097360.8779 | 2718523.8545 | 1097369.894
29 | 2718554.7666 | 1097466.6951 | 2718576.7524 | 1097474.702
30 | 2718696.4403 | 1097329.9236 | 2718694.5932 | 1097323.3608
31 | 2718569.1236 | 1097359.8429 | 2718565.9238 | 1097368.2141 | 2718580.1179 | 1097375.2341
32 | 2718553.1296 | 1097466.0989 | 2718554.7666 | 1097466.6951
33 | 2718573.9728 | 1097347.1565 | 2718573.9728 | 1097347.1565 | 2718569.1236 | 1097359.8429
34 | 2718573.9728 | 1097347.1565 | 2718582.4475 | 1097350.5162
35 | 2718593.7668 | 1097355.0036 | 2718582.4475 | 1097350.5162
36 | 2718694.5932 | 1097323.3608 | 2718642.1708 | 1097306.0202
37 | 2718619.6365 | 1097298.5662 | 2718618.6027 | 1097298.2242
38 | 2718596.6872 | 1097290.9749 | 2718618.6027 | 1097298.2242
39 | 2718619.6365 | 1097298.5662 | 2718642.1708 | 1097306.0202
40 | 2718596.6872 | 1097290.9749 | 2718591.8261 | 1097289.3669
41 | 2718574.8157 | 1097283.7401 | 2718591.8261 | 1097289.3669
42 | 2718525.4239 | 1097149.5395 | 2718502.5928 | 1097237.9196
43 | 2718525.4239 | 1097149.5395 | 2718569.1295 | 1097158.3423 | 2718582.3363 | 1097160.3903 | 2718609.2594 | 1097164.5851
44 | 2718609.2594 | 1097164.5851 | 2718595.8729 | 1097204.6739
45 | 2718604.9826 | 1097229.2909 | 2718612.9744 | 1097165.158 | 2718609.2594 | 1097164.5851
46 | 2718553.1296 | 1097466.0989 | 2718550.1779 | 1097478.1432
47 | 2718548.7434 | 1097486.0383 | 2718550.0407 | 1097478.703 | 2718550.1779 | 1097478.1432
48 | 2718553.1296 | 1097466.0989 | 2718538.9308 | 1097460.9296 | 2718537.5779 | 1097460.303
49 | 2718548.7434 | 1097486.0383 | 2718547.8782 | 1097491.8699 | 2718548.5398 | 1097504.2939
50 | 2718525.9721 | 1097454.9283 | 2718537.5779 | 1097460.303
51 | 2718549.5166 | 1097511.1152 | 2718548.7738 | 1097508.6879 | 2718548.5398 | 1097504.2939
52 | 2718525.9721 | 1097454.9283 | 2718523.9911 | 1097454.0102
53 | 2718549.5166 | 1097511.1152 | 2718538.0986 | 1097510.3103
54 | 2718510.377 | 1097448.0187 | 2718516.5295 | 1097450.5522 | 2718523.9911 | 1097454.0102

## bus_geodata
| x | y | coords
0 | 2718560.2744 | 1097411.3322
1 | 2718532.9975 | 1097380.2585
2 | 2718567.6639 | 1097419.7901
3 | 2718529.9575 | 1097376.8124
4 | 2718601.1311 | 1097438.4495
5 | 2718527.1122 | 1097373.5869
6 | 2718613.9383 | 1097432.373
7 | 2718597.3097 | 1097449.579
8 | 2718524.651 | 1097370.7969
9 | 2718625.5378 | 1097397.6976
10 | 2718656.5418 | 1097487.9384
11 | 2718651.4521 | 1097370.9487
12 | 2718611.8677 | 1097390.9367
13 | 2718587.3573 | 1097478.5641
14 | 2718482.2101 | 1097251.8267
15 | 2718527.3058 | 1097267.4109
16 | 2718527.9612 | 1097267.6374
17 | 2718568.4734 | 1097281.6483
18 | 2718573.2777 | 1097283.2329
19 | 2718577.9239 | 1097262.9807
20 | 2718464.2399 | 1097287.798
21 | 2718483.7763 | 1097317.6318
22 | 2718502.3187 | 1097343.8069
23 | 2718487.7235 | 1097323.6595
24 | 2718513.2636 | 1097357.563
25 | 2718523.8545 | 1097369.894
26 | 2718576.7524 | 1097474.702
27 | 2718696.4403 | 1097329.9236
28 | 2718580.1179 | 1097375.2341
29 | 2718554.7666 | 1097466.6951
30 | 2718569.1236 | 1097359.8429
31 | 2718573.9728 | 1097347.1565
32 | 2718582.4475 | 1097350.5162
33 | 2718593.7668 | 1097355.0036
34 | 2718694.5932 | 1097323.3608
35 | 2718618.6027 | 1097298.2242
36 | 2718619.6365 | 1097298.5662
37 | 2718596.6872 | 1097290.9749
38 | 2718642.1708 | 1097306.0202
39 | 2718591.8261 | 1097289.3669
40 | 2718574.8157 | 1097283.7401
41 | 2718502.5928 | 1097237.9196
42 | 2718525.4239 | 1097149.5395
43 | 2718609.2594 | 1097164.5851
44 | 2718595.8729 | 1097204.6739
45 | 2718604.9826 | 1097229.2909
46 | 2718550.1779 | 1097478.1432
47 | 2718553.1296 | 1097466.0989
48 | 2718548.7434 | 1097486.0383
49 | 2718537.5779 | 1097460.303
50 | 2718548.5398 | 1097504.2939
51 | 2718525.9721 | 1097454.9283
52 | 2718549.5166 | 1097511.1152
53 | 2718523.9911 | 1097454.0102
54 | 2718538.0986 | 1097510.3103
55 | 2718510.377 | 1097448.0187
56 | 2718593.7668 | 1097355.0036

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1