## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5192-9_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5192-9_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5192-9_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5192-9_0_4_node_4 | 0.4 | n |  | TRUE
4 | bus_LV_5192-9_0_4_node_41 | 0.4 | n |  | TRUE
5 | bus_LV_5192-9_0_4_node_42 | 0.4 | n |  | TRUE
6 | bus_LV_5192-9_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_5192-9_0_4_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_5192-9_0_4_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_5192-9_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_5192-9_0_4_node_35 | 0.4 | n |  | TRUE
11 | bus_LV_5192-9_0_4_node_33 | 0.4 | n |  | TRUE
12 | bus_LV_5192-9_0_4_node_52 | 0.4 | n |  | TRUE
13 | bus_LV_5192-9_0_4_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_5192-9_0_4_node_9 | 0.4 | n |  | TRUE
15 | bus_LV_5192-9_0_4_node_10 | 0.4 | n |  | TRUE
16 | bus_LV_5192-9_0_4_node_12 | 0.4 | n |  | TRUE
17 | bus_LV_5192-9_0_4_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_5192-9_0_4_node_15 | 0.4 | n |  | TRUE
19 | bus_LV_5192-9_0_4_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_5192-9_0_4_node_46 | 0.4 | n |  | TRUE
21 | bus_LV_5192-9_0_4_node_43 | 0.4 | n |  | TRUE
22 | bus_LV_5192-9_0_4_node_16 | 0.4 | n |  | TRUE
23 | bus_LV_5192-9_0_4_node_17 | 0.4 | n |  | TRUE
24 | bus_LV_5192-9_0_4_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_5192-9_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_5192-9_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_5192-9_0_4_node_18 | 0.4 | n |  | TRUE
28 | bus_LV_5192-9_0_4_node_49 | 0.4 | n |  | TRUE
29 | bus_LV_5192-9_0_4_node_27 | 0.4 | n |  | TRUE
30 | bus_LV_5192-9_0_4_node_48 | 0.4 | n |  | TRUE
31 | bus_LV_5192-9_0_4_node_21 | 0.4 | n |  | TRUE
32 | bus_LV_5192-9_0_4_node_28 | 0.4 | n |  | TRUE
33 | bus_LV_5192-9_0_4_node_51 | 0.4 | n |  | TRUE
34 | bus_LV_5192-9_0_4_node_26 | 0.4 | n |  | TRUE
35 | bus_LV_5192-9_0_4_node_57 | 0.4 | n |  | TRUE
36 | bus_LV_5192-9_0_4_node_44 | 0.4 | n |  | TRUE
37 | bus_LV_5192-9_0_4_node_24 | 0.4 | n |  | TRUE
38 | bus_LV_5192-9_0_4_node_25 | 0.4 | n |  | TRUE
39 | bus_LV_5192-9_0_4_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_5192-9_0_4_node_30 | 0.4 | n |  | TRUE
41 | bus_LV_5192-9_0_4_node_31 | 0.4 | n |  | TRUE
42 | bus_LV_5192-9_0_4_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_5192-9_0_4_node_56 | 0.4 | n |  | TRUE
44 | bus_LV_5192-9_0_4_node_36 | 0.4 | n |  | TRUE
45 | bus_LV_5192-9_0_4_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_5192-9_0_4_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_5192-9_0_4_node_40 | 0.4 | n |  | TRUE
48 | bus_LV_5192-9_0_4_node_39 | 0.4 | n |  | TRUE
49 | bus_LV_5192-9_0_4_node_55 | 0.4 | n |  | TRUE
50 | bus_LV_5192-9_0_4_node_53 | 0.4 | n |  | TRUE
51 | bus_LV_5192-9_0_4_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_5192-9_0_4_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_5192-9_0_4_node_47 | 0.4 | n |  | TRUE
54 | bus_LV_5192-9_0_4_node_50 | 0.4 | n |  | TRUE
55 | bus_MV_248_0_node_91 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5192-9_0_4_load_0 | 0 | 0.0076794 | 0.0019246 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5192-9_0_4_load_1 | 1 | 0.0057947 | 0.0014523 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5192-9_0_4_load_2 | 2 | 0.0065497 | 0.0016415 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5192-9_0_4_load_4 | 3 | 0.0075377 | 0.0018891 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5192-9_0_4_load_5 | 6 | 0.013371 | 0.0033511 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5192-9_0_4_load_6 | 7 | 0.010133 | 0.0025396 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5192-9_0_4_load_7 | 8 | 0.020937 | 0.0052473 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5192-9_0_4_load_35 | 10 | 0.015996 | 0.004009 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5192-9_0_4_load_33 | 11 | 0.017911 | 0.004489 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5192-9_0_4_load_9 | 14 | 0.005453 | 0.0013666 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5192-9_0_4_load_10 | 15 | 0.0055582 | 0.001393 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5192-9_0_4_load_14 | 17 | 0.0075791 | 0.0018995 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5192-9_0_4_load_15 | 18 | 0.0061983 | 0.0015534 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5192-9_0_4_load_46 | 20 | 0.0030631 | 0.00076769 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5192-9_0_4_load_43 | 21 | 0.0070021 | 0.0017549 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5192-9_0_4_load_16 | 22 | 0.005685 | 0.0014248 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5192-9_0_4_load_23 | 25 | 0.0075536 | 0.0018931 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5192-9_0_4_load_18 | 27 | 0.0065422 | 0.0016396 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5192-9_0_4_load_49 | 28 | 0.0049136 | 0.0012315 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5192-9_0_4_load_27 | 29 | 0.0088636 | 0.0022214 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5192-9_0_4_load_28 | 32 | 0.00231 | 0.00057894 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5192-9_0_4_load_51 | 33 | 0.003025 | 0.00075814 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5192-9_0_4_load_26 | 34 | 0.0021275 | 0.00053321 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5192-9_0_4_load_57 | 35 | 0.0089046 | 0.0022317 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5192-9_0_4_load_44 | 36 | 0.0092 | 0.0023057 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5192-9_0_4_load_24 | 37 | 0.0045489 | 0.0011401 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5192-9_0_4_load_25 | 38 | 0.0050422 | 0.0012637 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5192-9_0_4_load_29 | 39 | 0.0079664 | 0.0019966 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5192-9_0_4_load_30 | 40 | 0.0088485 | 0.0022177 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5192-9_0_4_load_31 | 41 | 0.0093795 | 0.0023507 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5192-9_0_4_load_34 | 42 | 0.010104 | 0.0025324 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5192-9_0_4_load_36 | 44 | 0.0097783 | 0.0024507 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5192-9_0_4_load_40 | 47 | 0.0076892 | 0.0019271 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5192-9_0_4_load_39 | 48 | 0.015764 | 0.0039508 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5192-9_0_4_load_55 | 49 | 0.0077402 | 0.0019399 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5192-9_0_4_load_53 | 50 | 0.019835 | 0.0049712 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5192-9_0_4_load_54 | 51 | 0.010293 | 0.0025797 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5192-9_0_4_load_45 | 52 | 0.0071244 | 0.0017856 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5192-9_0_4_load_47 | 53 | 0.0080988 | 0.0020297 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5192-9_0_4_load_50 | 54 | 0.01644 | 0.0041203 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5192-9_0_4_line_0 |  | 0 | 1 | 0.022579 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5192-9_0_4_line_1 |  | 0 | 2 | 0.029938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5192-9_0_4_line_2 |  | 2 | 3 | 0.005738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5192-9_0_4_line_3 |  | 3 | 4 | 0.011239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5192-9_0_4_line_4 |  | 4 | 5 | 0.024985 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5192-9_0_4_line_5 |  | 5 | 51 | 0.012395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5192-9_0_4_line_6 |  | 5 | 43 | 0.013164 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5192-9_0_4_line_7 |  | 6 | 7 | 0.03464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_5192-9_0_4_line_8 |  | 6 | 8 | 0.038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5192-9_0_4_line_9 |  | 7 | 9 | 0.027866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_5192-9_0_4_line_10 |  | 9 | 10 | 0.025 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
11 | LV_5192-9_0_4_line_11 |  | 9 | 11 | 0.038626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
12 | LV_5192-9_0_4_line_12 |  | 10 | 12 | 0.055659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_5192-9_0_4_line_13 |  | 11 | 13 | 0.0085203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5192-9_0_4_line_14 |  | 12 | 33 | 0.011501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5192-9_0_4_line_15 |  | 12 | 31 | 0.06123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5192-9_0_4_line_16 |  | 13 | 42 | 0.012411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5192-9_0_4_line_17 |  | 13 | 41 | 0.017424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5192-9_0_4_line_18 |  | 14 | 15 | 0.023761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5192-9_0_4_line_19 |  | 15 | 16 | 0.017047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5192-9_0_4_line_20 |  | 16 | 17 | 0.015338 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5192-9_0_4_line_21 |  | 17 | 18 | 0.024543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5192-9_0_4_line_22 |  | 18 | 22 | 0.027583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5192-9_0_4_line_23 |  | 19 | 20 | 0.043675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5192-9_0_4_line_24 |  | 19 | 21 | 0.010777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5192-9_0_4_line_25 |  | 20 | 35 | 0.022924 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5192-9_0_4_line_26 |  | 21 | 36 | 0.0043852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5192-9_0_4_line_27 |  | 22 | 23 | 0.012414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5192-9_0_4_line_28 |  | 23 | 24 | 0.013361 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5192-9_0_4_line_29 |  | 24 | 25 | 0.024847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5192-9_0_4_line_30 |  | 24 | 26 | 0.067153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5192-9_0_4_line_31 |  | 26 | 31 | 0.037248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5192-9_0_4_line_32 |  | 27 | 28 | 0.025663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5192-9_0_4_line_33 |  | 28 | 29 | 0.04172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5192-9_0_4_line_34 |  | 28 | 30 | 0.0054921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5192-9_0_4_line_35 |  | 29 | 38 | 0.020173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5192-9_0_4_line_36 |  | 30 | 53 | 0.0056863 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5192-9_0_4_line_37 |  | 31 | 32 | 0.027068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5192-9_0_4_line_38 |  | 32 | 34 | 0.017923 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5192-9_0_4_line_39 |  | 33 | 54 | 0.054753 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5192-9_0_4_line_40 |  | 34 | 37 | 0.014542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5192-9_0_4_line_41 |  | 36 | 52 | 0.026451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5192-9_0_4_line_42 |  | 37 | 38 | 0.0037626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5192-9_0_4_line_43 |  | 39 | 40 | 0.023296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5192-9_0_4_line_44 |  | 40 | 41 | 0.020798 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5192-9_0_4_line_45 |  | 42 | 43 | 0.023121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5192-9_0_4_line_46 |  | 44 | 45 | 0.031522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5192-9_0_4_line_47 |  | 45 | 46 | 0.024191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5192-9_0_4_line_48 |  | 46 | 47 | 0.0035147 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5192-9_0_4_line_49 |  | 46 | 48 | 0.019271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5192-9_0_4_line_50 |  | 47 | 49 | 0.024461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5192-9_0_4_line_51 |  | 49 | 50 | 0.0097828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5192-9_0_4_line_52 |  | 50 | 51 | 0.020782 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5192-9_0_4_line_53 |  | 52 | 53 | 0.021626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5192-9_0_4_trafo_5 | 0.63 MVA 20/0.4 kV | 55 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6
0 | 2718558.8304 | 1097996.7246 | 2718555.4073 | 1097984.769 | 2718548.2817 | 1097977.5497
1 | 2718558.8304 | 1097996.7246 | 2718567.0713 | 1098025.5064
2 | 2718568.6508 | 1098031.0227 | 2718567.0713 | 1098025.5064
3 | 2718571.7443 | 1098041.8272 | 2718568.6508 | 1098031.0227
4 | 2718596.5634 | 1098045.2805 | 2718571.7443 | 1098041.8272
5 | 2718596.5634 | 1098045.2805 | 2718597.8328 | 1098032.9508
6 | 2718596.5634 | 1098045.2805 | 2718609.3827 | 1098048.4328
7 | 2718667.0258 | 1098019.7543 | 2718665.1171 | 1098029.9413 | 2718662.9705 | 1098038.7165 | 2718663.6372 | 1098047.0131 | 2718669.3992 | 1098050.8418
8 | 2718674.0239 | 1097982.4045 | 2718667.0258 | 1098019.7543
9 | 2718689.0049 | 1098067.1779 | 2718688.3018 | 1098060.7486 | 2718684.4017 | 1098058.1818 | 2718679.4639 | 1098055.6058 | 2718671.0159 | 1098051.9161 | 2718669.3992 | 1098050.8418
10 | 2718689.0049 | 1098067.1779 | 2718692.7034 | 1098084.4176 | 2718691.4831 | 1098091.6839
11 | 2718689.0049 | 1098067.1779 | 2718681.6268 | 1098061.8524 | 2718669.4264 | 1098059.1345 | 2718652.8879 | 1098055.0839
12 | 2718697.3831 | 1098146.174 | 2718693.1307 | 1098136.273 | 2718692.4144 | 1098126.9525 | 2718689.8371 | 1098101.4846 | 2718691.4831 | 1098091.6839
13 | 2718644.6122 | 1098053.057 | 2718652.8879 | 1098055.0839
14 | 2718697.3831 | 1098146.174 | 2718699.3745 | 1098134.847
15 | 2718697.3831 | 1098146.174 | 2718711.8952 | 1098170.0962 | 2718743.8903 | 1098161.0483
16 | 2718644.6122 | 1098053.057 | 2718632.3068 | 1098051.4418
17 | 2718644.6122 | 1098053.057 | 2718642.8821 | 1098044.8731 | 2718643.6372 | 1098035.8453
18 | 2718839.1825 | 1097971.5567 | 2718835.8109 | 1097977.0841 | 2718831.7849 | 1097993.8952
19 | 2718827.8147 | 1098010.4732 | 2718831.7849 | 1097993.8952
20 | 2718827.8147 | 1098010.4732 | 2718824.2417 | 1098025.3895
21 | 2718824.2417 | 1098025.3895 | 2718818.5245 | 1098049.257
22 | 2718818.5245 | 1098049.257 | 2718818.4356 | 1098049.628 | 2718818.0338 | 1098070.1677 | 2718819.5263 | 1098076.6561
23 | 2718769.1116 | 1097964.8719 | 2718747.1505 | 1097961.0179 | 2718738.0946 | 1097970.9813 | 2718730.1824 | 1097971.1824
24 | 2718769.1116 | 1097964.8719 | 2718766.9471 | 1097975.4298
25 | 2718711.9132 | 1097977.7745 | 2718712.6872 | 1097974.6319 | 2718714.1157 | 1097971.6911 | 2718717.1652 | 1097970.6166 | 2718723.5155 | 1097969.8846 | 2718730.1824 | 1097971.1824
26 | 2718766.9471 | 1097975.4298 | 2718766.0663 | 1097979.7257
27 | 2718827.5842 | 1098084.809 | 2718820.4823 | 1098080.8119 | 2718819.5263 | 1098076.6561
28 | 2718821.4876 | 1098096.3311 | 2718822.8221 | 1098090.6755 | 2718827.5842 | 1098084.809
29 | 2718821.4876 | 1098096.3311 | 2718811.5954 | 1098106.6894 | 2718805.3898 | 1098112.3053 | 2718803.7543 | 1098113.7085
30 | 2718821.4876 | 1098096.3311 | 2718820.6429 | 1098099.9171 | 2718815.134 | 1098108.3264 | 2718794.2183 | 1098125.1069 | 2718783.8803 | 1098134.1 | 2718779.8435 | 1098141.3038 | 2718775.4931 | 1098143.1534
31 | 2718743.8903 | 1098161.0483 | 2718762.0179 | 1098155.7322 | 2718775.4931 | 1098143.1534
32 | 2718757.0837 | 1098037.9785 | 2718782.0639 | 1098043.8576
33 | 2718757.0837 | 1098037.9785 | 2718757.2597 | 1098039.0028 | 2718755.8779 | 1098048.2711 | 2718750.2586 | 1098079.0726
34 | 2718756.154 | 1098032.5656 | 2718757.0837 | 1098037.9785
35 | 2718750.2586 | 1098079.0726 | 2718746.6381 | 1098098.9176
36 | 2718756.154 | 1098032.5656 | 2718757.1576 | 1098026.9686
37 | 2718743.8903 | 1098161.0483 | 2718739.2388 | 1098139.4758 | 2718740.1361 | 1098134.5573
38 | 2718743.3528 | 1098116.9254 | 2718740.1361 | 1098134.5573
39 | 2718721.8103 | 1098085.6904 | 2718711.1392 | 1098100.9892 | 2718703.5661 | 1098116.3408 | 2718700.1455 | 1098130.4615 | 2718699.3745 | 1098134.847
40 | 2718743.3528 | 1098116.9254 | 2718745.9628 | 1098102.6191
41 | 2718761.0352 | 1098005.6935 | 2718765.4812 | 1097982.5799 | 2718766.0663 | 1097979.7257
42 | 2718746.6381 | 1098098.9176 | 2718745.9628 | 1098102.6191
43 | 2718649.4612 | 1097992.1497 | 2718646.1404 | 1098015.2077
44 | 2718646.1404 | 1098015.2077 | 2718644.2869 | 1098028.0778 | 2718643.6372 | 1098035.8453
45 | 2718609.3827 | 1098048.4328 | 2718632.3068 | 1098051.4418
46 | 2718606.3116 | 1097950.6608 | 2718623.9873 | 1097952.6404 | 2718626.6736 | 1097953.1154 | 2718628.0084 | 1097954.1755 | 2718627.7589 | 1097956.2388 | 2718626.9257 | 1097963.4153
47 | 2718606.3116 | 1097950.6608 | 2718603.828 | 1097974.7178
48 | 2718603.828 | 1097974.7178 | 2718603.468 | 1097978.214
49 | 2718603.828 | 1097974.7178 | 2718622.8536 | 1097977.7863
50 | 2718603.468 | 1097978.214 | 2718600.9629 | 1098002.5468
51 | 2718599.9611 | 1098012.2781 | 2718600.9629 | 1098002.5468
52 | 2718599.9611 | 1098012.2781 | 2718597.8328 | 1098032.9508
53 | 2718761.0352 | 1098005.6935 | 2718760.1096 | 1098010.5054 | 2718757.1576 | 1098026.9686

## bus_geodata
| x | y | coords
0 | 2718558.8304 | 1097996.7246
1 | 2718548.2817 | 1097977.5497
2 | 2718567.0713 | 1098025.5064
3 | 2718568.6508 | 1098031.0227
4 | 2718571.7443 | 1098041.8272
5 | 2718596.5634 | 1098045.2805
6 | 2718667.0258 | 1098019.7543
7 | 2718669.3992 | 1098050.8418
8 | 2718674.0239 | 1097982.4045
9 | 2718689.0049 | 1098067.1779
10 | 2718691.4831 | 1098091.6839
11 | 2718652.8879 | 1098055.0839
12 | 2718697.3831 | 1098146.174
13 | 2718644.6122 | 1098053.057
14 | 2718839.1825 | 1097971.5567
15 | 2718831.7849 | 1097993.8952
16 | 2718827.8147 | 1098010.4732
17 | 2718824.2417 | 1098025.3895
18 | 2718818.5245 | 1098049.257
19 | 2718769.1116 | 1097964.8719
20 | 2718730.1824 | 1097971.1824
21 | 2718766.947 | 1097975.4298
22 | 2718819.5263 | 1098076.6561
23 | 2718827.5842 | 1098084.809
24 | 2718821.4876 | 1098096.3311
25 | 2718803.7543 | 1098113.7085
26 | 2718775.4931 | 1098143.1534
27 | 2718782.0639 | 1098043.8576
28 | 2718757.0837 | 1098037.9785
29 | 2718750.2586 | 1098079.0726
30 | 2718756.154 | 1098032.5656
31 | 2718743.8903 | 1098161.0483
32 | 2718740.1361 | 1098134.5573
33 | 2718699.3745 | 1098134.847
34 | 2718743.3528 | 1098116.9254
35 | 2718711.9132 | 1097977.7745
36 | 2718766.0663 | 1097979.7257
37 | 2718745.9628 | 1098102.6191
38 | 2718746.6381 | 1098098.9176
39 | 2718649.4612 | 1097992.1497
40 | 2718646.1404 | 1098015.2077
41 | 2718643.6372 | 1098035.8453
42 | 2718632.3068 | 1098051.4418
43 | 2718609.3827 | 1098048.4328
44 | 2718626.9257 | 1097963.4153
45 | 2718606.3116 | 1097950.6608
46 | 2718603.828 | 1097974.7178
47 | 2718603.468 | 1097978.214
48 | 2718622.8536 | 1097977.7863
49 | 2718600.9629 | 1098002.5468
50 | 2718599.9611 | 1098012.2781
51 | 2718597.8328 | 1098032.9508
52 | 2718761.0352 | 1098005.6935
53 | 2718757.1576 | 1098026.9686
54 | 2718721.8103 | 1098085.6904
55 | 2718674.0239 | 1097982.4045

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1