## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5216-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5216-6_0_5_node_30 | 0.4 | n |  | TRUE
2 | bus_LV_5216-6_0_5_node_20 | 0.4 | n |  | TRUE
3 | bus_LV_5216-6_0_5_node_31 | 0.4 | n |  | TRUE
4 | bus_LV_5216-6_0_5_node_28 | 0.4 | n |  | TRUE
5 | bus_LV_5216-6_0_5_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_5216-6_0_5_node_2 | 0.4 | n |  | TRUE
7 | bus_LV_5216-6_0_5_node_1 | 0.4 | n |  | TRUE
8 | bus_LV_5216-6_0_5_node_32 | 0.4 | n |  | TRUE
9 | bus_LV_5216-6_0_5_node_33 | 0.4 | n |  | TRUE
10 | bus_LV_5216-6_0_5_node_3 | 0.4 | n |  | TRUE
11 | bus_LV_5216-6_0_5_node_5 | 0.4 | n |  | TRUE
12 | bus_LV_5216-6_0_5_node_4 | 0.4 | n |  | TRUE
13 | bus_LV_5216-6_0_5_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_5216-6_0_5_node_7 | 0.4 | n |  | TRUE
15 | bus_LV_5216-6_0_5_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_5216-6_0_5_node_9 | 0.4 | n |  | TRUE
17 | bus_LV_5216-6_0_5_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_5216-6_0_5_node_16 | 0.4 | n |  | TRUE
19 | bus_LV_5216-6_0_5_node_91 | 0.4 | n |  | TRUE
20 | bus_LV_5216-6_0_5_node_17 | 0.4 | n |  | TRUE
21 | bus_LV_5216-6_0_5_node_85 | 0.4 | n |  | TRUE
22 | bus_LV_5216-6_0_5_node_11 | 0.4 | n |  | TRUE
23 | bus_LV_5216-6_0_5_node_12 | 0.4 | n |  | TRUE
24 | bus_LV_5216-6_0_5_node_13 | 0.4 | n |  | TRUE
25 | bus_LV_5216-6_0_5_node_14 | 0.4 | n |  | TRUE
26 | bus_LV_5216-6_0_5_node_15 | 0.4 | n |  | TRUE
27 | bus_LV_5216-6_0_5_node_117 | 0.4 | n |  | TRUE
28 | bus_LV_5216-6_0_5_node_128 | 0.4 | n |  | TRUE
29 | bus_LV_5216-6_0_5_node_116 | 0.4 | n |  | TRUE
30 | bus_LV_5216-6_0_5_node_18 | 0.4 | n |  | TRUE
31 | bus_LV_5216-6_0_5_node_144 | 0.4 | n |  | TRUE
32 | bus_LV_5216-6_0_5_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_5216-6_0_5_node_22 | 0.4 | n |  | TRUE
34 | bus_LV_5216-6_0_5_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_5216-6_0_5_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_5216-6_0_5_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_5216-6_0_5_node_26 | 0.4 | n |  | TRUE
38 | bus_LV_5216-6_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_5216-6_0_5_node_131 | 0.4 | n |  | TRUE
40 | bus_LV_5216-6_0_5_node_29 | 0.4 | n |  | TRUE
41 | bus_LV_5216-6_0_5_node_129 | 0.4 | n |  | TRUE
42 | bus_LV_5216-6_0_5_node_36 | 0.4 | n |  | TRUE
43 | bus_LV_5216-6_0_5_node_34 | 0.4 | n |  | TRUE
44 | bus_LV_5216-6_0_5_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_5216-6_0_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_5216-6_0_5_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_5216-6_0_5_node_39 | 0.4 | n |  | TRUE
48 | bus_LV_5216-6_0_5_node_40 | 0.4 | n |  | TRUE
49 | bus_LV_5216-6_0_5_node_41 | 0.4 | n |  | TRUE
50 | bus_LV_5216-6_0_5_node_42 | 0.4 | n |  | TRUE
51 | bus_LV_5216-6_0_5_node_43 | 0.4 | n |  | TRUE
52 | bus_LV_5216-6_0_5_node_55 | 0.4 | n |  | TRUE
53 | bus_LV_5216-6_0_5_node_54 | 0.4 | n |  | TRUE
54 | bus_LV_5216-6_0_5_node_44 | 0.4 | n |  | TRUE
55 | bus_LV_5216-6_0_5_node_56 | 0.4 | n |  | TRUE
56 | bus_LV_5216-6_0_5_node_45 | 0.4 | n |  | TRUE
57 | bus_LV_5216-6_0_5_node_60 | 0.4 | n |  | TRUE
58 | bus_LV_5216-6_0_5_node_57 | 0.4 | n |  | TRUE
59 | bus_LV_5216-6_0_5_node_46 | 0.4 | n |  | TRUE
60 | bus_LV_5216-6_0_5_node_47 | 0.4 | n |  | TRUE
61 | bus_LV_5216-6_0_5_node_48 | 0.4 | n |  | TRUE
62 | bus_LV_5216-6_0_5_node_53 | 0.4 | n |  | TRUE
63 | bus_LV_5216-6_0_5_node_50 | 0.4 | n |  | TRUE
64 | bus_LV_5216-6_0_5_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_5216-6_0_5_node_51 | 0.4 | n |  | TRUE
66 | bus_LV_5216-6_0_5_node_52 | 0.4 | n |  | TRUE
67 | bus_LV_5216-6_0_5_node_97 | 0.4 | n |  | TRUE
68 | bus_LV_5216-6_0_5_node_58 | 0.4 | n |  | TRUE
69 | bus_LV_5216-6_0_5_node_59 | 0.4 | n |  | TRUE
70 | bus_LV_5216-6_0_5_node_61 | 0.4 | n |  | TRUE
71 | bus_LV_5216-6_0_5_node_62 | 0.4 | n |  | TRUE
72 | bus_LV_5216-6_0_5_node_98 | 0.4 | n |  | TRUE
73 | bus_LV_5216-6_0_5_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_5216-6_0_5_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_5216-6_0_5_node_65 | 0.4 | n |  | TRUE
76 | bus_LV_5216-6_0_5_node_66 | 0.4 | n |  | TRUE
77 | bus_LV_5216-6_0_5_node_67 | 0.4 | n |  | TRUE
78 | bus_LV_5216-6_0_5_node_68 | 0.4 | n |  | TRUE
79 | bus_LV_5216-6_0_5_node_69 | 0.4 | n |  | TRUE
80 | bus_LV_5216-6_0_5_node_70 | 0.4 | n |  | TRUE
81 | bus_LV_5216-6_0_5_node_71 | 0.4 | n |  | TRUE
82 | bus_LV_5216-6_0_5_node_72 | 0.4 | n |  | TRUE
83 | bus_LV_5216-6_0_5_node_88 | 0.4 | n |  | TRUE
84 | bus_LV_5216-6_0_5_node_99 | 0.4 | n |  | TRUE
85 | bus_LV_5216-6_0_5_node_94 | 0.4 | n |  | TRUE
86 | bus_LV_5216-6_0_5_node_84 | 0.4 | n |  | TRUE
87 | bus_LV_5216-6_0_5_node_73 | 0.4 | n |  | TRUE
88 | bus_LV_5216-6_0_5_node_74 | 0.4 | n |  | TRUE
89 | bus_LV_5216-6_0_5_node_75 | 0.4 | n |  | TRUE
90 | bus_LV_5216-6_0_5_node_76 | 0.4 | n |  | TRUE
91 | bus_LV_5216-6_0_5_node_77 | 0.4 | n |  | TRUE
92 | bus_LV_5216-6_0_5_node_78 | 0.4 | n |  | TRUE
93 | bus_LV_5216-6_0_5_node_79 | 0.4 | n |  | TRUE
94 | bus_LV_5216-6_0_5_node_82 | 0.4 | n |  | TRUE
95 | bus_LV_5216-6_0_5_node_80 | 0.4 | n |  | TRUE
96 | bus_LV_5216-6_0_5_node_81 | 0.4 | n |  | TRUE
97 | bus_LV_5216-6_0_5_node_83 | 0.4 | n |  | TRUE
98 | bus_LV_5216-6_0_5_node_86 | 0.4 | n |  | TRUE
99 | bus_LV_5216-6_0_5_node_87 | 0.4 | n |  | TRUE
100 | bus_LV_5216-6_0_5_node_89 | 0.4 | n |  | TRUE
101 | bus_LV_5216-6_0_5_node_90 | 0.4 | n |  | TRUE
102 | bus_LV_5216-6_0_5_node_92 | 0.4 | n |  | TRUE
103 | bus_LV_5216-6_0_5_node_93 | 0.4 | n |  | TRUE
104 | bus_LV_5216-6_0_5_node_95 | 0.4 | n |  | TRUE
105 | bus_LV_5216-6_0_5_node_96 | 0.4 | n |  | TRUE
106 | bus_LV_5216-6_0_5_node_125 | 0.4 | n |  | TRUE
107 | bus_LV_5216-6_0_5_node_126 | 0.4 | n |  | TRUE
108 | bus_LV_5216-6_0_5_node_100 | 0.4 | n |  | TRUE
109 | bus_LV_5216-6_0_5_node_101 | 0.4 | n |  | TRUE
110 | bus_LV_5216-6_0_5_node_108 | 0.4 | n |  | TRUE
111 | bus_LV_5216-6_0_5_node_107 | 0.4 | n |  | TRUE
112 | bus_LV_5216-6_0_5_node_102 | 0.4 | n |  | TRUE
113 | bus_LV_5216-6_0_5_node_103 | 0.4 | n |  | TRUE
114 | bus_LV_5216-6_0_5_node_104 | 0.4 | n |  | TRUE
115 | bus_LV_5216-6_0_5_node_105 | 0.4 | n |  | TRUE
116 | bus_LV_5216-6_0_5_node_106 | 0.4 | n |  | TRUE
117 | bus_LV_5216-6_0_5_node_111 | 0.4 | n |  | TRUE
118 | bus_LV_5216-6_0_5_node_113 | 0.4 | n |  | TRUE
119 | bus_LV_5216-6_0_5_node_109 | 0.4 | n |  | TRUE
120 | bus_LV_5216-6_0_5_node_112 | 0.4 | n |  | TRUE
121 | bus_LV_5216-6_0_5_node_127 | 0.4 | n |  | TRUE
122 | bus_LV_5216-6_0_5_node_110 | 0.4 | n |  | TRUE
123 | bus_LV_5216-6_0_5_node_122 | 0.4 | n |  | TRUE
124 | bus_LV_5216-6_0_5_node_121 | 0.4 | n |  | TRUE
125 | bus_LV_5216-6_0_5_node_114 | 0.4 | n |  | TRUE
126 | bus_LV_5216-6_0_5_node_115 | 0.4 | n |  | TRUE
127 | bus_LV_5216-6_0_5_node_118 | 0.4 | n |  | TRUE
128 | bus_LV_5216-6_0_5_node_119 | 0.4 | n |  | TRUE
129 | bus_LV_5216-6_0_5_node_120 | 0.4 | n |  | TRUE
130 | bus_LV_5216-6_0_5_node_123 | 0.4 | n |  | TRUE
131 | bus_LV_5216-6_0_5_node_124 | 0.4 | n |  | TRUE
132 | bus_LV_5216-6_0_5_node_130 | 0.4 | n |  | TRUE
133 | bus_LV_5216-6_0_5_node_132 | 0.4 | n |  | TRUE
134 | bus_LV_5216-6_0_5_node_133 | 0.4 | n |  | TRUE
135 | bus_LV_5216-6_0_5_node_134 | 0.4 | n |  | TRUE
136 | bus_LV_5216-6_0_5_node_135 | 0.4 | n |  | TRUE
137 | bus_LV_5216-6_0_5_node_136 | 0.4 | n |  | TRUE
138 | bus_LV_5216-6_0_5_node_137 | 0.4 | n |  | TRUE
139 | bus_LV_5216-6_0_5_node_138 | 0.4 | n |  | TRUE
140 | bus_LV_5216-6_0_5_node_139 | 0.4 | n |  | TRUE
141 | bus_LV_5216-6_0_5_node_140 | 0.4 | n |  | TRUE
142 | bus_LV_5216-6_0_5_node_141 | 0.4 | n |  | TRUE
143 | bus_LV_5216-6_0_5_node_142 | 0.4 | n |  | TRUE
144 | bus_LV_5216-6_0_5_node_143 | 0.4 | n |  | TRUE
145 | bus_MV_246_0_node_76 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5216-6_0_5_load_0 | 0 | 0.0043641 | 0.0010937 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5216-6_0_5_load_30 | 1 | 0.0053895 | 0.0013507 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5216-6_0_5_load_20 | 2 | 0.0089931 | 0.0022539 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5216-6_0_5_load_31 | 3 | 0.0014715 | 0.00036879 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5216-6_0_5_load_28 | 4 | 0.0027187 | 0.00068136 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5216-6_0_5_load_19 | 5 | 0.0037766 | 0.00094651 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5216-6_0_5_load_1 | 7 | 0.0020825 | 0.00052193 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5216-6_0_5_load_32 | 8 | 0.0019584 | 0.00049081 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5216-6_0_5_load_33 | 9 | 0.0015572 | 0.00039028 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5216-6_0_5_load_3 | 10 | 0.0043249 | 0.0010839 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5216-6_0_5_load_5 | 11 | 0.0043439 | 0.0010887 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5216-6_0_5_load_4 | 12 | 0.0025614 | 0.00064194 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5216-6_0_5_load_6 | 13 | 0.0053699 | 0.0013458 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5216-6_0_5_load_7 | 14 | 0.0032147 | 0.00080568 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5216-6_0_5_load_8 | 15 | 0.0043366 | 0.0010869 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5216-6_0_5_load_9 | 16 | 0.0023798 | 0.00059645 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5216-6_0_5_load_10 | 17 | 0.0044636 | 0.0011187 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5216-6_0_5_load_16 | 18 | 0.0023759 | 0.00059545 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5216-6_0_5_load_91 | 19 | 0.0015857 | 0.00039743 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5216-6_0_5_load_85 | 21 | 0.0069466 | 0.001741 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5216-6_0_5_load_11 | 22 | 0.0053511 | 0.0013411 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5216-6_0_5_load_12 | 23 | 0.0038869 | 0.00097416 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5216-6_0_5_load_13 | 24 | 0.0059407 | 0.0014889 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5216-6_0_5_load_14 | 25 | 0.0029437 | 0.00073775 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5216-6_0_5_load_15 | 26 | 0.022167 | 0.0055557 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5216-6_0_5_load_128 | 28 | 0.0026426 | 0.00066231 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5216-6_0_5_load_144 | 31 | 0.0025585 | 0.00064122 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5216-6_0_5_load_21 | 32 | 0.0062659 | 0.0015704 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5216-6_0_5_load_24 | 35 | 0.0027559 | 0.00069071 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5216-6_0_5_load_25 | 36 | 0.0019806 | 0.00049638 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5216-6_0_5_load_26 | 37 | 0.0039972 | 0.0010018 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5216-6_0_5_load_131 | 39 | 0.0064656 | 0.0016204 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5216-6_0_5_load_29 | 40 | 0.002649 | 0.00066389 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5216-6_0_5_load_129 | 41 | 0.0022291 | 0.00055867 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5216-6_0_5_load_36 | 42 | 0.011288 | 0.0028291 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5216-6_0_5_load_34 | 43 | 0.001942 | 0.00048671 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5216-6_0_5_load_35 | 44 | 0.0018223 | 0.00045672 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5216-6_0_5_load_37 | 45 | 0.0013922 | 0.00034892 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5216-6_0_5_load_38 | 46 | 0.00096546 | 0.00024197 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5216-6_0_5_load_39 | 47 | 0.0042408 | 0.0010628 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5216-6_0_5_load_40 | 48 | 0.0031021 | 0.00077747 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5216-6_0_5_load_42 | 50 | 0.0018128 | 0.00045433 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5216-6_0_5_load_55 | 52 | 0.0031131 | 0.00078023 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5216-6_0_5_load_54 | 53 | 0.0048349 | 0.0012117 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5216-6_0_5_load_44 | 54 | 0.0032077 | 0.00080394 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5216-6_0_5_load_56 | 55 | 0.0043482 | 0.0010898 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5216-6_0_5_load_45 | 56 | 0.0020752 | 0.00052011 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5216-6_0_5_load_60 | 57 | 0.0012695 | 0.00031817 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5216-6_0_5_load_57 | 58 | 0.0027549 | 0.00069045 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5216-6_0_5_load_46 | 59 | 0.0033721 | 0.00084512 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5216-6_0_5_load_47 | 60 | 0.0029768 | 0.00074604 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5216-6_0_5_load_48 | 61 | 0.003394 | 0.00085061 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5216-6_0_5_load_53 | 62 | 0.0040527 | 0.0010157 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5216-6_0_5_load_50 | 63 | 0.0036873 | 0.00092413 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5216-6_0_5_load_49 | 64 | 0.0043758 | 0.0010967 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5216-6_0_5_load_51 | 65 | 0.0056515 | 0.0014164 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5216-6_0_5_load_52 | 66 | 0.003854 | 0.00096591 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5216-6_0_5_load_97 | 67 | 0.0021933 | 0.0005497 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5216-6_0_5_load_58 | 68 | 0.0027986 | 0.0007014 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5216-6_0_5_load_59 | 69 | 0.0014691 | 0.00036819 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5216-6_0_5_load_61 | 70 | 0.001189 | 0.00029799 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5216-6_0_5_load_62 | 71 | 0.001699 | 0.00042581 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5216-6_0_5_load_63 | 73 | 0.0012609 | 0.00031602 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5216-6_0_5_load_64 | 74 | 0.0031224 | 0.00078255 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5216-6_0_5_load_65 | 75 | 0.0029838 | 0.00074782 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5216-6_0_5_load_66 | 76 | 0.0028445 | 0.00071289 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5216-6_0_5_load_67 | 77 | 0.003306 | 0.00082857 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5216-6_0_5_load_68 | 78 | 0.0037619 | 0.00094282 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5216-6_0_5_load_70 | 80 | 0.002995 | 0.00075061 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5216-6_0_5_load_71 | 81 | 0.0023679 | 0.00059344 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5216-6_0_5_load_72 | 82 | 0.0013887 | 0.00034803 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5216-6_0_5_load_99 | 84 | 0.0038943 | 0.000976 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5216-6_0_5_load_94 | 85 | 0.0034067 | 0.0008538 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5216-6_0_5_load_73 | 87 | 0.0028291 | 0.00070904 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_5216-6_0_5_load_74 | 88 | 0.0021547 | 0.00054001 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_5216-6_0_5_load_75 | 89 | 0.0020465 | 0.00051291 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_5216-6_0_5_load_76 | 90 | 0.0020648 | 0.0005175 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_5216-6_0_5_load_77 | 91 | 0.004253 | 0.0010659 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_5216-6_0_5_load_78 | 92 | 0.0017027 | 0.00042675 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_5216-6_0_5_load_79 | 93 | 0.0017225 | 0.00043171 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_5216-6_0_5_load_80 | 95 | 0.0015406 | 0.0003861 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_5216-6_0_5_load_81 | 96 | 0.0015876 | 0.00039788 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_5216-6_0_5_load_83 | 97 | 0.0015444 | 0.00038707 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_5216-6_0_5_load_86 | 98 | 0.0012809 | 0.00032103 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_5216-6_0_5_load_87 | 99 | 0.0037166 | 0.00093147 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_5216-6_0_5_load_89 | 100 | 0.0020665 | 0.00051791 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_5216-6_0_5_load_90 | 101 | 0.01472 | 0.0036893 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_5216-6_0_5_load_92 | 102 | 0.0020782 | 0.00052085 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_5216-6_0_5_load_93 | 103 | 0.0040006 | 0.0010027 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_5216-6_0_5_load_95 | 104 | 0.004425 | 0.001109 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_5216-6_0_5_load_96 | 105 | 0.0042659 | 0.0010691 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_5216-6_0_5_load_125 | 106 | 0.0042983 | 0.0010773 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_5216-6_0_5_load_126 | 107 | 0.003858 | 0.00096691 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_5216-6_0_5_load_100 | 108 | 0.0022257 | 0.00055781 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_5216-6_0_5_load_101 | 109 | 0.0025572 | 0.0006409 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_5216-6_0_5_load_108 | 110 | 0.0036714 | 0.00092013 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_5216-6_0_5_load_107 | 111 | 0.0051796 | 0.0012981 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_5216-6_0_5_load_102 | 112 | 0.0058264 | 0.0014602 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_5216-6_0_5_load_103 | 113 | 0.0028339 | 0.00071025 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_5216-6_0_5_load_104 | 114 | 0.0031281 | 0.00078397 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_5216-6_0_5_load_105 | 115 | 0.0029165 | 0.00073093 | 0 | 0 |  | 1 | TRUE | wye
101 | LV_5216-6_0_5_load_111 | 117 | 0.0031298 | 0.0007844 | 0 | 0 |  | 1 | TRUE | wye
102 | LV_5216-6_0_5_load_113 | 118 | 0.0034398 | 0.00086209 | 0 | 0 |  | 1 | TRUE | wye
103 | LV_5216-6_0_5_load_112 | 120 | 0.0039472 | 0.00098927 | 0 | 0 |  | 1 | TRUE | wye
104 | LV_5216-6_0_5_load_127 | 121 | 0.0026882 | 0.00067372 | 0 | 0 |  | 1 | TRUE | wye
105 | LV_5216-6_0_5_load_110 | 122 | 0.0036672 | 0.00091909 | 0 | 0 |  | 1 | TRUE | wye
106 | LV_5216-6_0_5_load_122 | 123 | 0.0038221 | 0.0009579 | 0 | 0 |  | 1 | TRUE | wye
107 | LV_5216-6_0_5_load_114 | 125 | 0.0041552 | 0.0010414 | 0 | 0 |  | 1 | TRUE | wye
108 | LV_5216-6_0_5_load_115 | 126 | 0.0045814 | 0.0011482 | 0 | 0 |  | 1 | TRUE | wye
109 | LV_5216-6_0_5_load_118 | 127 | 0.0026045 | 0.00065274 | 0 | 0 |  | 1 | TRUE | wye
110 | LV_5216-6_0_5_load_119 | 128 | 0.0038851 | 0.00097369 | 0 | 0 |  | 1 | TRUE | wye
111 | LV_5216-6_0_5_load_120 | 129 | 0.0014708 | 0.00036862 | 0 | 0 |  | 1 | TRUE | wye
112 | LV_5216-6_0_5_load_123 | 130 | 0.0041913 | 0.0010504 | 0 | 0 |  | 1 | TRUE | wye
113 | LV_5216-6_0_5_load_124 | 131 | 0.0038745 | 0.00097105 | 0 | 0 |  | 1 | TRUE | wye
114 | LV_5216-6_0_5_load_130 | 132 | 0.012674 | 0.0031764 | 0 | 0 |  | 1 | TRUE | wye
115 | LV_5216-6_0_5_load_132 | 133 | 0.0072823 | 0.0018251 | 0 | 0 |  | 1 | TRUE | wye
116 | LV_5216-6_0_5_load_133 | 134 | 0.0024561 | 0.00061556 | 0 | 0 |  | 1 | TRUE | wye
117 | LV_5216-6_0_5_load_134 | 135 | 0.0048302 | 0.0012106 | 0 | 0 |  | 1 | TRUE | wye
118 | LV_5216-6_0_5_load_135 | 136 | 0.0021485 | 0.00053845 | 0 | 0 |  | 1 | TRUE | wye
119 | LV_5216-6_0_5_load_136 | 137 | 0.0021575 | 0.00054073 | 0 | 0 |  | 1 | TRUE | wye
120 | LV_5216-6_0_5_load_137 | 138 | 0.0028031 | 0.00070252 | 0 | 0 |  | 1 | TRUE | wye
121 | LV_5216-6_0_5_load_138 | 139 | 0.0022416 | 0.00056179 | 0 | 0 |  | 1 | TRUE | wye
122 | LV_5216-6_0_5_load_139 | 140 | 0.0023766 | 0.00059564 | 0 | 0 |  | 1 | TRUE | wye
123 | LV_5216-6_0_5_load_140 | 141 | 0.0029923 | 0.00074994 | 0 | 0 |  | 1 | TRUE | wye
124 | LV_5216-6_0_5_load_141 | 142 | 0.0026861 | 0.00067321 | 0 | 0 |  | 1 | TRUE | wye
125 | LV_5216-6_0_5_load_142 | 143 | 0.0084587 | 0.0021199 | 0 | 0 |  | 1 | TRUE | wye
126 | LV_5216-6_0_5_load_143 | 144 | 0.00243 | 0.00060901 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5216-6_0_5_line_0 |  | 0 | 1 | 0.070709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5216-6_0_5_line_1 |  | 0 | 2 | 0.1248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5216-6_0_5_line_2 |  | 1 | 3 | 0.012975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
3 | LV_5216-6_0_5_line_3 |  | 1 | 4 | 0.026822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
4 | LV_5216-6_0_5_line_4 |  | 2 | 6 | 0.18516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5216-6_0_5_line_5 |  | 2 | 5 | 0.022094 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5216-6_0_5_line_6 |  | 3 | 8 | 0.01271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
7 | LV_5216-6_0_5_line_7 |  | 4 | 38 | 0.00085587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
8 | LV_5216-6_0_5_line_8 |  | 6 | 10 | 0.0079077 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5216-6_0_5_line_9 |  | 7 | 8 | 0.035441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5216-6_0_5_line_10 |  | 8 | 9 | 0.01628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
11 | LV_5216-6_0_5_line_11 |  | 9 | 43 | 0.02502 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
12 | LV_5216-6_0_5_line_12 |  | 10 | 11 | 0.028429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5216-6_0_5_line_13 |  | 11 | 12 | 0.011575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5216-6_0_5_line_14 |  | 13 | 14 | 0.019895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5216-6_0_5_line_15 |  | 13 | 15 | 0.02141 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5216-6_0_5_line_16 |  | 14 | 16 | 0.0054457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5216-6_0_5_line_17 |  | 15 | 17 | 0.004122 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5216-6_0_5_line_18 |  | 16 | 18 | 0.015461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5216-6_0_5_line_19 |  | 17 | 19 | 0.017936 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5216-6_0_5_line_20 |  | 18 | 20 | 0.036604 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5216-6_0_5_line_21 |  | 19 | 21 | 0.01404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5216-6_0_5_line_22 |  | 20 | 30 | 0.024296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5216-6_0_5_line_23 |  | 21 | 94 | 0.0075951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5216-6_0_5_line_24 |  | 22 | 23 | 0.042691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5216-6_0_5_line_25 |  | 22 | 24 | 0.013068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5216-6_0_5_line_26 |  | 23 | 25 | 0.001833 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5216-6_0_5_line_27 |  | 24 | 26 | 0.00050657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5216-6_0_5_line_28 |  | 25 | 27 | 0.035776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5216-6_0_5_line_29 |  | 27 | 28 | 0.01638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5216-6_0_5_line_30 |  | 27 | 29 | 0.018961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5216-6_0_5_line_31 |  | 28 | 121 | 0.007332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5216-6_0_5_line_32 |  | 29 | 126 | 0.033625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5216-6_0_5_line_33 |  | 30 | 31 | 0.06416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5216-6_0_5_line_34 |  | 32 | 33 | 0.044903 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5216-6_0_5_line_35 |  | 32 | 34 | 0.06018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5216-6_0_5_line_36 |  | 33 | 35 | 0.054052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5216-6_0_5_line_37 |  | 34 | 36 | 0.027642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5216-6_0_5_line_38 |  | 34 | 37 | 0.068573 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5216-6_0_5_line_39 |  | 35 | 38 | 0.025658 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_5216-6_0_5_line_40 |  | 36 | 39 | 0.0054644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5216-6_0_5_line_41 |  | 38 | 40 | 0.036898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5216-6_0_5_line_42 |  | 39 | 41 | 0.06569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5216-6_0_5_line_43 |  | 40 | 42 | 0.019839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5216-6_0_5_line_44 |  | 41 | 132 | 0.021038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5216-6_0_5_line_45 |  | 43 | 44 | 0.0040259 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
46 | LV_5216-6_0_5_line_46 |  | 44 | 45 | 0.021762 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
47 | LV_5216-6_0_5_line_47 |  | 45 | 46 | 0.0084047 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
48 | LV_5216-6_0_5_line_48 |  | 46 | 47 | 0.020324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
49 | LV_5216-6_0_5_line_49 |  | 47 | 48 | 0.0087139 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
50 | LV_5216-6_0_5_line_50 |  | 48 | 49 | 0.011276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
51 | LV_5216-6_0_5_line_51 |  | 49 | 50 | 0.0090512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
52 | LV_5216-6_0_5_line_52 |  | 49 | 51 | 0.016819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
53 | LV_5216-6_0_5_line_53 |  | 50 | 54 | 0.00039722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
54 | LV_5216-6_0_5_line_54 |  | 51 | 55 | 0.025118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
55 | LV_5216-6_0_5_line_55 |  | 52 | 53 | 0.013404 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5216-6_0_5_line_56 |  | 53 | 62 | 0.020723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5216-6_0_5_line_57 |  | 54 | 56 | 0.00054163 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
58 | LV_5216-6_0_5_line_58 |  | 55 | 57 | 0.0017864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
59 | LV_5216-6_0_5_line_59 |  | 55 | 58 | 0.02175 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5216-6_0_5_line_60 |  | 56 | 59 | 0.01803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
61 | LV_5216-6_0_5_line_61 |  | 57 | 67 | 0.017557 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 4 | cs | TRUE
62 | LV_5216-6_0_5_line_62 |  | 58 | 68 | 0.010272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5216-6_0_5_line_63 |  | 59 | 60 | 0.010997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5216-6_0_5_line_64 |  | 60 | 61 | 0.011495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5216-6_0_5_line_65 |  | 61 | 63 | 0.053583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5216-6_0_5_line_66 |  | 62 | 66 | 0.0080204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5216-6_0_5_line_67 |  | 63 | 66 | 0.016467 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5216-6_0_5_line_68 |  | 63 | 64 | 0.011172 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5216-6_0_5_line_69 |  | 64 | 65 | 0.006895 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5216-6_0_5_line_70 |  | 67 | 72 | 0.016157 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
71 | LV_5216-6_0_5_line_71 |  | 68 | 69 | 0.0086248 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5216-6_0_5_line_72 |  | 69 | 70 | 0.0081308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5216-6_0_5_line_73 |  | 70 | 71 | 0.007074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5216-6_0_5_line_74 |  | 71 | 73 | 0.0075558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5216-6_0_5_line_75 |  | 72 | 84 | 0.025405 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5216-6_0_5_line_76 |  | 72 | 81 | 0.016324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5216-6_0_5_line_77 |  | 73 | 74 | 0.016884 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5216-6_0_5_line_78 |  | 74 | 75 | 0.01027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5216-6_0_5_line_79 |  | 75 | 76 | 0.01072 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5216-6_0_5_line_80 |  | 77 | 78 | 0.039612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5216-6_0_5_line_81 |  | 77 | 79 | 0.03324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5216-6_0_5_line_82 |  | 78 | 80 | 0.013313 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5216-6_0_5_line_83 |  | 79 | 81 | 0.0089838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5216-6_0_5_line_84 |  | 79 | 82 | 0.01059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_5216-6_0_5_line_85 |  | 82 | 83 | 0.025365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_5216-6_0_5_line_86 |  | 83 | 85 | 0.015351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_5216-6_0_5_line_87 |  | 83 | 86 | 0.01251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_5216-6_0_5_line_88 |  | 84 | 108 | 0.0050945 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_5216-6_0_5_line_89 |  | 85 | 102 | 0.013775 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_5216-6_0_5_line_90 |  | 86 | 94 | 0.022011 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_5216-6_0_5_line_91 |  | 86 | 93 | 0.049402 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_5216-6_0_5_line_92 |  | 87 | 88 | 0.012882 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_5216-6_0_5_line_93 |  | 87 | 89 | 0.0071038 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_5216-6_0_5_line_94 |  | 88 | 90 | 0.019907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_5216-6_0_5_line_95 |  | 90 | 91 | 0.012359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_5216-6_0_5_line_96 |  | 91 | 92 | 0.0072414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_5216-6_0_5_line_97 |  | 92 | 93 | 0.015451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_5216-6_0_5_line_98 |  | 94 | 95 | 0.029236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
99 | LV_5216-6_0_5_line_99 |  | 95 | 96 | 0.017368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_5216-6_0_5_line_100 |  | 96 | 97 | 0.001757 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
101 | LV_5216-6_0_5_line_101 |  | 97 | 98 | 0.0079301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_5216-6_0_5_line_102 |  | 98 | 99 | 0.038965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_5216-6_0_5_line_103 |  | 99 | 100 | 0.0067951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_5216-6_0_5_line_104 |  | 100 | 101 | 0.0093616 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_5216-6_0_5_line_105 |  | 102 | 103 | 0.0222 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_5216-6_0_5_line_106 |  | 103 | 104 | 0.014333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_5216-6_0_5_line_107 |  | 104 | 105 | 0.0097468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_5216-6_0_5_line_108 |  | 105 | 106 | 0.023907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_5216-6_0_5_line_109 |  | 106 | 107 | 0.0019064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_5216-6_0_5_line_110 |  | 108 | 109 | 0.01468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
111 | LV_5216-6_0_5_line_111 |  | 109 | 110 | 0.015044 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_5216-6_0_5_line_112 |  | 110 | 111 | 0.014409 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_5216-6_0_5_line_113 |  | 111 | 119 | 0.010166 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_5216-6_0_5_line_114 |  | 112 | 113 | 0.0053115 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_5216-6_0_5_line_115 |  | 112 | 114 | 0.0071709 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_5216-6_0_5_line_116 |  | 113 | 115 | 0.007399 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_5216-6_0_5_line_117 |  | 114 | 116 | 0.014529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_5216-6_0_5_line_118 |  | 115 | 117 | 0.0087623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_5216-6_0_5_line_119 |  | 116 | 118 | 0.011437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_5216-6_0_5_line_120 |  | 116 | 119 | 0.007914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_5216-6_0_5_line_121 |  | 117 | 120 | 0.010987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_5216-6_0_5_line_122 |  | 118 | 121 | 0.017004 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_5216-6_0_5_line_123 |  | 119 | 122 | 0.010585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_5216-6_0_5_line_124 |  | 120 | 125 | 0.0065411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_5216-6_0_5_line_125 |  | 122 | 123 | 0.00155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_5216-6_0_5_line_126 |  | 123 | 124 | 0.012058 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_5216-6_0_5_line_127 |  | 124 | 130 | 0.0059061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_5216-6_0_5_line_128 |  | 124 | 128 | 0.024888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_5216-6_0_5_line_129 |  | 127 | 128 | 0.015293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_5216-6_0_5_line_130 |  | 127 | 129 | 0.0045398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_5216-6_0_5_line_131 |  | 130 | 131 | 0.0060335 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
132 | LV_5216-6_0_5_line_132 |  | 132 | 133 | 0.001644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
133 | LV_5216-6_0_5_line_133 |  | 133 | 134 | 0.02698 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
134 | LV_5216-6_0_5_line_134 |  | 134 | 135 | 0.0012564 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
135 | LV_5216-6_0_5_line_135 |  | 135 | 136 | 0.0061392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
136 | LV_5216-6_0_5_line_136 |  | 136 | 137 | 0.0068853 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
137 | LV_5216-6_0_5_line_137 |  | 137 | 138 | 0.0036452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
138 | LV_5216-6_0_5_line_138 |  | 138 | 139 | 0.0033714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
139 | LV_5216-6_0_5_line_139 |  | 139 | 140 | 0.0072703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
140 | LV_5216-6_0_5_line_140 |  | 140 | 141 | 0.0064548 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
141 | LV_5216-6_0_5_line_141 |  | 141 | 142 | 0.015666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
142 | LV_5216-6_0_5_line_142 |  | 142 | 143 | 0.0041582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
143 | LV_5216-6_0_5_line_143 |  | 143 | 144 | 0.0055392 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5216-6_0_5_trafo_46 | 0.63 MVA 20/0.4 kV | 145 | 59 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8
0 | 2710654.6988 | 1094093.1595 | 2710668.712 | 1094162.4658
1 | 2710668.712 | 1094162.4658 | 2710570.3172 | 1094239.2303
2 | 2710666.8702 | 1094088.6656 | 2710654.6988 | 1094093.1595
3 | 2710628.9216 | 1094095.9256 | 2710641.5065 | 1094098.0302 | 2710654.6988 | 1094093.1595
4 | 2710570.3172 | 1094239.2303 | 2710577.8088 | 1094424.235
5 | 2710570.3172 | 1094239.2303 | 2710557.2889 | 1094221.3859
6 | 2710666.8702 | 1094088.6656 | 2710670.7509 | 1094087.2328 | 2710677.6257 | 1094082.1101
7 | 2710628.9216 | 1094095.9256 | 2710628.0775 | 1094095.7844
8 | 2710577.8088 | 1094424.235 | 2710578.8364 | 1094432.0757
9 | 2710677.6257 | 1094082.1101 | 2710710.7206 | 1094094.7908
10 | 2710677.6257 | 1094082.1101 | 2710677.6257 | 1094082.1101 | 2710681.949 | 1094067.7124 | 2710682.2557 | 1094066.5034
11 | 2710682.2557 | 1094066.5034 | 2710685.7397 | 1094052.7714 | 2710687.1872 | 1094042.0154
12 | 2710578.8364 | 1094432.0757 | 2710579.5441 | 1094437.4754 | 2710576.3607 | 1094457.3976 | 2710575.4701 | 1094460.0605
13 | 2710571.7984 | 1094471.038 | 2710575.4701 | 1094460.0605
14 | 2710869.5287 | 1093852.4123 | 2710869.2263 | 1093832.5195
15 | 2710869.8541 | 1093873.8195 | 2710869.5287 | 1093852.4123
16 | 2710869.1436 | 1093827.0744 | 2710869.2263 | 1093832.5195
17 | 2710869.9167 | 1093877.9411 | 2710869.8541 | 1093873.8195
18 | 2710869.1436 | 1093827.0744 | 2710868.9086 | 1093811.6147
19 | 2710868.9748 | 1093895.8367 | 2710869.9928 | 1093882.9466 | 2710869.9167 | 1093877.9411
20 | 2710866.9371 | 1093775.1296 | 2710868.5168 | 1093785.8322 | 2710868.9086 | 1093811.6147
21 | 2710868.9748 | 1093895.8367 | 2710868.9748 | 1093895.8367 | 2710865.0441 | 1093906.5278 | 2710863.7334 | 1093908.83
22 | 2710866.9371 | 1093775.1296 | 2710877.6282 | 1093771.5665 | 2710888.1254 | 1093763.7638
23 | 2710859.9757 | 1093915.4303 | 2710863.7334 | 1093908.83
24 | 2710778.531 | 1093813.6172 | 2710787.6959 | 1093813.745 | 2710820.4272 | 1093806.4919 | 2710820.4272 | 1093806.4919
25 | 2710819.3589 | 1093793.4675 | 2710820.4272 | 1093806.4919
26 | 2710778.531 | 1093813.6172 | 2710776.6982 | 1093813.5916
27 | 2710819.3175 | 1093792.9626 | 2710819.3589 | 1093793.4675
28 | 2710740.9253 | 1093813.0928 | 2710776.6982 | 1093813.5916
29 | 2710740.9253 | 1093813.0928 | 2710741.7397 | 1093816.8879 | 2710744.6247 | 1093829.0493
30 | 2710735.8949 | 1093794.8111 | 2710740.9253 | 1093813.0928
31 | 2710746.3171 | 1093836.1833 | 2710744.6247 | 1093829.0493
32 | 2710735.8949 | 1093794.8111 | 2710712.0748 | 1093810.2656 | 2710710.9656 | 1093815.3774
33 | 2710888.1254 | 1093763.7638 | 2710891.8497 | 1093771.1922 | 2710894.748 | 1093778.4388 | 2710896.7656 | 1093787.226 | 2710898.8256 | 1093800.061 | 2710901.7383 | 1093804.3948 | 2710905.8069 | 1093806.9708 | 2710910.6494 | 1093806.6366 | 2710921.623 | 1093804.722
34 | 2710568.1496 | 1094056.3348 | 2710553.1605 | 1094042.7088 | 2710547.563 | 1094033.8566 | 2710541.0559 | 1094021.2663
35 | 2710505.6072 | 1093972.6642 | 2710534.8413 | 1094012.311 | 2710540.1435 | 1094019.501 | 2710541.0559 | 1094021.2663
36 | 2710568.1496 | 1094056.3348 | 2710578.9704 | 1094057.1099 | 2710585.0154 | 1094066.4927 | 2710589.8727 | 1094076.8324 | 2710595.782 | 1094088.5589 | 2710602.9857 | 1094090.5994
37 | 2710505.6072 | 1093972.6642 | 2710495.4067 | 1093957.3686 | 2710493.0604 | 1093953.8459 | 2710488.7357 | 1093951.2878
38 | 2710484.4119 | 1094037.3559 | 2710497.9794 | 1093985.1006 | 2710505.6072 | 1093972.6642
39 | 2710628.0775 | 1094095.7844 | 2710611.5962 | 1094093.0384 | 2710602.9857 | 1094090.5994
40 | 2710483.7137 | 1093953.4417 | 2710488.7357 | 1093951.2878
41 | 2710628.0775 | 1094095.7844 | 2710625.8981 | 1094066.4918 | 2710624.7248 | 1094059.0593
42 | 2710447.3389 | 1093991.3217 | 2710451.4064 | 1093997.1072 | 2710456.8691 | 1093998.0292 | 2710461.5779 | 1093995.6576 | 2710480.6385 | 1093958.0008 | 2710483.1896 | 1093953.6664 | 2710483.7137 | 1093953.4417
43 | 2710621.6314 | 1094039.4627 | 2710624.7248 | 1094059.0593
44 | 2710447.3389 | 1093991.3217 | 2710447.1226 | 1093991.0142 | 2710440.5367 | 1093976.407 | 2710440.2151 | 1093971.7796
45 | 2710687.7242 | 1094038.0255 | 2710687.1872 | 1094042.0154
46 | 2710687.7242 | 1094038.0255 | 2710690.6267 | 1094016.4579
47 | 2710690.6267 | 1094016.4579 | 2710691.1356 | 1094012.676 | 2710691.3312 | 1094008.0915
48 | 2710692.1976 | 1093987.7855 | 2710691.3312 | 1094008.0915
49 | 2710692.1976 | 1093987.7855 | 2710692.569 | 1093979.0795
50 | 2710700.8424 | 1093972.0698 | 2710696.5968 | 1093973.6825 | 2710692.569 | 1093979.0795
51 | 2710700.8424 | 1093972.0698 | 2710700.5421 | 1093963.0236
52 | 2710717.0787 | 1093975.5121 | 2710712.5235 | 1093973.2721 | 2710706.8241 | 1093972.1565 | 2710700.8424 | 1093972.0698
53 | 2710700.5289 | 1093962.6267 | 2710700.5421 | 1093963.0236
54 | 2710740.1988 | 1093965.6931 | 2710724.0309 | 1093971.6806 | 2710717.0787 | 1093975.5121
55 | 2710635.1536 | 1093944.1645 | 2710631.2932 | 1093957.0005
56 | 2710635.1536 | 1093944.1645 | 2710641.1221 | 1093924.3196
57 | 2710700.511 | 1093962.0853 | 2710700.5289 | 1093962.6267
58 | 2710740.1988 | 1093965.6931 | 2710741.8883 | 1093965.1129
59 | 2710740.1988 | 1093965.6931 | 2710744.2715 | 1093987.058
60 | 2710700.511 | 1093962.0853 | 2710700.0817 | 1093949.1517 | 2710699.8496 | 1093944.0676
61 | 2710741.8883 | 1093965.1129 | 2710758.4932 | 1093959.4109
62 | 2710744.2715 | 1093987.058 | 2710746.195 | 1093997.1481
63 | 2710699.8496 | 1093944.0676 | 2710699.6717 | 1093940.1715 | 2710699.2738 | 1093933.0863
64 | 2710699.2738 | 1093933.0863 | 2710699.1216 | 1093930.3772 | 2710697.5254 | 1093921.7418
65 | 2710697.5254 | 1093921.7418 | 2710648.1747 | 1093900.8701
66 | 2710643.4321 | 1093916.6391 | 2710641.1221 | 1093924.3196
67 | 2710643.4321 | 1093916.6391 | 2710648.1747 | 1093900.8701
68 | 2710651.3923 | 1093890.1717 | 2710648.1747 | 1093900.8701
69 | 2710651.3923 | 1093890.1717 | 2710653.3781 | 1093883.5689
70 | 2710773.7744 | 1093954.1635 | 2710758.4932 | 1093959.4109
71 | 2710747.8101 | 1094005.6204 | 2710746.195 | 1093997.1481
72 | 2710747.8101 | 1094005.6204 | 2710749.3326 | 1094013.6074
73 | 2710750.6573 | 1094020.5563 | 2710749.3326 | 1094013.6074
74 | 2710750.6573 | 1094020.5563 | 2710752.0722 | 1094027.9784
75 | 2710773.7744 | 1093954.1635 | 2710772.5198 | 1093948.5813 | 2710768.2068 | 1093929.3758
76 | 2710773.7744 | 1093954.1635 | 2710789.0993 | 1093948.5405
77 | 2710755.2338 | 1094044.5635 | 2710752.0722 | 1094027.9784
78 | 2710755.2338 | 1094044.5635 | 2710757.157 | 1094054.6523
79 | 2710759.1645 | 1094065.1831 | 2710757.157 | 1094054.6523
80 | 2710783.7762 | 1093975.6379 | 2710783.7762 | 1093975.6379 | 2710783.9671 | 1093989.8287 | 2710784.6724 | 1094000.8823 | 2710787.5956 | 1094013.9888 | 2710787.9433 | 1094014.8358
81 | 2710797.5333 | 1093945.446 | 2710790.4103 | 1093958.6473 | 2710783.7762 | 1093975.6379
82 | 2710792.9979 | 1094027.1516 | 2710787.9433 | 1094014.8358
83 | 2710797.5333 | 1093945.446 | 2710789.0993 | 1093948.5405
84 | 2710797.5333 | 1093945.446 | 2710801.9851 | 1093944.0039 | 2710807.6061 | 1093942.1775
85 | 2710831.7292 | 1093934.3393 | 2710807.6061 | 1093942.1775
86 | 2710831.7292 | 1093934.3393 | 2710828.8992 | 1093919.251
87 | 2710831.7292 | 1093934.3393 | 2710843.422 | 1093929.8049
88 | 2710768.2068 | 1093929.3758 | 2710767.0906 | 1093924.4051
89 | 2710826.3599 | 1093905.7123 | 2710828.8992 | 1093919.251
90 | 2710859.9757 | 1093915.4303 | 2710850.3799 | 1093925.2398 | 2710843.422 | 1093929.8049
91 | 2710843.422 | 1093929.8049 | 2710835.5064 | 1093978.5685
92 | 2710827.7734 | 1094045.3216 | 2710829.4412 | 1094032.5477
93 | 2710827.7734 | 1094045.3216 | 2710826.8537 | 1094052.3655
94 | 2710829.8901 | 1094013.1674 | 2710829.0853 | 1094018.1252 | 2710830.8208 | 1094021.9817 | 2710829.4412 | 1094032.5477
95 | 2710831.8704 | 1094000.968 | 2710829.8901 | 1094013.1674
96 | 2710831.8704 | 1094000.968 | 2710833.0306 | 1093993.8201
97 | 2710835.5064 | 1093978.5685 | 2710833.0306 | 1093993.8201
98 | 2710859.9757 | 1093915.4303 | 2710862.0195 | 1093921.9275 | 2710862.8935 | 1093944.3355
99 | 2710862.8935 | 1093944.3355 | 2710863.5704 | 1093961.6902
100 | 2710863.6389 | 1093963.4458 | 2710863.5704 | 1093961.6902
101 | 2710863.6389 | 1093963.4458 | 2710863.948 | 1093971.3698
102 | 2710865.4666 | 1094010.3054 | 2710863.948 | 1093971.3698
103 | 2710865.7314 | 1094017.0954 | 2710865.4666 | 1094010.3054
104 | 2710866.0963 | 1094026.4498 | 2710865.7314 | 1094017.0954
105 | 2710826.3599 | 1093905.7123 | 2710822.2675 | 1093883.8926
106 | 2710819.6252 | 1093869.8049 | 2710822.2675 | 1093883.8926
107 | 2710819.6252 | 1093869.8049 | 2710817.8284 | 1093860.2251
108 | 2710817.8284 | 1093860.2251 | 2710813.4213 | 1093836.7277
109 | 2710813.4213 | 1093836.7277 | 2710813.0699 | 1093834.854
110 | 2710767.0906 | 1093924.4051 | 2710763.8739 | 1093910.0814
111 | 2710763.8739 | 1093910.0814 | 2710760.5776 | 1093895.4028
112 | 2710757.4204 | 1093881.3438 | 2710760.5776 | 1093895.4028
113 | 2710755.193 | 1093871.4251 | 2710757.4204 | 1093881.3438
114 | 2710731.9102 | 1093868.7899 | 2710728.8392 | 1093867.7094 | 2710728.2432 | 1093865.7418
115 | 2710731.9102 | 1093868.7899 | 2710732.8052 | 1093869.1048 | 2710738.825 | 1093867.5309
116 | 2710728.2432 | 1093865.7418 | 2710726.0983 | 1093858.6605
117 | 2710752.8817 | 1093863.8557 | 2710738.825 | 1093867.5309
118 | 2710726.0983 | 1093858.6605 | 2710723.5583 | 1093850.2744
119 | 2710752.8817 | 1093863.8557 | 2710750.2419 | 1093852.7277
120 | 2710755.193 | 1093871.4251 | 2710752.8817 | 1093863.8557
121 | 2710723.5583 | 1093850.2744 | 2710720.3732 | 1093839.7587 | 2710720.3732 | 1093839.7587
122 | 2710750.2419 | 1093852.7277 | 2710746.3171 | 1093836.1833
123 | 2710755.193 | 1093871.4251 | 2710765.5044 | 1093869.0348
124 | 2710716.5638 | 1093834.4414 | 2710720.3732 | 1093839.7587
125 | 2710765.5044 | 1093869.0348 | 2710767.0144 | 1093868.6847
126 | 2710778.7611 | 1093865.9617 | 2710767.0144 | 1093868.6847
127 | 2710778.7611 | 1093865.9617 | 2710784.543 | 1093864.7569
128 | 2710778.7611 | 1093865.9617 | 2710784.986 | 1093890.0588
129 | 2710788.8109 | 1093904.8657 | 2710784.986 | 1093890.0588
130 | 2710789.9464 | 1093909.2612 | 2710788.8109 | 1093904.8657
131 | 2710784.543 | 1093864.7569 | 2710790.4496 | 1093863.526
132 | 2710440.2151 | 1093971.7796 | 2710440.1011 | 1093970.1396
133 | 2710438.455 | 1093943.2141 | 2710438.5768 | 1093948.2081 | 2710440.1011 | 1093970.1396
134 | 2710438.455 | 1093943.2141 | 2710438.4244 | 1093941.9581
135 | 2710438.2747 | 1093935.8207 | 2710438.4244 | 1093941.9581
136 | 2710438.2747 | 1093935.8207 | 2710438.1068 | 1093928.9374
137 | 2710438.1068 | 1093928.9374 | 2710438.018 | 1093925.2933
138 | 2710437.9358 | 1093921.9229 | 2710438.018 | 1093925.2933
139 | 2710437.9358 | 1093921.9229 | 2710437.7585 | 1093914.6548
140 | 2710437.7585 | 1093914.6548 | 2710437.6012 | 1093908.2019
141 | 2710437.2193 | 1093892.5408 | 2710437.6012 | 1093908.2019
142 | 2710437.1179 | 1093888.3839 | 2710437.2193 | 1093892.5408
143 | 2710437.1179 | 1093888.3839 | 2710436.9829 | 1093882.8463

## bus_geodata
| x | y | coords
0 | 2710668.712 | 1094162.4658
1 | 2710654.6988 | 1094093.1595
2 | 2710570.3172 | 1094239.2303
3 | 2710666.8702 | 1094088.6656
4 | 2710628.9216 | 1094095.9256
5 | 2710557.2889 | 1094221.3859
6 | 2710577.8088 | 1094424.235
7 | 2710710.7206 | 1094094.7908
8 | 2710677.6257 | 1094082.1101
9 | 2710682.2557 | 1094066.5034
10 | 2710578.8364 | 1094432.0757
11 | 2710575.4701 | 1094460.0605
12 | 2710571.7984 | 1094471.038
13 | 2710869.5287 | 1093852.4123
14 | 2710869.2263 | 1093832.5195
15 | 2710869.8541 | 1093873.8195
16 | 2710869.1436 | 1093827.0744
17 | 2710869.9167 | 1093877.9411
18 | 2710868.9086 | 1093811.6147
19 | 2710868.9748 | 1093895.8367
20 | 2710866.9371 | 1093775.1296
21 | 2710863.7334 | 1093908.83
22 | 2710820.4272 | 1093806.4919
23 | 2710778.531 | 1093813.6172
24 | 2710819.3589 | 1093793.4675
25 | 2710776.6982 | 1093813.5916
26 | 2710819.3175 | 1093792.9626
27 | 2710740.9253 | 1093813.0928
28 | 2710744.6247 | 1093829.0493
29 | 2710735.8949 | 1093794.8111
30 | 2710888.1254 | 1093763.7638
31 | 2710921.623 | 1093804.722
32 | 2710541.0559 | 1094021.2663
33 | 2710568.1496 | 1094056.3348
34 | 2710505.6072 | 1093972.6642
35 | 2710602.9857 | 1094090.5994
36 | 2710488.7357 | 1093951.2878
37 | 2710484.4119 | 1094037.3559
38 | 2710628.0775 | 1094095.7844
39 | 2710483.7137 | 1093953.4417
40 | 2710624.7248 | 1094059.0593
41 | 2710447.3389 | 1093991.3217
42 | 2710621.6314 | 1094039.4627
43 | 2710687.1872 | 1094042.0154
44 | 2710687.7242 | 1094038.0255
45 | 2710690.6267 | 1094016.4579
46 | 2710691.3312 | 1094008.0915
47 | 2710692.1976 | 1093987.7855
48 | 2710692.569 | 1093979.0795
49 | 2710700.8424 | 1093972.0698
50 | 2710700.5421 | 1093963.0236
51 | 2710717.0787 | 1093975.5121
52 | 2710631.2932 | 1093957.0005
53 | 2710635.1536 | 1093944.1645
54 | 2710700.5289 | 1093962.6267
55 | 2710740.1988 | 1093965.6931
56 | 2710700.511 | 1093962.0853
57 | 2710741.8883 | 1093965.1129
58 | 2710744.2715 | 1093987.058
59 | 2710699.8496 | 1093944.0676
60 | 2710699.2738 | 1093933.0863
61 | 2710697.5254 | 1093921.7418
62 | 2710641.1221 | 1093924.3196
63 | 2710648.1747 | 1093900.8701
64 | 2710651.3923 | 1093890.1717
65 | 2710653.3781 | 1093883.5689
66 | 2710643.4321 | 1093916.6391
67 | 2710758.4932 | 1093959.4109
68 | 2710746.195 | 1093997.1481
69 | 2710747.8101 | 1094005.6204
70 | 2710749.3326 | 1094013.6074
71 | 2710750.6573 | 1094020.5563
72 | 2710773.7744 | 1093954.1635
73 | 2710752.0722 | 1094027.9784
74 | 2710755.2338 | 1094044.5635
75 | 2710757.157 | 1094054.6523
76 | 2710759.1645 | 1094065.1831
77 | 2710783.7762 | 1093975.6379
78 | 2710787.9433 | 1094014.8358
79 | 2710797.5333 | 1093945.446
80 | 2710792.9979 | 1094027.1516
81 | 2710789.0993 | 1093948.5405
82 | 2710807.6061 | 1093942.1775
83 | 2710831.7292 | 1093934.3393
84 | 2710768.2068 | 1093929.3758
85 | 2710828.8992 | 1093919.251
86 | 2710843.422 | 1093929.8049
87 | 2710827.7734 | 1094045.3216
88 | 2710829.4412 | 1094032.5477
89 | 2710826.8537 | 1094052.3655
90 | 2710829.8901 | 1094013.1674
91 | 2710831.8704 | 1094000.968
92 | 2710833.0306 | 1093993.8201
93 | 2710835.5064 | 1093978.5685
94 | 2710859.9757 | 1093915.4303
95 | 2710862.8935 | 1093944.3355
96 | 2710863.5704 | 1093961.6902
97 | 2710863.6389 | 1093963.4458
98 | 2710863.948 | 1093971.3698
99 | 2710865.4666 | 1094010.3054
100 | 2710865.7314 | 1094017.0954
101 | 2710866.0963 | 1094026.4498
102 | 2710826.3599 | 1093905.7123
103 | 2710822.2675 | 1093883.8926
104 | 2710819.6252 | 1093869.8049
105 | 2710817.8284 | 1093860.2251
106 | 2710813.4213 | 1093836.7277
107 | 2710813.0699 | 1093834.854
108 | 2710767.0906 | 1093924.4051
109 | 2710763.8739 | 1093910.0814
110 | 2710760.5776 | 1093895.4028
111 | 2710757.4204 | 1093881.3438
112 | 2710731.9102 | 1093868.7899
113 | 2710728.2432 | 1093865.7418
114 | 2710738.825 | 1093867.5309
115 | 2710726.0983 | 1093858.6605
116 | 2710752.8817 | 1093863.8557
117 | 2710723.5583 | 1093850.2744
118 | 2710750.2419 | 1093852.7277
119 | 2710755.193 | 1093871.4251
120 | 2710720.3732 | 1093839.7587
121 | 2710746.3171 | 1093836.1833
122 | 2710765.5044 | 1093869.0348
123 | 2710767.0144 | 1093868.6847
124 | 2710778.7611 | 1093865.9617
125 | 2710716.5638 | 1093834.4414
126 | 2710710.9656 | 1093815.3774
127 | 2710788.8109 | 1093904.8657
128 | 2710784.986 | 1093890.0588
129 | 2710789.9464 | 1093909.2612
130 | 2710784.543 | 1093864.7569
131 | 2710790.4496 | 1093863.526
132 | 2710440.2151 | 1093971.7796
133 | 2710440.1011 | 1093970.1396
134 | 2710438.455 | 1093943.2141
135 | 2710438.4244 | 1093941.9581
136 | 2710438.2747 | 1093935.8207
137 | 2710438.1068 | 1093928.9374
138 | 2710438.018 | 1093925.2933
139 | 2710437.9358 | 1093921.9229
140 | 2710437.7585 | 1093914.6548
141 | 2710437.6012 | 1093908.2019
142 | 2710437.2193 | 1093892.5408
143 | 2710437.1179 | 1093888.3839
144 | 2710436.9829 | 1093882.8463
145 | 2710700.8424 | 1093972.0698

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.9909 | -0.17352 | 0.0043641 | 0.0010937
1 | 0.99274 | -0.13797 | 0.0053895 | 0.0013507
2 | 0.98815 | -0.22686 | 0.0089931 | 0.0022539
3 | 0.99313 | -0.13053 | 0.0014715 | 0.00036879
4 | 0.99214 | -0.14935 | 0.0027187 | 0.00068136
5 | 0.98807 | -0.22835 | 0.0037766 | 0.00094651
6 | 0.98623 | -0.26406 | 0 | 0
7 | 0.99345 | -0.12448 | 0.0020825 | 0.00052193
8 | 0.99351 | -0.12317 | 0.0019584 | 0.00049081
9 | 0.99402 | -0.11346 | 0.0015572 | 0.00039028
10 | 0.98615 | -0.26566 | 0.0043249 | 0.0010839
11 | 0.98597 | -0.26917 | 0.0043439 | 0.0010887
12 | 0.98594 | -0.26971 | 0.0025614 | 0.00064194
13 | 0.98228 | -0.34069 | 0.0053699 | 0.0013458
14 | 0.98209 | -0.34448 | 0.0032147 | 0.00080568
15 | 0.98259 | -0.33454 | 0.0043366 | 0.0010869
16 | 0.98205 | -0.3452 | 0.0023798 | 0.00059645
17 | 0.98267 | -0.33304 | 0.0044636 | 0.0011187
18 | 0.98198 | -0.34658 | 0.0023759 | 0.00059545
19 | 0.98308 | -0.32504 | 0.0015857 | 0.00039743
20 | 0.98189 | -0.34827 | 0 | 0
21 | 0.98342 | -0.31839 | 0.0069466 | 0.001741
22 | 0.97729 | -0.43785 | 0.0053511 | 0.0013411
23 | 0.97861 | -0.41182 | 0.0038869 | 0.00097416
24 | 0.97695 | -0.44456 | 0.0059407 | 0.0014889
25 | 0.97868 | -0.41058 | 0.0029437 | 0.00073775
26 | 0.97694 | -0.44477 | 0.022167 | 0.0055557
27 | 0.98001 | -0.38438 | 0 | 0
28 | 0.9807 | -0.37105 | 0.0026426 | 0.00066231
29 | 0.97993 | -0.38596 | 0 | 0
30 | 0.98184 | -0.3494 | 0 | 0
31 | 0.98168 | -0.35237 | 0.0025585 | 0.00064122
32 | 0.98413 | -0.30296 | 0.0062659 | 0.0015704
33 | 0.98732 | -0.24136 | 0 | 0
34 | 0.98019 | -0.37932 | 0 | 0
35 | 0.99118 | -0.16772 | 0.0027559 | 0.00069071
36 | 0.97848 | -0.41258 | 0.0019806 | 0.00049638
37 | 0.97993 | -0.38429 | 0.0039972 | 0.0010018
38 | 0.99212 | -0.1497 | 0 | 0
39 | 0.97816 | -0.41897 | 0.0064656 | 0.0016204
40 | 0.99165 | -0.15881 | 0.002649 | 0.00066389
41 | 0.97462 | -0.48836 | 0.0022291 | 0.00055867
42 | 0.99145 | -0.16278 | 0.011288 | 0.0028291
43 | 0.99481 | -0.098384 | 0.001942 | 0.00048671
44 | 0.99494 | -0.095926 | 0.0018223 | 0.00045672
45 | 0.99565 | -0.082474 | 0.0013922 | 0.00034892
46 | 0.99592 | -0.077233 | 0.00096546 | 0.00024197
47 | 0.9966 | -0.064484 | 0.0042408 | 0.0010628
48 | 0.99689 | -0.058861 | 0.0031021 | 0.00077747
49 | 0.99728 | -0.051436 | 0 | 0
50 | 0.99815 | -0.034976 | 0.0018128 | 0.00045433
51 | 0.99625 | -0.071 | 0 | 0
52 | 0.99734 | -0.051076 | 0.0031131 | 0.00078023
53 | 0.99738 | -0.050345 | 0.0048349 | 0.0012117
54 | 0.99819 | -0.034251 | 0.0032077 | 0.00080394
55 | 0.99472 | -0.10029 | 0.0043482 | 0.0010898
56 | 0.99824 | -0.033256 | 0.0020752 | 0.00052011
57 | 0.99462 | -0.10219 | 0.0012695 | 0.00031817
58 | 0.99432 | -0.108 | 0.0027549 | 0.00069045
59 | 1 | 0 | -0.4666 | -0.11904
60 | 0.99964 | -0.0068918 | 0.0029768 | 0.00074604
61 | 0.9993 | -0.013504 | 0.003394 | 0.00085061
62 | 0.99753 | -0.047459 | 0.0040527 | 0.0010157
63 | 0.99786 | -0.041201 | 0.0036873 | 0.00092413
64 | 0.99775 | -0.043163 | 0.0043758 | 0.0010967
65 | 0.99772 | -0.043845 | 0.0056515 | 0.0014164
66 | 0.99762 | -0.045773 | 0.003854 | 0.00096591
67 | 0.99365 | -0.12072 | 0.0021933 | 0.0005497
68 | 0.99415 | -0.11115 | 0.0027986 | 0.0007014
69 | 0.99404 | -0.11337 | 0.0014691 | 0.00036819
70 | 0.99394 | -0.11525 | 0.001189 | 0.00029799
71 | 0.99387 | -0.11673 | 0.001699 | 0.00042581
72 | 0.99188 | -0.15462 | 0 | 0
73 | 0.9938 | -0.11809 | 0.0012609 | 0.00031602
74 | 0.99366 | -0.12076 | 0.0031224 | 0.00078255
75 | 0.9936 | -0.12182 | 0.0029838 | 0.00074782
76 | 0.99358 | -0.12236 | 0.0028445 | 0.00071289
77 | 0.98887 | -0.21264 | 0.003306 | 0.00082857
78 | 0.98862 | -0.21741 | 0.0037619 | 0.00094282
79 | 0.98917 | -0.20668 | 0 | 0
80 | 0.98858 | -0.21813 | 0.002995 | 0.00075061
81 | 0.99012 | -0.18841 | 0.0023679 | 0.00059344
82 | 0.98816 | -0.22636 | 0.0013887 | 0.00034803
83 | 0.98575 | -0.27302 | 0 | 0
84 | 0.98904 | -0.20907 | 0.0038943 | 0.000976
85 | 0.98538 | -0.28027 | 0.0034067 | 0.0008538
86 | 0.98487 | -0.2902 | 0 | 0
87 | 0.98351 | -0.31671 | 0.0028291 | 0.00070904
88 | 0.98357 | -0.31557 | 0.0021547 | 0.00054001
89 | 0.9835 | -0.31697 | 0.0020465 | 0.00051291
90 | 0.9837 | -0.31305 | 0.0020648 | 0.0005175
91 | 0.9838 | -0.31103 | 0.004253 | 0.0010659
92 | 0.98389 | -0.30929 | 0.0017027 | 0.00042675
93 | 0.9841 | -0.3051 | 0.0017225 | 0.00043171
94 | 0.98365 | -0.31384 | 0 | 0
95 | 0.98294 | -0.32778 | 0.0015406 | 0.0003861
96 | 0.98254 | -0.33559 | 0.0015876 | 0.00039788
97 | 0.9825 | -0.33633 | 0.0015444 | 0.00038707
98 | 0.98234 | -0.33945 | 0.0012809 | 0.00032103
99 | 0.9816 | -0.35389 | 0.0037166 | 0.00093147
100 | 0.9815 | -0.35596 | 0.0020665 | 0.00051791
101 | 0.98137 | -0.35845 | 0.01472 | 0.0036893
102 | 0.98509 | -0.28595 | 0.0020782 | 0.00052085
103 | 0.98466 | -0.29426 | 0.0040006 | 0.0010027
104 | 0.98444 | -0.2986 | 0.004425 | 0.001109
105 | 0.98433 | -0.30078 | 0.0042659 | 0.0010691
106 | 0.98415 | -0.30429 | 0.0042983 | 0.0010773
107 | 0.98414 | -0.30442 | 0.003858 | 0.00096691
108 | 0.98849 | -0.21967 | 0.0022257 | 0.00055781
109 | 0.98694 | -0.24971 | 0.0025572 | 0.0006409
110 | 0.98538 | -0.2799 | 0.0036714 | 0.00092013
111 | 0.98393 | -0.30794 | 0.0051796 | 0.0012981
112 | 0.98188 | -0.34797 | 0.0058264 | 0.0014602
113 | 0.9818 | -0.3496 | 0.0028339 | 0.00071025
114 | 0.98203 | -0.34501 | 0.0031281 | 0.00078397
115 | 0.9817 | -0.35149 | 0.0029165 | 0.00073093
116 | 0.98238 | -0.3382 | 0 | 0
117 | 0.98161 | -0.35327 | 0.0031298 | 0.0007844
118 | 0.98181 | -0.34929 | 0.0034398 | 0.00086209
119 | 0.98296 | -0.32683 | 0 | 0
120 | 0.98153 | -0.35488 | 0.0039472 | 0.00098927
121 | 0.98102 | -0.36474 | 0.0026882 | 0.00067372
122 | 0.98273 | -0.33133 | 0.0036672 | 0.00091909
123 | 0.98271 | -0.33188 | 0.0038221 | 0.0009579
124 | 0.98253 | -0.33537 | 0 | 0
125 | 0.9815 | -0.35537 | 0.0041552 | 0.0010414
126 | 0.97979 | -0.38875 | 0.0045814 | 0.0011482
127 | 0.98229 | -0.34007 | 0.0026045 | 0.00065274
128 | 0.98234 | -0.33895 | 0.0038851 | 0.00097369
129 | 0.98228 | -0.34019 | 0.0014708 | 0.00036862
130 | 0.98248 | -0.33623 | 0.0041913 | 0.0010504
131 | 0.98246 | -0.33665 | 0.0038745 | 0.00097105
132 | 0.97353 | -0.50982 | 0.012674 | 0.0031764
133 | 0.97346 | -0.51112 | 0.0072823 | 0.0018251
134 | 0.97257 | -0.52879 | 0.0024561 | 0.00061556
135 | 0.97253 | -0.52956 | 0.0048302 | 0.0012106
136 | 0.97237 | -0.53276 | 0.0021485 | 0.00053845
137 | 0.9722 | -0.53608 | 0.0021575 | 0.00054073
138 | 0.97212 | -0.53769 | 0.0028031 | 0.00070252
139 | 0.97205 | -0.53901 | 0.0022416 | 0.00056179
140 | 0.97192 | -0.54155 | 0.0023766 | 0.00059564
141 | 0.97182 | -0.54352 | 0.0029923 | 0.00074994
142 | 0.97162 | -0.54745 | 0.0026861 | 0.00067321
143 | 0.97158 | -0.54828 | 0.0084587 | 0.0021199
144 | 0.97157 | -0.54853 | 0.00243 | 0.00060901
145 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.028448 | -0.0071573 | 0.028496 | 0.0071874 | 4.8412e-05 | 3.0071e-05 | 0.042729 | 0.042729 | 0.042729 | 0.9909 | -0.17352 | 0.99274 | -0.13797 | 11.7388
1 | 0.024083 | 0.0060636 | -0.024022 | -0.006026 | 6.1246e-05 | 3.7594e-05 | 0.036176 | 0.036176 | 0.036176 | 0.9909 | -0.17352 | 0.98815 | -0.22686 | 9.9385
2 | -0.1311 | -0.033411 | 0.13115 | 0.033441 | 4.7064e-05 | 2.945e-05 | 0.1967 | 0.1967 | 0.1967 | 0.99274 | -0.13797 | 0.99313 | -0.13053 | 13.5099
3 | 0.097215 | 0.024873 | -0.097162 | -0.02484 | 5.3526e-05 | 3.287e-05 | 0.1459 | 0.1459 | 0.1459 | 0.99274 | -0.13797 | 0.99214 | -0.14935 | 10.0205
4 | 0.011252 | 0.0028257 | -0.011232 | -0.0028153 | 1.9941e-05 | 1.0395e-05 | 0.016946 | 0.016947 | 0.016947 | 0.98815 | -0.22686 | 0.98623 | -0.26406 | 4.6558
5 | 0.0037769 | 0.0009464 | -0.0037766 | -0.00094651 | 2.6801e-07 | -1.1148e-07 | 0.0056874 | 0.0056875 | 0.0056875 | 0.98815 | -0.22686 | 0.98807 | -0.22835 | 1.5625
6 | -0.13262 | -0.03381 | 0.13267 | 0.033839 | 4.7145e-05 | 2.9515e-05 | 0.19891 | 0.19891 | 0.19891 | 0.99313 | -0.13053 | 0.99351 | -0.12317 | 13.6613
7 | 0.094443 | 0.024159 | -0.094441 | -0.024158 | 1.6138e-06 | 9.8864e-07 | 0.14182 | 0.14182 | 0.14182 | 0.99214 | -0.14935 | 0.99212 | -0.1497 | 9.7404
8 | 0.011232 | 0.0028153 | -0.011231 | -0.0028148 | 8.5169e-07 | 4.4418e-07 | 0.016947 | 0.016947 | 0.016947 | 0.98623 | -0.26406 | 0.98615 | -0.26566 | 4.6558
9 | -0.0020825 | -0.00052193 | 0.0020827 | 0.00052156 | 1.2931e-07 | -3.7616e-07 | 0.0031193 | 0.0031191 | 0.0031193 | 0.99345 | -0.12448 | 0.99351 | -0.12317 | 0.85695
10 | -0.13671 | -0.034851 | 0.13677 | 0.034892 | 6.4116e-05 | 4.0191e-05 | 0.20496 | 0.20496 | 0.20496 | 0.99351 | -0.12317 | 0.99402 | -0.11346 | 14.077
11 | -0.13833 | -0.035282 | 0.13843 | 0.035345 | 0.00010079 | 6.3208e-05 | 0.20729 | 0.20729 | 0.20729 | 0.99402 | -0.11346 | 0.99481 | -0.098384 | 14.2371
12 | 0.0069065 | 0.0017309 | -0.0069054 | -0.0017305 | 1.1578e-06 | 3.7836e-07 | 0.010421 | 0.010421 | 0.010421 | 0.98615 | -0.26566 | 0.98597 | -0.26917 | 2.863
13 | 0.0025614 | 0.00064183 | -0.0025614 | -0.00064194 | 6.4864e-08 | -1.0611e-07 | 0.0038656 | 0.0038657 | 0.0038657 | 0.98597 | -0.26917 | 0.98594 | -0.26971 | 1.062
14 | 0.010532 | 0.0026387 | -0.01053 | -0.0026378 | 1.8991e-06 | 9.636e-07 | 0.015954 | 0.015954 | 0.015954 | 0.98228 | -0.34069 | 0.98209 | -0.34448 | 4.3831
15 | -0.015902 | -0.0039845 | 0.015907 | 0.0039873 | 4.6588e-06 | 2.7105e-06 | 0.024089 | 0.024089 | 0.024089 | 0.98228 | -0.34069 | 0.98259 | -0.33454 | 6.6178
16 | 0.0073155 | 0.0018321 | -0.0073152 | -0.001832 | 2.5087e-07 | 9.1653e-08 | 0.011084 | 0.011084 | 0.011084 | 0.98209 | -0.34448 | 0.98205 | -0.3452 | 3.045
17 | -0.020243 | -0.0050741 | 0.020245 | 0.005075 | 1.4527e-06 | 8.7751e-07 | 0.030656 | 0.030656 | 0.030656 | 0.98259 | -0.33454 | 0.98267 | -0.33304 | 8.422
18 | 0.0049354 | 0.0012355 | -0.0049351 | -0.0012355 | 3.242e-07 | 1.1878e-08 | 0.0074777 | 0.0074777 | 0.0074777 | 0.98205 | -0.3452 | 0.98198 | -0.34658 | 2.0543
19 | -0.024708 | -0.0061937 | 0.024718 | 0.0061995 | 9.4159e-06 | 5.7988e-06 | 0.037415 | 0.037415 | 0.037415 | 0.98267 | -0.33304 | 0.98308 | -0.32504 | 10.2789
20 | 0.0025592 | 0.00064009 | -0.002559 | -0.00064042 | 2.0639e-07 | -3.3094e-07 | 0.0038775 | 0.0038777 | 0.0038777 | 0.98198 | -0.34658 | 0.98189 | -0.34827 | 1.0653
21 | -0.026303 | -0.0065969 | 0.026312 | 0.0066021 | 8.3463e-06 | 5.1636e-06 | 0.039815 | 0.039815 | 0.039815 | 0.98308 | -0.32504 | 0.98342 | -0.31839 | 10.9383
22 | 0.002559 | 0.00064042 | -0.0025588 | -0.00064064 | 1.37e-07 | -2.1961e-07 | 0.0038777 | 0.0038778 | 0.0038778 | 0.98189 | -0.34827 | 0.98184 | -0.3494 | 1.0653
23 | -0.033258 | -0.0083431 | 0.033266 | 0.0083476 | 7.2136e-06 | 4.5203e-06 | 0.050326 | 0.050326 | 0.050326 | 0.98342 | -0.31839 | 0.98365 | -0.31384 | 13.8259
24 | -0.033468 | -0.0083914 | 0.03351 | 0.0084175 | 4.1575e-05 | 2.6072e-05 | 0.05096 | 0.05096 | 0.05096 | 0.97729 | -0.43785 | 0.97861 | -0.41182 | 14
25 | 0.028117 | 0.0070503 | -0.028108 | -0.0070447 | 8.9823e-06 | 5.585e-06 | 0.042813 | 0.042813 | 0.042813 | 0.97729 | -0.43785 | 0.97695 | -0.44456 | 11.7617
26 | -0.037397 | -0.0093916 | 0.037399 | 0.009393 | 2.2231e-06 | 1.3997e-06 | 0.05687 | 0.05687 | 0.05687 | 0.97861 | -0.41182 | 0.97868 | -0.41058 | 15.6237
27 | 0.022168 | 0.0055558 | -0.022167 | -0.0055557 | 2.1657e-07 | 1.3226e-07 | 0.033764 | 0.033764 | 0.033764 | 0.97695 | -0.44456 | 0.97694 | -0.44477 | 9.2759
28 | -0.040343 | -0.010131 | 0.040393 | 0.010163 | 5.0489e-05 | 3.1863e-05 | 0.061346 | 0.061346 | 0.061346 | 0.97868 | -0.41058 | 0.98001 | -0.38438 | 16.8532
29 | -0.044976 | -0.011311 | 0.045004 | 0.011329 | 2.8658e-05 | 1.8134e-05 | 0.068303 | 0.068303 | 0.068303 | 0.98001 | -0.38438 | 0.9807 | -0.37105 | 18.7646
30 | 0.0045823 | 0.0011481 | -0.004582 | -0.0011482 | 3.442e-07 | -1.8606e-08 | 0.0069575 | 0.0069576 | 0.0069576 | 0.98001 | -0.38438 | 0.97993 | -0.38596 | 1.9114
31 | -0.047647 | -0.011991 | 0.047661 | 0.012 | 1.4378e-05 | 9.1091e-06 | 0.072313 | 0.072313 | 0.072313 | 0.9807 | -0.37105 | 0.98102 | -0.36474 | 19.8661
32 | 0.004582 | 0.0011482 | -0.0045814 | -0.0011482 | 6.1041e-07 | -3.2886e-08 | 0.0069576 | 0.0069578 | 0.0069578 | 0.97993 | -0.38596 | 0.97979 | -0.38875 | 1.9115
33 | 0.0025588 | 0.00064064 | -0.0025585 | -0.00064122 | 3.6183e-07 | -5.7974e-07 | 0.0038778 | 0.0038781 | 0.0038781 | 0.98184 | -0.3494 | 0.98168 | -0.35237 | 1.0654
34 | -0.077164 | -0.019603 | 0.077393 | 0.019749 | 0.00022959 | 0.00014636 | 0.11677 | 0.11677 | 0.11677 | 0.98413 | -0.30296 | 0.98732 | -0.24136 | 32.0791
35 | 0.070898 | 0.018033 | -0.070638 | -0.017867 | 0.0002598 | 0.00016551 | 0.10729 | 0.10729 | 0.10729 | 0.98413 | -0.30296 | 0.98019 | -0.37932 | 29.4764
36 | -0.077393 | -0.019749 | 0.07767 | 0.019925 | 0.00027637 | 0.00017618 | 0.11677 | 0.11677 | 0.11677 | 0.98732 | -0.24136 | 0.99118 | -0.16772 | 32.079
37 | 0.06664 | 0.016866 | -0.066534 | -0.016798 | 0.00010621 | 6.7628e-05 | 0.10122 | 0.10122 | 0.10122 | 0.98019 | -0.37932 | 0.97848 | -0.41258 | 27.809
38 | 0.0039981 | 0.0010015 | -0.0039972 | -0.0010018 | 9.473e-07 | -2.5784e-07 | 0.0060693 | 0.0060696 | 0.0060696 | 0.98019 | -0.37932 | 0.97993 | -0.38429 | 1.6675
39 | -0.080426 | -0.020616 | 0.080496 | 0.020661 | 7.0324e-05 | 4.4345e-05 | 0.1209 | 0.1209 | 0.1209 | 0.99118 | -0.16772 | 0.99212 | -0.1497 | 16.6078
40 | 0.064553 | 0.016302 | -0.064534 | -0.016289 | 1.9766e-05 | 1.2581e-05 | 0.098213 | 0.098213 | 0.098213 | 0.97848 | -0.41258 | 0.97816 | -0.41897 | 26.9816
41 | 0.013945 | 0.0034975 | -0.013939 | -0.0034941 | 6.0536e-06 | 3.3981e-06 | 0.020916 | 0.020917 | 0.020917 | 0.99212 | -0.1497 | 0.99165 | -0.15881 | 5.7463
42 | 0.058068 | 0.014669 | -0.057876 | -0.014546 | 0.0001924 | 0.00012232 | 0.088377 | 0.088378 | 0.088378 | 0.97816 | -0.41897 | 0.97462 | -0.48836 | 24.2795
43 | 0.01129 | 0.0028302 | -0.011288 | -0.0028291 | 2.1354e-06 | 1.1107e-06 | 0.016942 | 0.016942 | 0.016942 | 0.99165 | -0.15881 | 0.99145 | -0.16278 | 4.6543
44 | 0.055646 | 0.013988 | -0.055589 | -0.013951 | 5.6965e-05 | 3.6196e-05 | 0.084974 | 0.084974 | 0.084974 | 0.97462 | -0.48836 | 0.97353 | -0.50982 | 23.3446
45 | -0.14037 | -0.035832 | 0.14039 | 0.035842 | 1.6676e-05 | 1.0463e-05 | 0.2102 | 0.2102 | 0.2102 | 0.99481 | -0.098384 | 0.99494 | -0.095926 | 14.4365
46 | -0.14221 | -0.036299 | 0.1423 | 0.036357 | 9.2493e-05 | 5.8064e-05 | 0.21292 | 0.21292 | 0.21292 | 0.99494 | -0.095926 | 0.99565 | -0.082474 | 14.6237
47 | -0.1437 | -0.036706 | 0.14373 | 0.036729 | 3.6423e-05 | 2.2873e-05 | 0.215 | 0.215 | 0.215 | 0.99565 | -0.082474 | 0.99592 | -0.077233 | 14.7666
48 | -0.1447 | -0.036971 | 0.14479 | 0.037027 | 8.9265e-05 | 5.6071e-05 | 0.21644 | 0.21644 | 0.21644 | 0.99592 | -0.077233 | 0.9966 | -0.064484 | 14.8657
49 | -0.14903 | -0.03809 | 0.14907 | 0.038115 | 4.0543e-05 | 2.5493e-05 | 0.22278 | 0.22278 | 0.22278 | 0.9966 | -0.064484 | 0.99689 | -0.058861 | 15.3005
50 | -0.15217 | -0.038893 | 0.15222 | 0.038927 | 5.4666e-05 | 3.4398e-05 | 0.22741 | 0.22741 | 0.22741 | 0.99689 | -0.058861 | 0.99728 | -0.051436 | 15.6185
51 | -0.42079 | -0.10754 | 0.42112 | 0.10775 | 0.00033528 | 0.0002141 | 0.62858 | 0.62858 | 0.62858 | 0.99728 | -0.051436 | 0.99815 | -0.034976 | 43.172
52 | 0.26856 | 0.06861 | -0.26831 | -0.068449 | 0.00025377 | 0.00016154 | 0.40118 | 0.40118 | 0.40118 | 0.99728 | -0.051436 | 0.99625 | -0.071 | 27.5535
53 | -0.42294 | -0.10821 | 0.42295 | 0.10822 | 1.4841e-05 | 9.4772e-06 | 0.63129 | 0.63129 | 0.63129 | 0.99815 | -0.034976 | 0.99819 | -0.034251 | 43.3576
54 | 0.26831 | 0.068449 | -0.26793 | -0.068207 | 0.00037899 | 0.00024125 | 0.40118 | 0.40118 | 0.40118 | 0.99625 | -0.071 | 0.99472 | -0.10029 | 27.5535
55 | -0.0031131 | -0.00078023 | 0.0031132 | 0.00078012 | 1.0844e-07 | -1.0552e-07 | 0.0046447 | 0.0046447 | 0.0046447 | 0.99734 | -0.051076 | 0.99738 | -0.050345 | 1.276
56 | -0.0079482 | -0.0019919 | 0.0079493 | 0.0019923 | 1.0927e-06 | 4.2884e-07 | 0.011858 | 0.011858 | 0.011858 | 0.99738 | -0.050345 | 0.99753 | -0.047459 | 3.2577
57 | -0.42616 | -0.10902 | 0.42618 | 0.10903 | 2.0544e-05 | 1.312e-05 | 0.63607 | 0.63607 | 0.63607 | 0.99819 | -0.034251 | 0.99824 | -0.033256 | 43.686
58 | 0.24344 | 0.062066 | -0.24342 | -0.062052 | 2.2257e-05 | 1.4152e-05 | 0.36455 | 0.36455 | 0.36455 | 0.99472 | -0.10029 | 0.99462 | -0.10219 | 25.0377
59 | 0.020138 | 0.0050519 | -0.020131 | -0.0050474 | 7.4025e-06 | 4.4554e-06 | 0.030126 | 0.030127 | 0.030127 | 0.99472 | -0.10029 | 0.99432 | -0.108 | 8.2765
60 | -0.42825 | -0.10955 | 0.42895 | 0.10999 | 0.00069054 | 0.000441 | 0.63916 | 0.63916 | 0.63916 | 0.99824 | -0.033256 | 1 | 0 | 43.8984
61 | 0.24215 | 0.061733 | -0.24194 | -0.061596 | 0.00021646 | 0.00013763 | 0.36265 | 0.36265 | 0.36265 | 0.99462 | -0.10219 | 0.99365 | -0.12072 | 24.9072
62 | 0.017376 | 0.004357 | -0.017373 | -0.0043554 | 2.6047e-06 | 1.5338e-06 | 0.026004 | 0.026004 | 0.026004 | 0.99432 | -0.108 | 0.99415 | -0.11115 | 7.1439
63 | 0.036008 | 0.009049 | -0.035996 | -0.0090416 | 1.1843e-05 | 7.435e-06 | 0.053589 | 0.053589 | 0.053589 | 1 | 0 | 0.99964 | -0.0068918 | 14.7224
64 | 0.03302 | 0.0082955 | -0.033009 | -0.008289 | 1.0417e-05 | 6.5162e-06 | 0.049158 | 0.049158 | 0.049158 | 0.99964 | -0.0068918 | 0.9993 | -0.013504 | 13.5051
65 | 0.029615 | 0.0074384 | -0.029576 | -0.0074141 | 3.9087e-05 | 2.4314e-05 | 0.044105 | 0.044105 | 0.044105 | 0.9993 | -0.013504 | 0.99786 | -0.041201 | 12.1167
66 | -0.012002 | -0.003008 | 0.012003 | 0.0030085 | 9.6403e-07 | 5.1227e-07 | 0.017903 | 0.017903 | 0.017903 | 0.99753 | -0.047459 | 0.99762 | -0.045773 | 4.9185
67 | 0.01586 | 0.0039764 | -0.015857 | -0.0039744 | 3.4544e-06 | 1.9957e-06 | 0.023652 | 0.023652 | 0.023652 | 0.99786 | -0.041201 | 0.99762 | -0.045773 | 6.4977
68 | 0.010028 | 0.0025136 | -0.010027 | -0.0025131 | 9.3692e-07 | 4.537e-07 | 0.014955 | 0.014955 | 0.014955 | 0.99786 | -0.041201 | 0.99775 | -0.043163 | 4.1084
69 | 0.0056517 | 0.0014164 | -0.0056515 | -0.0014164 | 1.8369e-07 | 2.7516e-08 | 0.0084288 | 0.0084288 | 0.0084288 | 0.99775 | -0.043163 | 0.99772 | -0.043845 | 2.3156
70 | 0.23974 | 0.061046 | -0.23935 | -0.060796 | 0.00039123 | 0.00024997 | 0.35936 | 0.35937 | 0.35937 | 0.99365 | -0.12072 | 0.99188 | -0.15462 | 49.3633
71 | 0.014574 | 0.003654 | -0.014573 | -0.0036532 | 1.5392e-06 | 8.7326e-07 | 0.021815 | 0.021815 | 0.021815 | 0.99415 | -0.11115 | 0.99404 | -0.11337 | 5.9931
72 | 0.013104 | 0.003285 | -0.013103 | -0.0032843 | 1.1732e-06 | 6.4547e-07 | 0.019616 | 0.019616 | 0.019616 | 0.99404 | -0.11337 | 0.99394 | -0.11525 | 5.389
73 | 0.011914 | 0.0029863 | -0.011913 | -0.0029859 | 8.4389e-07 | 4.4841e-07 | 0.017836 | 0.017836 | 0.017836 | 0.99394 | -0.11525 | 0.99387 | -0.11673 | 4.9
74 | 0.010214 | 0.0025601 | -0.010213 | -0.0025597 | 6.626e-07 | 3.2615e-07 | 0.015292 | 0.015292 | 0.015292 | 0.99387 | -0.11673 | 0.9938 | -0.11809 | 4.2012
75 | 0.12185 | 0.031013 | -0.12153 | -0.030809 | 0.00031895 | 0.0002038 | 0.18297 | 0.18297 | 0.18297 | 0.99188 | -0.15462 | 0.98904 | -0.20907 | 50.2672
76 | 0.1175 | 0.029783 | -0.11731 | -0.029662 | 0.00019047 | 0.00012169 | 0.17639 | 0.17639 | 0.17639 | 0.99188 | -0.15462 | 0.99012 | -0.18841 | 48.4595
77 | 0.0089522 | 0.0022437 | -0.0089511 | -0.0022432 | 1.1376e-06 | 5.0933e-07 | 0.013404 | 0.013404 | 0.013404 | 0.9938 | -0.11809 | 0.99366 | -0.12076 | 3.6825
78 | 0.0058287 | 0.0014607 | -0.0058284 | -0.0014606 | 2.9343e-07 | 5.4762e-08 | 0.0087285 | 0.0087285 | 0.0087285 | 0.99366 | -0.12076 | 0.9936 | -0.12182 | 2.3979
79 | 0.0028445 | 0.00071279 | -0.0028445 | -0.00071289 | 7.2954e-08 | -9.2156e-08 | 0.0042599 | 0.00426 | 0.00426 | 0.9936 | -0.12182 | 0.99358 | -0.12236 | 1.1703
80 | 0.0067585 | 0.0016938 | -0.006757 | -0.0016933 | 1.5364e-06 | 4.7526e-07 | 0.01017 | 0.01017 | 0.01017 | 0.98887 | -0.21264 | 0.98862 | -0.21741 | 2.794
81 | -0.010065 | -0.0025224 | 0.010067 | 0.0025238 | 2.859e-06 | 1.4032e-06 | 0.015145 | 0.015145 | 0.015145 | 0.98887 | -0.21264 | 0.98917 | -0.20668 | 4.1607
82 | 0.0029951 | 0.00075051 | -0.002995 | -0.00075061 | 1.0145e-07 | -1.0576e-07 | 0.004508 | 0.004508 | 0.004508 | 0.98862 | -0.21741 | 0.98858 | -0.21813 | 1.2385
83 | -0.11484 | -0.029004 | 0.11494 | 0.029068 | 0.00010064 | 6.4291e-05 | 0.17283 | 0.17283 | 0.17283 | 0.98917 | -0.20668 | 0.99012 | -0.18841 | 47.4819
84 | 0.10477 | 0.02648 | -0.10467 | -0.026417 | 9.8748e-05 | 6.3063e-05 | 0.15769 | 0.15769 | 0.15769 | 0.98917 | -0.20668 | 0.98816 | -0.22636 | 43.3213
85 | 0.10329 | 0.026069 | -0.10306 | -0.025922 | 0.00023029 | 0.00014706 | 0.1556 | 0.1556 | 0.1556 | 0.98816 | -0.22636 | 0.98575 | -0.27302 | 42.7469
86 | 0.026363 | 0.0066174 | -0.026353 | -0.0066117 | 9.1183e-06 | 5.6401e-06 | 0.039799 | 0.039799 | 0.039799 | 0.98575 | -0.27302 | 0.98538 | -0.28027 | 10.9337
87 | 0.076693 | 0.019305 | -0.07663 | -0.019265 | 6.2908e-05 | 4.0102e-05 | 0.1158 | 0.1158 | 0.1158 | 0.98575 | -0.27302 | 0.98487 | -0.2902 | 31.8132
88 | 0.11764 | 0.029833 | -0.11758 | -0.029795 | 5.9929e-05 | 3.8289e-05 | 0.17711 | 0.17711 | 0.17711 | 0.98904 | -0.20907 | 0.98849 | -0.21967 | 48.6576
89 | 0.022947 | 0.0057579 | -0.022941 | -0.0057541 | 6.2034e-06 | 3.7948e-06 | 0.034654 | 0.034654 | 0.034654 | 0.98538 | -0.28027 | 0.98509 | -0.28595 | 9.5204
90 | 0.059839 | 0.015051 | -0.059771 | -0.015008 | 6.7496e-05 | 4.2918e-05 | 0.090428 | 0.090428 | 0.090428 | 0.98487 | -0.2902 | 0.98365 | -0.31384 | 24.843
91 | 0.016791 | 0.0042138 | -0.01678 | -0.0042068 | 1.1926e-05 | 7.0043e-06 | 0.025372 | 0.025372 | 0.025372 | 0.98487 | -0.2902 | 0.9841 | -0.3051 | 6.9703
92 | -0.0048757 | -0.0012219 | 0.0048759 | 0.0012219 | 2.6287e-07 | 4.7507e-09 | 0.0073767 | 0.0073767 | 0.0073767 | 0.98351 | -0.31671 | 0.98357 | -0.31557 | 2.0266
93 | 0.0020466 | 0.00051284 | -0.0020465 | -0.00051291 | 2.554e-08 | -7.3801e-08 | 0.0030964 | 0.0030964 | 0.0030964 | 0.98351 | -0.31671 | 0.9835 | -0.31697 | 0.85066
94 | -0.0070306 | -0.0017619 | 0.0070315 | 0.0017622 | 8.4456e-07 | 2.8783e-07 | 0.010636 | 0.010636 | 0.010636 | 0.98357 | -0.31557 | 0.9837 | -0.31305 | 2.9221
95 | -0.0090963 | -0.0022797 | 0.0090972 | 0.0022801 | 8.7748e-07 | 4.0467e-07 | 0.01376 | 0.01376 | 0.01376 | 0.9837 | -0.31305 | 0.9838 | -0.31103 | 3.7801
96 | -0.01335 | -0.003346 | 0.013351 | 0.0033466 | 1.1072e-06 | 6.1665e-07 | 0.020192 | 0.020192 | 0.020192 | 0.9838 | -0.31103 | 0.98389 | -0.30929 | 5.5474
97 | -0.015054 | -0.0037733 | 0.015057 | 0.0037751 | 3.0035e-06 | 1.726e-06 | 0.022768 | 0.022767 | 0.022768 | 0.98389 | -0.30929 | 0.9841 | -0.3051 | 6.2548
98 | 0.026505 | 0.0066604 | -0.026488 | -0.0066495 | 1.7632e-05 | 1.0913e-05 | 0.040102 | 0.040102 | 0.040102 | 0.98365 | -0.31384 | 0.98294 | -0.32778 | 11.0171
99 | 0.024947 | 0.0062634 | -0.024938 | -0.0062576 | 9.2913e-06 | 5.7264e-06 | 0.03777 | 0.03777 | 0.03777 | 0.98294 | -0.32778 | 0.98254 | -0.33559 | 10.3764
100 | 0.02335 | 0.0058598 | -0.02335 | -0.0058592 | 8.2407e-07 | 5.0515e-07 | 0.035366 | 0.035366 | 0.035366 | 0.98254 | -0.33559 | 0.9825 | -0.33633 | 9.7159
101 | 0.021805 | 0.0054722 | -0.021802 | -0.0054702 | 3.2437e-06 | 1.9756e-06 | 0.033027 | 0.033027 | 0.033027 | 0.9825 | -0.33633 | 0.98234 | -0.33945 | 9.0733
102 | 0.020521 | 0.0051492 | -0.020507 | -0.0051406 | 1.4121e-05 | 8.5443e-06 | 0.031087 | 0.031087 | 0.031087 | 0.98234 | -0.33945 | 0.9816 | -0.35389 | 8.5403
103 | 0.01679 | 0.0042092 | -0.016789 | -0.0042082 | 1.6508e-06 | 9.7064e-07 | 0.025453 | 0.025453 | 0.025453 | 0.9816 | -0.35389 | 0.9815 | -0.35596 | 6.9925
104 | 0.014722 | 0.0036903 | -0.01472 | -0.0036893 | 1.7489e-06 | 1.001e-06 | 0.02232 | 0.02232 | 0.02232 | 0.9815 | -0.35596 | 0.98137 | -0.35845 | 6.1319
105 | 0.020862 | 0.0052333 | -0.020854 | -0.0052283 | 8.2685e-06 | 5.0093e-06 | 0.031515 | 0.031515 | 0.031515 | 0.98509 | -0.28595 | 0.98466 | -0.29426 | 8.658
106 | 0.016853 | 0.0042256 | -0.01685 | -0.0042236 | 3.4867e-06 | 2.0492e-06 | 0.025469 | 0.025469 | 0.025469 | 0.98466 | -0.29426 | 0.98444 | -0.2986 | 6.9971
107 | 0.012425 | 0.0031146 | -0.012424 | -0.0031139 | 1.2892e-06 | 7.0119e-07 | 0.018781 | 0.018781 | 0.018781 | 0.98444 | -0.2986 | 0.98433 | -0.30078 | 5.1596
108 | 0.0081577 | 0.0020447 | -0.0081563 | -0.0020442 | 1.3635e-06 | 5.6878e-07 | 0.012332 | 0.012332 | 0.012332 | 0.98433 | -0.30078 | 0.98415 | -0.30429 | 3.388
109 | 0.003858 | 0.0009669 | -0.003858 | -0.00096691 | 2.4326e-08 | -8.655e-09 | 0.0058333 | 0.0058333 | 0.0058333 | 0.98415 | -0.30429 | 0.98414 | -0.30442 | 1.6026
110 | 0.11535 | 0.029237 | -0.11519 | -0.029131 | 0.00016622 | 0.00010619 | 0.17376 | 0.17376 | 0.17376 | 0.98849 | -0.21967 | 0.98694 | -0.24971 | 47.7372
111 | 0.11263 | 0.02849 | -0.11247 | -0.028386 | 0.00016286 | 0.00010404 | 0.16991 | 0.16991 | 0.16991 | 0.98694 | -0.24971 | 0.98538 | -0.2799 | 46.678
112 | 0.1088 | 0.027465 | -0.10865 | -0.027372 | 0.00014598 | 9.3241e-05 | 0.16436 | 0.16436 | 0.16436 | 0.98538 | -0.2799 | 0.98393 | -0.30794 | 45.1549
113 | 0.10347 | 0.026074 | -0.10338 | -0.026014 | 9.3405e-05 | 5.965e-05 | 0.15653 | 0.15653 | 0.15653 | 0.98393 | -0.30794 | 0.98296 | -0.32683 | 43.0029
114 | 0.016987 | 0.0042585 | -0.016986 | -0.0042577 | 1.32e-06 | 7.7765e-07 | 0.025744 | 0.025744 | 0.025744 | 0.98188 | -0.34797 | 0.9818 | -0.3496 | 7.0724
115 | -0.022813 | -0.0057187 | 0.022817 | 0.0057207 | 3.2143e-06 | 1.9664e-06 | 0.034573 | 0.034573 | 0.034573 | 0.98188 | -0.34797 | 0.98203 | -0.34501 | 9.4982
116 | 0.014152 | 0.0035475 | -0.01415 | -0.0035467 | 1.2764e-06 | 7.2336e-07 | 0.021449 | 0.021449 | 0.021449 | 0.9818 | -0.3496 | 0.9817 | -0.35149 | 5.8925
117 | -0.025945 | -0.0065047 | 0.025953 | 0.0065099 | 8.4207e-06 | 5.2054e-06 | 0.039313 | 0.039313 | 0.039313 | 0.98203 | -0.34501 | 0.98238 | -0.3382 | 10.8003
118 | 0.011234 | 0.0028158 | -0.011233 | -0.0028153 | 9.5274e-07 | 4.9898e-07 | 0.017028 | 0.017028 | 0.017028 | 0.9817 | -0.35149 | 0.98161 | -0.35327 | 4.678
119 | 0.053855 | 0.013578 | -0.053826 | -0.01356 | 2.856e-05 | 1.8133e-05 | 0.081603 | 0.081603 | 0.081603 | 0.98238 | -0.3382 | 0.98181 | -0.34929 | 22.4185
120 | -0.079808 | -0.020088 | 0.079851 | 0.020115 | 4.3391e-05 | 2.767e-05 | 0.12092 | 0.12092 | 0.12092 | 0.98238 | -0.3382 | 0.98296 | -0.32683 | 33.2188
121 | 0.0081032 | 0.0020309 | -0.0081025 | -0.0020306 | 6.217e-07 | 2.59e-07 | 0.012284 | 0.012284 | 0.012284 | 0.98161 | -0.35327 | 0.98153 | -0.35488 | 3.3746
122 | 0.050387 | 0.012698 | -0.050349 | -0.012674 | 3.7209e-05 | 2.3599e-05 | 0.07639 | 0.07639 | 0.07639 | 0.98181 | -0.34929 | 0.98102 | -0.36474 | 20.9863
123 | 0.023526 | 0.005899 | -0.023521 | -0.005896 | 5.0346e-06 | 3.088e-06 | 0.035614 | 0.035614 | 0.035614 | 0.98296 | -0.32683 | 0.98273 | -0.33133 | 9.7842
124 | 0.0041553 | 0.0010414 | -0.0041552 | -0.0010414 | 9.7341e-08 | -2.0373e-08 | 0.0062995 | 0.0062995 | 0.0062995 | 0.98153 | -0.35488 | 0.9815 | -0.35537 | 1.7306
125 | 0.019853 | 0.0049769 | -0.019853 | -0.0049765 | 5.2526e-07 | 3.1653e-07 | 0.030062 | 0.030062 | 0.030062 | 0.98273 | -0.33133 | 0.98271 | -0.33188 | 8.2587
126 | 0.016031 | 0.0040186 | -0.016028 | -0.0040171 | 2.6645e-06 | 1.5525e-06 | 0.024274 | 0.024274 | 0.024274 | 0.98271 | -0.33188 | 0.98253 | -0.33537 | 6.6688
127 | 0.0080663 | 0.0020216 | -0.0080659 | -0.0020215 | 3.3053e-07 | 1.3674e-07 | 0.012216 | 0.012216 | 0.012216 | 0.98253 | -0.33537 | 0.98248 | -0.33623 | 3.3561
128 | 0.0079619 | 0.0019955 | -0.0079605 | -0.0019949 | 1.357e-06 | 5.5335e-07 | 0.012058 | 0.012058 | 0.012058 | 0.98253 | -0.33537 | 0.98234 | -0.33895 | 3.3127
129 | -0.0040753 | -0.0010213 | 0.0040755 | 0.0010212 | 2.1856e-07 | -5.3723e-08 | 0.0061734 | 0.0061733 | 0.0061734 | 0.98229 | -0.34007 | 0.98234 | -0.33895 | 1.696
130 | 0.0014708 | 0.00036856 | -0.0014708 | -0.00036862 | 8.4511e-09 | -5.2059e-08 | 0.002228 | 0.002228 | 0.002228 | 0.98229 | -0.34007 | 0.98228 | -0.34019 | 0.6121
131 | 0.0038746 | 0.00097102 | -0.0038745 | -0.00097105 | 7.7915e-08 | -2.6539e-08 | 0.0058683 | 0.0058683 | 0.0058683 | 0.98248 | -0.33623 | 0.98246 | -0.33665 | 1.6122
132 | 0.042915 | 0.010775 | -0.042913 | -0.010773 | 2.6531e-06 | 1.6776e-06 | 0.065602 | 0.065602 | 0.065602 | 0.97353 | -0.50982 | 0.97346 | -0.51112 | 18.0226
133 | 0.03563 | 0.0089481 | -0.0356 | -0.0089292 | 3.0019e-05 | 1.8877e-05 | 0.054471 | 0.054471 | 0.054471 | 0.97346 | -0.51112 | 0.97257 | -0.52879 | 14.9645
134 | 0.033144 | 0.0083137 | -0.033143 | -0.0083129 | 1.2117e-06 | 7.599e-07 | 0.050713 | 0.050713 | 0.050713 | 0.97257 | -0.52879 | 0.97253 | -0.52956 | 13.9321
135 | 0.028313 | 0.0071023 | -0.028309 | -0.0070996 | 4.3209e-06 | 2.6892e-06 | 0.043322 | 0.043322 | 0.043322 | 0.97253 | -0.52956 | 0.97237 | -0.53276 | 11.9018
136 | 0.02616 | 0.0065612 | -0.026156 | -0.0065586 | 4.1384e-06 | 2.5632e-06 | 0.040035 | 0.040035 | 0.040035 | 0.97237 | -0.53276 | 0.9722 | -0.53608 | 10.9985
137 | 0.023998 | 0.0060179 | -0.023997 | -0.0060168 | 1.8444e-06 | 1.1352e-06 | 0.036732 | 0.036732 | 0.036732 | 0.9722 | -0.53608 | 0.97212 | -0.53769 | 10.0913
138 | 0.021193 | 0.0053142 | -0.021192 | -0.0053134 | 1.3306e-06 | 8.0979e-07 | 0.032442 | 0.032442 | 0.032442 | 0.97212 | -0.53769 | 0.97205 | -0.53901 | 8.9126
139 | 0.018951 | 0.0047516 | -0.018948 | -0.0047503 | 2.2945e-06 | 1.3784e-06 | 0.02901 | 0.02901 | 0.02901 | 0.97205 | -0.53901 | 0.97192 | -0.54155 | 7.9699
140 | 0.016572 | 0.0041546 | -0.01657 | -0.0041537 | 1.5582e-06 | 9.1725e-07 | 0.025372 | 0.025372 | 0.025372 | 0.97192 | -0.54155 | 0.97182 | -0.54352 | 6.9703
141 | 0.013578 | 0.0034038 | -0.013575 | -0.0034023 | 2.5392e-06 | 1.431e-06 | 0.02079 | 0.02079 | 0.02079 | 0.97182 | -0.54352 | 0.97162 | -0.54745 | 5.7116
142 | 0.010889 | 0.0027291 | -0.010889 | -0.0027289 | 4.3365e-07 | 2.2604e-07 | 0.016676 | 0.016676 | 0.016676 | 0.97162 | -0.54745 | 0.97158 | -0.54828 | 4.5814
143 | 0.00243 | 0.00060896 | -0.00243 | -0.00060901 | 2.8771e-08 | -5.0184e-08 | 0.0037217 | 0.0037217 | 0.0037217 | 0.97158 | -0.54828 | 0.97157 | -0.54853 | 1.0224

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.46998 | 0.11989

## res_load
| p_mw | q_mvar
0 | 0.0043641 | 0.0010937
1 | 0.0053895 | 0.0013507
2 | 0.0089931 | 0.0022539
3 | 0.0014715 | 0.00036879
4 | 0.0027187 | 0.00068136
5 | 0.0037766 | 0.00094651
6 | 0.0020825 | 0.00052193
7 | 0.0019584 | 0.00049081
8 | 0.0015572 | 0.00039028
9 | 0.0043249 | 0.0010839
10 | 0.0043439 | 0.0010887
11 | 0.0025614 | 0.00064194
12 | 0.0053699 | 0.0013458
13 | 0.0032147 | 0.00080568
14 | 0.0043366 | 0.0010869
15 | 0.0023798 | 0.00059645
16 | 0.0044636 | 0.0011187
17 | 0.0023759 | 0.00059545
18 | 0.0015857 | 0.00039743
19 | 0.0069466 | 0.001741
20 | 0.0053511 | 0.0013411
21 | 0.0038869 | 0.00097416
22 | 0.0059407 | 0.0014889
23 | 0.0029437 | 0.00073775
24 | 0.022167 | 0.0055557
25 | 0.0026426 | 0.00066231
26 | 0.0025585 | 0.00064122
27 | 0.0062659 | 0.0015704
28 | 0.0027559 | 0.00069071
29 | 0.0019806 | 0.00049638
30 | 0.0039972 | 0.0010018
31 | 0.0064656 | 0.0016204
32 | 0.002649 | 0.00066389
33 | 0.0022291 | 0.00055867
34 | 0.011288 | 0.0028291
35 | 0.001942 | 0.00048671
36 | 0.0018223 | 0.00045672
37 | 0.0013922 | 0.00034892
38 | 0.00096546 | 0.00024197
39 | 0.0042408 | 0.0010628
40 | 0.0031021 | 0.00077747
41 | 0.0018128 | 0.00045433
42 | 0.0031131 | 0.00078023
43 | 0.0048349 | 0.0012117
44 | 0.0032077 | 0.00080394
45 | 0.0043482 | 0.0010898
46 | 0.0020752 | 0.00052011
47 | 0.0012695 | 0.00031817
48 | 0.0027549 | 0.00069045
49 | 0.0033721 | 0.00084512
50 | 0.0029768 | 0.00074604
51 | 0.003394 | 0.00085061
52 | 0.0040527 | 0.0010157
53 | 0.0036873 | 0.00092413
54 | 0.0043758 | 0.0010967
55 | 0.0056515 | 0.0014164
56 | 0.003854 | 0.00096591
57 | 0.0021933 | 0.0005497
58 | 0.0027986 | 0.0007014
59 | 0.0014691 | 0.00036819
60 | 0.001189 | 0.00029799
61 | 0.001699 | 0.00042581
62 | 0.0012609 | 0.00031602
63 | 0.0031224 | 0.00078255
64 | 0.0029838 | 0.00074782
65 | 0.0028445 | 0.00071289
66 | 0.003306 | 0.00082857
67 | 0.0037619 | 0.00094282
68 | 0.002995 | 0.00075061
69 | 0.0023679 | 0.00059344
70 | 0.0013887 | 0.00034803
71 | 0.0038943 | 0.000976
72 | 0.0034067 | 0.0008538
73 | 0.0028291 | 0.00070904
74 | 0.0021547 | 0.00054001
75 | 0.0020465 | 0.00051291
76 | 0.0020648 | 0.0005175
77 | 0.004253 | 0.0010659
78 | 0.0017027 | 0.00042675
79 | 0.0017225 | 0.00043171
80 | 0.0015406 | 0.0003861
81 | 0.0015876 | 0.00039788
82 | 0.0015444 | 0.00038707
83 | 0.0012809 | 0.00032103
84 | 0.0037166 | 0.00093147
85 | 0.0020665 | 0.00051791
86 | 0.01472 | 0.0036893
87 | 0.0020782 | 0.00052085
88 | 0.0040006 | 0.0010027
89 | 0.004425 | 0.001109
90 | 0.0042659 | 0.0010691
91 | 0.0042983 | 0.0010773
92 | 0.003858 | 0.00096691
93 | 0.0022257 | 0.00055781
94 | 0.0025572 | 0.0006409
95 | 0.0036714 | 0.00092013
96 | 0.0051796 | 0.0012981
97 | 0.0058264 | 0.0014602
98 | 0.0028339 | 0.00071025
99 | 0.0031281 | 0.00078397
100 | 0.0029165 | 0.00073093
101 | 0.0031298 | 0.0007844
102 | 0.0034398 | 0.00086209
103 | 0.0039472 | 0.00098927
104 | 0.0026882 | 0.00067372
105 | 0.0036672 | 0.00091909
106 | 0.0038221 | 0.0009579
107 | 0.0041552 | 0.0010414
108 | 0.0045814 | 0.0011482
109 | 0.0026045 | 0.00065274
110 | 0.0038851 | 0.00097369
111 | 0.0014708 | 0.00036862
112 | 0.0041913 | 0.0010504
113 | 0.0038745 | 0.00097105
114 | 0.012674 | 0.0031764
115 | 0.0072823 | 0.0018251
116 | 0.0024561 | 0.00061556
117 | 0.0048302 | 0.0012106
118 | 0.0021485 | 0.00053845
119 | 0.0021575 | 0.00054073
120 | 0.0028031 | 0.00070252
121 | 0.0022416 | 0.00056179
122 | 0.0023766 | 0.00059564
123 | 0.0029923 | 0.00074994
124 | 0.0026861 | 0.00067321
125 | 0.0084587 | 0.0021199
126 | 0.00243 | 0.00060901

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1