## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5225-4_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5225-4_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5225-4_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5225-4_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5225-4_0_4_node_9 | 0.4 | n |  | TRUE
5 | bus_LV_5225-4_0_4_node_4 | 0.4 | n |  | TRUE
6 | bus_LV_5225-4_0_4_node_5 | 0.4 | n |  | TRUE
7 | bus_LV_5225-4_0_4_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_5225-4_0_4_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5225-4_0_4_node_17 | 0.4 | n |  | TRUE
10 | bus_LV_5225-4_0_4_node_18 | 0.4 | n |  | TRUE
11 | bus_LV_5225-4_0_4_node_19 | 0.4 | n |  | TRUE
12 | bus_LV_5225-4_0_4_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_5225-4_0_4_node_36 | 0.4 | n |  | TRUE
14 | bus_LV_5225-4_0_4_node_20 | 0.4 | n |  | TRUE
15 | bus_LV_5225-4_0_4_node_15 | 0.4 | n |  | TRUE
16 | bus_LV_5225-4_0_4_node_8 | 0.4 | n |  | TRUE
17 | bus_LV_5225-4_0_4_node_10 | 0.4 | n |  | TRUE
18 | bus_LV_5225-4_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_5225-4_0_4_node_12 | 0.4 | n |  | TRUE
20 | bus_LV_5225-4_0_4_node_11 | 0.4 | n |  | TRUE
21 | bus_LV_5225-4_0_4_node_61 | 0.4 | n |  | TRUE
22 | bus_LV_5225-4_0_4_node_60 | 0.4 | n |  | TRUE
23 | bus_LV_5225-4_0_4_node_13 | 0.4 | n |  | TRUE
24 | bus_LV_5225-4_0_4_node_59 | 0.4 | n |  | TRUE
25 | bus_LV_5225-4_0_4_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_5225-4_0_4_node_22 | 0.4 | n |  | TRUE
27 | bus_LV_5225-4_0_4_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_5225-4_0_4_node_24 | 0.4 | n |  | TRUE
29 | bus_LV_5225-4_0_4_node_25 | 0.4 | n |  | TRUE
30 | bus_LV_5225-4_0_4_node_26 | 0.4 | n |  | TRUE
31 | bus_LV_5225-4_0_4_node_30 | 0.4 | n |  | TRUE
32 | bus_LV_5225-4_0_4_node_35 | 0.4 | n |  | TRUE
33 | bus_LV_5225-4_0_4_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_5225-4_0_4_node_31 | 0.4 | n |  | TRUE
35 | bus_LV_5225-4_0_4_node_34 | 0.4 | n |  | TRUE
36 | bus_LV_5225-4_0_4_node_28 | 0.4 | n |  | TRUE
37 | bus_LV_5225-4_0_4_node_29 | 0.4 | n |  | TRUE
38 | bus_LV_5225-4_0_4_node_58 | 0.4 | n |  | TRUE
39 | bus_LV_5225-4_0_4_node_57 | 0.4 | n |  | TRUE
40 | bus_LV_5225-4_0_4_node_32 | 0.4 | n |  | TRUE
41 | bus_LV_5225-4_0_4_node_33 | 0.4 | n |  | TRUE
42 | bus_LV_5225-4_0_4_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_5225-4_0_4_node_40 | 0.4 | n |  | TRUE
44 | bus_LV_5225-4_0_4_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_5225-4_0_4_node_42 | 0.4 | n |  | TRUE
46 | bus_LV_5225-4_0_4_node_43 | 0.4 | n |  | TRUE
47 | bus_LV_5225-4_0_4_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_5225-4_0_4_node_45 | 0.4 | n |  | TRUE
49 | bus_LV_5225-4_0_4_node_50 | 0.4 | n |  | TRUE
50 | bus_LV_5225-4_0_4_node_48 | 0.4 | n |  | TRUE
51 | bus_LV_5225-4_0_4_node_46 | 0.4 | n |  | TRUE
52 | bus_LV_5225-4_0_4_node_47 | 0.4 | n |  | TRUE
53 | bus_LV_5225-4_0_4_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_5225-4_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_5225-4_0_4_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_5225-4_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_5225-4_0_4_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_5225-4_0_4_node_53 | 0.4 | n |  | TRUE
59 | bus_LV_5225-4_0_4_node_55 | 0.4 | n |  | TRUE
60 | bus_MV_254_0_node_87 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5225-4_0_4_load_0 | 0 | 0.0077125 | 0.0019329 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5225-4_0_4_load_1 | 1 | 0.0034849 | 0.00087341 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5225-4_0_4_load_2 | 2 | 0.0041349 | 0.0010363 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5225-4_0_4_load_7 | 7 | 0.0059444 | 0.0014898 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5225-4_0_4_load_6 | 8 | 0.0049196 | 0.001233 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5225-4_0_4_load_18 | 10 | 0.011665 | 0.0029235 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5225-4_0_4_load_19 | 11 | 0.0069471 | 0.0017411 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5225-4_0_4_load_16 | 12 | 0.0038021 | 0.00095289 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5225-4_0_4_load_36 | 13 | 0.076735 | 0.019232 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5225-4_0_4_load_15 | 15 | 0.00339 | 0.0008496 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5225-4_0_4_load_14 | 18 | 0.014466 | 0.0036256 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5225-4_0_4_load_12 | 19 | 0.0040795 | 0.0010224 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5225-4_0_4_load_11 | 20 | 0.0060718 | 0.0015217 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5225-4_0_4_load_61 | 21 | 0.005807 | 0.0014554 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5225-4_0_4_load_60 | 22 | 0.0090108 | 0.0022583 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5225-4_0_4_load_13 | 23 | 0.0057552 | 0.0014424 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5225-4_0_4_load_59 | 24 | 0.0082159 | 0.0020591 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5225-4_0_4_load_22 | 26 | 0.0048165 | 0.0012071 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5225-4_0_4_load_23 | 27 | 0.0034128 | 0.00085533 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5225-4_0_4_load_24 | 28 | 0.024456 | 0.0061293 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5225-4_0_4_load_25 | 29 | 0.0023355 | 0.00058534 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5225-4_0_4_load_26 | 30 | 0.0038342 | 0.00096095 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5225-4_0_4_load_30 | 31 | 0.0059029 | 0.0014794 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5225-4_0_4_load_35 | 32 | 0.0032243 | 0.00080809 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5225-4_0_4_load_34 | 35 | 0.0055065 | 0.0013801 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5225-4_0_4_load_29 | 37 | 0.0054531 | 0.0013667 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5225-4_0_4_load_58 | 38 | 0.0098663 | 0.0024727 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5225-4_0_4_load_57 | 39 | 0.0058939 | 0.0014771 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5225-4_0_4_load_32 | 40 | 0.0031444 | 0.00078807 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5225-4_0_4_load_33 | 41 | 0.024179 | 0.0060597 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5225-4_0_4_load_39 | 42 | 0.0019649 | 0.00049245 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5225-4_0_4_load_40 | 43 | 0.0014502 | 0.00036347 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5225-4_0_4_load_41 | 44 | 0.0012922 | 0.00032384 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5225-4_0_4_load_42 | 45 | 0.0046141 | 0.0011564 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5225-4_0_4_load_43 | 46 | 0.0021138 | 0.00052977 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5225-4_0_4_load_44 | 47 | 0.0016237 | 0.00040693 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5225-4_0_4_load_45 | 48 | 0.004069 | 0.0010198 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5225-4_0_4_load_50 | 49 | 0.0060269 | 0.0015105 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5225-4_0_4_load_48 | 50 | 0.0023756 | 0.00059539 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5225-4_0_4_load_46 | 51 | 0.0098233 | 0.002462 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5225-4_0_4_load_47 | 52 | 0.008064 | 0.002021 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5225-4_0_4_load_49 | 53 | 0.033278 | 0.0083402 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5225-4_0_4_load_51 | 54 | 0.0074882 | 0.0018767 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5225-4_0_4_load_52 | 55 | 0.012963 | 0.0032488 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5225-4_0_4_load_56 | 56 | 0.012898 | 0.0032325 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5225-4_0_4_load_54 | 57 | 0.0064897 | 0.0016265 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5225-4_0_4_load_53 | 58 | 0.010213 | 0.0025597 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5225-4_0_4_load_55 | 59 | 0.0060227 | 0.0015094 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 26 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5225-4_0_4_line_0 |  | 0 | 1 | 0.0081372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5225-4_0_4_line_1 |  | 0 | 2 | 0.012851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5225-4_0_4_line_2 |  | 1 | 3 | 0.013176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5225-4_0_4_line_3 |  | 2 | 4 | 0.10271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5225-4_0_4_line_4 |  | 3 | 5 | 0.031756 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5225-4_0_4_line_5 |  | 3 | 6 | 0.049628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
6 | LV_5225-4_0_4_line_6 |  | 4 | 7 | 0.033384 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5225-4_0_4_line_7 |  | 5 | 9 | 0.021443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5225-4_0_4_line_8 |  | 5 | 10 | 0.024583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5225-4_0_4_line_9 |  | 6 | 11 | 0.0097898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
10 | LV_5225-4_0_4_line_10 |  | 6 | 12 | 0.012628 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5225-4_0_4_line_11 |  | 7 | 8 | 0.028014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5225-4_0_4_line_12 |  | 8 | 16 | 0.021652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5225-4_0_4_line_13 |  | 9 | 13 | 0.027457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5225-4_0_4_line_14 |  | 11 | 14 | 0.020428 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
15 | LV_5225-4_0_4_line_15 |  | 12 | 15 | 0.0087553 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5225-4_0_4_line_16 |  | 14 | 25 | 0.013883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_5225-4_0_4_line_17 |  | 14 | 26 | 0.031897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
18 | LV_5225-4_0_4_line_18 |  | 15 | 23 | 0.012592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5225-4_0_4_line_19 |  | 16 | 17 | 0.0258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5225-4_0_4_line_20 |  | 17 | 20 | 0.025182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5225-4_0_4_line_21 |  | 18 | 19 | 0.0067855 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5225-4_0_4_line_22 |  | 19 | 23 | 0.013619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5225-4_0_4_line_23 |  | 20 | 21 | 0.018589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5225-4_0_4_line_24 |  | 21 | 22 | 0.020371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5225-4_0_4_line_25 |  | 22 | 24 | 0.022108 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5225-4_0_4_line_26 |  | 25 | 27 | 0.0096483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5225-4_0_4_line_27 |  | 25 | 28 | 0.033569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
28 | LV_5225-4_0_4_line_28 |  | 26 | 29 | 0.011459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5225-4_0_4_line_29 |  | 27 | 30 | 0.010809 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5225-4_0_4_line_30 |  | 28 | 31 | 0.0033265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5225-4_0_4_line_31 |  | 29 | 32 | 9.4152e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5225-4_0_4_line_32 |  | 30 | 33 | 0.010879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5225-4_0_4_line_33 |  | 31 | 34 | 0.049372 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5225-4_0_4_line_34 |  | 32 | 35 | 0.00071887 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5225-4_0_4_line_35 |  | 33 | 36 | 0.053477 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5225-4_0_4_line_36 |  | 34 | 40 | 0.035217 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5225-4_0_4_line_37 |  | 34 | 41 | 0.022051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5225-4_0_4_line_38 |  | 36 | 37 | 0.009266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5225-4_0_4_line_39 |  | 37 | 38 | 0.018411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5225-4_0_4_line_40 |  | 38 | 39 | 0.0062991 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5225-4_0_4_line_41 |  | 39 | 59 | 0.01182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5225-4_0_4_line_42 |  | 40 | 42 | 0.016173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5225-4_0_4_line_43 |  | 42 | 43 | 0.016684 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5225-4_0_4_line_44 |  | 43 | 44 | 0.0091306 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5225-4_0_4_line_45 |  | 44 | 45 | 0.027631 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5225-4_0_4_line_46 |  | 45 | 46 | 0.036544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5225-4_0_4_line_47 |  | 46 | 47 | 0.0055388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5225-4_0_4_line_48 |  | 47 | 48 | 0.020052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5225-4_0_4_line_49 |  | 48 | 49 | 1.9502e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5225-4_0_4_line_50 |  | 49 | 50 | 0.059771 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5225-4_0_4_line_51 |  | 50 | 51 | 0.0081591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5225-4_0_4_line_52 |  | 51 | 52 | 0.018491 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5225-4_0_4_line_53 |  | 52 | 53 | 0.0095285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5225-4_0_4_line_54 |  | 54 | 55 | 0.012388 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5225-4_0_4_line_55 |  | 54 | 56 | 0.050153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5225-4_0_4_line_56 |  | 56 | 57 | 0.011907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5225-4_0_4_line_57 |  | 57 | 58 | 0.0054715 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5225-4_0_4_line_58 |  | 58 | 59 | 0.0045852 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5225-4_0_4_trafo_22 | 0.63 MVA 20/0.4 kV | 60 | 26 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2715763.4959 | 1095584.4204 | 2715757.6305 | 1095590.0605
1 | 2715772.7593 | 1095575.5128 | 2715763.4959 | 1095584.4204
2 | 2715748.1326 | 1095599.1935 | 2715757.6305 | 1095590.0605
3 | 2715772.7593 | 1095575.5128 | 2715865.8342 | 1095532.0893
4 | 2715770.3639 | 1095621.9323 | 2715748.1326 | 1095599.1935
5 | 2715748.1326 | 1095599.1935 | 2715738.3356 | 1095589.9896 | 2715721.7524 | 1095574.1854 | 2715711.0144 | 1095566.3756
6 | 2715865.8342 | 1095532.0893 | 2715861.8189 | 1095498.9472
7 | 2715770.3639 | 1095621.9323 | 2715766.2085 | 1095626.523 | 2715762.6725 | 1095627.0672 | 2715757.8664 | 1095625.9527 | 2715752.8312 | 1095621.4093
8 | 2715770.3639 | 1095621.9323 | 2715774.7952 | 1095626.0418 | 2715784.8705 | 1095634.0613 | 2715790.3108 | 1095635.6305
9 | 2715711.0144 | 1095566.3756 | 2715702.3319 | 1095561.853
10 | 2715711.0144 | 1095566.3756 | 2715717.4794 | 1095555.5276
11 | 2715858.4495 | 1095471.1368 | 2715861.8189 | 1095498.9472
12 | 2715855.8453 | 1095449.6424 | 2715858.4495 | 1095471.1368
13 | 2715752.8312 | 1095621.4093 | 2715732.6292 | 1095640.0046
14 | 2715683.7277 | 1095553.5588 | 2715691.2961 | 1095556.1045 | 2715702.3319 | 1095561.853
15 | 2715721.9616 | 1095548.0067 | 2715717.4794 | 1095555.5276
16 | 2715670.1193 | 1095554.8785 | 2715677.5035 | 1095552.851 | 2715683.7277 | 1095553.5588
17 | 2715683.7277 | 1095553.5588 | 2715689.3694 | 1095522.1643
18 | 2715728.408 | 1095537.1899 | 2715721.9616 | 1095548.0067
19 | 2715851.8369 | 1095424.1597 | 2715855.8453 | 1095449.6424
20 | 2715851.8369 | 1095424.1597 | 2715847.4235 | 1095399.3677
21 | 2715738.8538 | 1095519.6624 | 2715735.38 | 1095525.4913
22 | 2715735.38 | 1095525.4913 | 2715728.408 | 1095537.1899
23 | 2715847.4235 | 1095399.3677 | 2715846.7625 | 1095395.6546 | 2715843.4536 | 1095381.2113
24 | 2715843.4536 | 1095381.2113 | 2715838.9046 | 1095361.3547
25 | 2715833.7161 | 1095339.8653 | 2715836.8691 | 1095352.4698 | 2715838.9046 | 1095361.3547
26 | 2715670.1193 | 1095554.8785 | 2715661.3627 | 1095558.9296
27 | 2715670.1193 | 1095554.8785 | 2715654.3196 | 1095543.4924 | 2715646.5687 | 1095535.4728 | 2715644.9801 | 1095532.9978
28 | 2715689.3694 | 1095522.1643 | 2715689.7772 | 1095519.8952 | 2715687.4762 | 1095511.036
29 | 2715651.5528 | 1095563.4678 | 2715661.3627 | 1095558.9296
30 | 2715644.9801 | 1095532.9978 | 2715643.1834 | 1095530.1983
31 | 2715687.4525 | 1095510.9449 | 2715687.4525 | 1095510.9449 | 2715687.4762 | 1095511.036
32 | 2715641.6794 | 1095568.0355 | 2715651.5528 | 1095563.4678
33 | 2715622.7388 | 1095485.9413 | 2715622.8926 | 1095490.892 | 2715624.2151 | 1095495.9095 | 2715631.41 | 1095510.7565 | 2715639.7054 | 1095524.7794 | 2715643.1834 | 1095530.1983
34 | 2715688.0517 | 1095510.5477 | 2715687.4525 | 1095510.9449
35 | 2715641.6794 | 1095568.0355 | 2715642.7301 | 1095589.7815 | 2715640.2444 | 1095611.2711 | 2715638.9002 | 1095621.2413
36 | 2715622.7388 | 1095485.9413 | 2715590.024 | 1095472.9035
37 | 2715633.4926 | 1095466.8772 | 2715623.6385 | 1095482.2336 | 2715622.7388 | 1095485.9413
38 | 2715638.9002 | 1095621.2413 | 2715645.76 | 1095627.4704
39 | 2715659.3903 | 1095639.8474 | 2715645.76 | 1095627.4704
40 | 2715659.3903 | 1095639.8474 | 2715664.0536 | 1095644.082
41 | 2715664.0536 | 1095644.082 | 2715672.8043 | 1095652.0281
42 | 2715575.0005 | 1095466.9161 | 2715590.024 | 1095472.9035
43 | 2715559.5021 | 1095460.7396 | 2715575.0005 | 1095466.9161
44 | 2715559.5021 | 1095460.7396 | 2715551.7795 | 1095457.6619 | 2715551.1048 | 1095457.2007
45 | 2715551.1048 | 1095457.2007 | 2715541.1546 | 1095450.3995 | 2715534.8126 | 1095442.8404 | 2715532.1374 | 1095437.7948
46 | 2715532.1374 | 1095437.7948 | 2715515.0189 | 1095405.5082
47 | 2715515.0189 | 1095405.5082 | 2715512.4243 | 1095400.6147
48 | 2715503.9683 | 1095382.4488 | 2715509.1694 | 1095394.4757 | 2715512.4243 | 1095400.6147
49 | 2715503.9683 | 1095382.4488 | 2715503.9606 | 1095382.4309
50 | 2715484.6193 | 1095326.5499 | 2715485.2389 | 1095339.1388 | 2715503.9606 | 1095382.4309
51 | 2715484.2182 | 1095318.4007 | 2715484.6193 | 1095326.5499
52 | 2715484.2182 | 1095318.4007 | 2715483.3091 | 1095299.9324
53 | 2715483.3091 | 1095299.9324 | 2715482.8407 | 1095290.4155 | 2715482.8407 | 1095290.4155
54 | 2715675.3049 | 1095715.0216 | 2715664.2971 | 1095720.7036
55 | 2715689.0646 | 1095666.7934 | 2715675.3049 | 1095715.0216
56 | 2715689.0646 | 1095666.7934 | 2715680.2495 | 1095658.7888
57 | 2715676.1988 | 1095655.1105 | 2715680.2495 | 1095658.7888
58 | 2715676.1988 | 1095655.1105 | 2715672.8043 | 1095652.0281

## bus_geodata
| x | y | coords
0 | 2715763.4959 | 1095584.4204
1 | 2715757.6305 | 1095590.0605
2 | 2715772.7593 | 1095575.5128
3 | 2715748.1326 | 1095599.1935
4 | 2715865.8342 | 1095532.0893
5 | 2715770.3639 | 1095621.9323
6 | 2715711.0144 | 1095566.3756
7 | 2715861.8189 | 1095498.9472
8 | 2715858.4495 | 1095471.1368
9 | 2715752.8312 | 1095621.4093
10 | 2715790.3108 | 1095635.6305
11 | 2715702.3319 | 1095561.853
12 | 2715717.4794 | 1095555.5276
13 | 2715732.6292 | 1095640.0046
14 | 2715683.7277 | 1095553.5588
15 | 2715721.9616 | 1095548.0067
16 | 2715855.8453 | 1095449.6424
17 | 2715851.8369 | 1095424.1597
18 | 2715738.8538 | 1095519.6624
19 | 2715735.38 | 1095525.4913
20 | 2715847.4235 | 1095399.3677
21 | 2715843.4536 | 1095381.2113
22 | 2715838.9046 | 1095361.3547
23 | 2715728.408 | 1095537.1899
24 | 2715833.7161 | 1095339.8653
25 | 2715670.1193 | 1095554.8785
26 | 2715689.3694 | 1095522.1643
27 | 2715661.3627 | 1095558.9296
28 | 2715644.9801 | 1095532.9978
29 | 2715687.4762 | 1095511.036
30 | 2715651.5528 | 1095563.4678
31 | 2715643.1834 | 1095530.1983
32 | 2715687.4525 | 1095510.9449
33 | 2715641.6794 | 1095568.0355
34 | 2715622.7388 | 1095485.9413
35 | 2715688.0517 | 1095510.5477
36 | 2715638.9002 | 1095621.2413
37 | 2715645.76 | 1095627.4704
38 | 2715659.3903 | 1095639.8474
39 | 2715664.0536 | 1095644.082
40 | 2715590.024 | 1095472.9035
41 | 2715633.4926 | 1095466.8772
42 | 2715575.0005 | 1095466.9161
43 | 2715559.5021 | 1095460.7396
44 | 2715551.1048 | 1095457.2007
45 | 2715532.1374 | 1095437.7948
46 | 2715515.0189 | 1095405.5082
47 | 2715512.4243 | 1095400.6147
48 | 2715503.9683 | 1095382.4488
49 | 2715503.9606 | 1095382.4309
50 | 2715484.6193 | 1095326.5499
51 | 2715484.2182 | 1095318.4007
52 | 2715483.3091 | 1095299.9324
53 | 2715482.8407 | 1095290.4155
54 | 2715675.3049 | 1095715.0216
55 | 2715664.2971 | 1095720.7036
56 | 2715689.0646 | 1095666.7934
57 | 2715680.2495 | 1095658.7888
58 | 2715676.1988 | 1095655.1105
59 | 2715672.8043 | 1095652.0281
60 | 2715683.7277 | 1095553.5588

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98979 | -0.1951 | 0.0077125 | 0.0019329
1 | 0.99018 | -0.1876 | 0.0034849 | 0.00087341
2 | 0.98927 | -0.20519 | 0.0041349 | 0.0010363
3 | 0.99085 | -0.17465 | 0 | 0
4 | 0.98547 | -0.2786 | 0 | 0
5 | 0.98827 | -0.22462 | 0 | 0
6 | 0.99414 | -0.11155 | 0 | 0
7 | 0.98424 | -0.30258 | 0.0059444 | 0.0014898
8 | 0.98336 | -0.31975 | 0.0049196 | 0.001233
9 | 0.98675 | -0.25403 | 0 | 0
10 | 0.988 | -0.22974 | 0.011665 | 0.0029235
11 | 0.99493 | -0.09644 | 0.0069471 | 0.0017411
12 | 0.99377 | -0.11857 | 0.0038021 | 0.00095289
13 | 0.98481 | -0.29182 | 0.076735 | 0.019232
14 | 0.99607 | -0.074624 | 0 | 0
15 | 0.99355 | -0.12285 | 0.00339 | 0.0008496
16 | 0.98278 | -0.33111 | 0 | 0
17 | 0.98208 | -0.34468 | 0 | 0
18 | 0.99295 | -0.13445 | 0.014466 | 0.0036256
19 | 0.99304 | -0.13272 | 0.0040795 | 0.0010224
20 | 0.98141 | -0.35793 | 0.0060718 | 0.0015217
21 | 0.98101 | -0.36568 | 0.005807 | 0.0014554
22 | 0.98069 | -0.37204 | 0.0090108 | 0.0022583
23 | 0.99327 | -0.12825 | 0.0057552 | 0.0014424
24 | 0.98052 | -0.37533 | 0.0082159 | 0.0020591
25 | 0.99466 | -0.10136 | 0 | 0
26 | 1 | 0 | -0.41955 | -0.10697
27 | 0.99391 | -0.11574 | 0.0034128 | 0.00085533
28 | 0.99258 | -0.14118 | 0.024456 | 0.0061293
29 | 0.99989 | -0.0022104 | 0.0023355 | 0.00058534
30 | 0.99311 | -0.13122 | 0.0038342 | 0.00096095
31 | 0.99224 | -0.14765 | 0.0059029 | 0.0014794
32 | 0.99988 | -0.0022248 | 0.0032243 | 0.00080809
33 | 0.99233 | -0.1461 | 0 | 0
34 | 0.98747 | -0.23902 | 0 | 0
35 | 0.99988 | -0.0022938 | 0.0055065 | 0.0013801
36 | 0.98853 | -0.21954 | 0 | 0
37 | 0.98787 | -0.23232 | 0.0054531 | 0.0013667
38 | 0.98665 | -0.25597 | 0.0098663 | 0.0024727
39 | 0.98629 | -0.26296 | 0.0058939 | 0.0014771
40 | 0.98485 | -0.28941 | 0.0031444 | 0.00078807
41 | 0.98698 | -0.24855 | 0.024179 | 0.0060597
42 | 0.98369 | -0.31173 | 0.0019649 | 0.00049245
43 | 0.98253 | -0.33422 | 0.0014502 | 0.00036347
44 | 0.98191 | -0.34631 | 0.0012922 | 0.00032384
45 | 0.98005 | -0.38234 | 0.0046141 | 0.0011564
46 | 0.97776 | -0.42712 | 0.0021138 | 0.00052977
47 | 0.97742 | -0.43371 | 0.0016237 | 0.00040693
48 | 0.97623 | -0.45702 | 0.004069 | 0.0010198
49 | 0.97623 | -0.45704 | 0.0060269 | 0.0015105
50 | 0.97324 | -0.51575 | 0.0023756 | 0.00059539
51 | 0.97285 | -0.52344 | 0.0098233 | 0.002462
52 | 0.97214 | -0.53753 | 0.008064 | 0.002021
53 | 0.97185 | -0.54338 | 0.033278 | 0.0083402
54 | 0.98396 | -0.30846 | 0.0074882 | 0.0018767
55 | 0.98381 | -0.31135 | 0.012963 | 0.0032488
56 | 0.9849 | -0.29001 | 0.012898 | 0.0032325
57 | 0.98527 | -0.28288 | 0.0064897 | 0.0016265
58 | 0.98547 | -0.27897 | 0.010213 | 0.0025597
59 | 0.98568 | -0.27485 | 0.0060227 | 0.0015094
60 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.052122 | -0.013178 | 0.052141 | 0.01319 | 1.8756e-05 | 1.1899e-05 | 0.078399 | 0.078399 | 0.078399 | 0.98979 | -0.1951 | 0.99018 | -0.1876 | 21.5382
1 | 0.044409 | 0.011245 | -0.044388 | -0.011231 | 2.1507e-05 | 1.36e-05 | 0.066804 | 0.066804 | 0.066804 | 0.98979 | -0.1951 | 0.98927 | -0.20519 | 18.3529
2 | -0.055626 | -0.014063 | 0.05566 | 0.014085 | 3.4564e-05 | 2.1951e-05 | 0.083636 | 0.083636 | 0.083636 | 0.99018 | -0.1876 | 0.99085 | -0.17465 | 22.977
3 | 0.040253 | 0.010195 | -0.040112 | -0.010106 | 0.00014137 | 8.9164e-05 | 0.060585 | 0.060585 | 0.060585 | 0.98927 | -0.20519 | 0.98547 | -0.2786 | 16.6443
4 | 0.088862 | 0.022449 | -0.088649 | -0.022314 | 0.00021227 | 0.00013545 | 0.13351 | 0.13351 | 0.13351 | 0.99085 | -0.17465 | 0.98827 | -0.22462 | 36.6791
5 | -0.14452 | -0.036534 | 0.14496 | 0.036814 | 0.00043877 | 0.00027953 | 0.21715 | 0.21715 | 0.21715 | 0.99085 | -0.17465 | 0.99414 | -0.11155 | 29.828
6 | 0.040112 | 0.010106 | -0.040066 | -0.010077 | 4.5953e-05 | 2.8985e-05 | 0.060585 | 0.060586 | 0.060586 | 0.98547 | -0.2786 | 0.98424 | -0.30258 | 16.6444
7 | 0.076982 | 0.019389 | -0.076874 | -0.01932 | 0.0001081 | 6.8908e-05 | 0.11594 | 0.11594 | 0.11594 | 0.98827 | -0.22462 | 0.98675 | -0.25403 | 31.8527
8 | 0.011668 | 0.002925 | -0.011665 | -0.0029235 | 2.8452e-06 | 1.5061e-06 | 0.017568 | 0.017568 | 0.017568 | 0.98827 | -0.22462 | 0.988 | -0.22974 | 4.8264
9 | -0.17648 | -0.044724 | 0.17661 | 0.044805 | 0.00012825 | 8.1828e-05 | 0.26433 | 0.26433 | 0.26433 | 0.99414 | -0.11155 | 0.99493 | -0.09644 | 36.3092
10 | 0.031521 | 0.0079099 | -0.03151 | -0.0079033 | 1.0543e-05 | 6.5837e-06 | 0.047183 | 0.047183 | 0.047183 | 0.99414 | -0.11155 | 0.99377 | -0.11857 | 12.9625
11 | 0.034121 | 0.008587 | -0.034093 | -0.0085694 | 2.7969e-05 | 1.7545e-05 | 0.051599 | 0.051599 | 0.051599 | 0.98424 | -0.30258 | 0.98336 | -0.31975 | 14.1755
12 | 0.029174 | 0.0073365 | -0.029158 | -0.0073266 | 1.583e-05 | 9.8564e-06 | 0.044154 | 0.044154 | 0.044154 | 0.98336 | -0.31975 | 0.98278 | -0.33111 | 12.1303
13 | 0.076874 | 0.01932 | -0.076735 | -0.019232 | 0.00013842 | 8.8236e-05 | 0.11594 | 0.11594 | 0.11594 | 0.98675 | -0.25403 | 0.98481 | -0.29182 | 31.8527
14 | -0.18356 | -0.046547 | 0.18375 | 0.046669 | 0.00019272 | 0.00012254 | 0.27472 | 0.27472 | 0.27472 | 0.99493 | -0.09644 | 0.99607 | -0.074624 | 25.1576
15 | 0.027708 | 0.0069504 | -0.027702 | -0.0069469 | 5.652e-06 | 3.5039e-06 | 0.04149 | 0.041491 | 0.041491 | 0.99377 | -0.11857 | 0.99355 | -0.12285 | 11.3985
16 | 0.22162 | 0.05659 | -0.22134 | -0.056408 | 0.00028597 | 0.00018266 | 0.33145 | 0.33145 | 0.33145 | 0.99607 | -0.074624 | 0.99466 | -0.10136 | 45.5289
17 | -0.40537 | -0.10326 | 0.40684 | 0.1042 | 0.0014651 | 0.00093638 | 0.60617 | 0.60617 | 0.60617 | 0.99607 | -0.074624 | 1 | 0 | 55.5101
18 | 0.024312 | 0.0060973 | -0.024306 | -0.0060934 | 6.2611e-06 | 3.8441e-06 | 0.036413 | 0.036414 | 0.036414 | 0.99355 | -0.12285 | 0.99327 | -0.12825 | 10.0037
19 | 0.029158 | 0.0073266 | -0.029139 | -0.0073148 | 1.8863e-05 | 1.1745e-05 | 0.044154 | 0.044155 | 0.044155 | 0.98278 | -0.33111 | 0.98208 | -0.34468 | 12.1304
20 | 0.029139 | 0.0073148 | -0.029121 | -0.0073034 | 1.8411e-05 | 1.1464e-05 | 0.044155 | 0.044155 | 0.044155 | 0.98208 | -0.34468 | 0.98141 | -0.35793 | 12.1304
21 | -0.014466 | -0.0036256 | 0.014468 | 0.0036263 | 1.1959e-06 | 6.7758e-07 | 0.021679 | 0.021679 | 0.021679 | 0.99295 | -0.13445 | 0.99304 | -0.13272 | 5.9557
22 | -0.018547 | -0.0046487 | 0.018551 | 0.0046511 | 3.9445e-06 | 2.3483e-06 | 0.027792 | 0.027792 | 0.027792 | 0.99304 | -0.13272 | 0.99327 | -0.12825 | 7.6351
23 | 0.023049 | 0.0057816 | -0.02304 | -0.0057764 | 8.5142e-06 | 5.2143e-06 | 0.034948 | 0.034949 | 0.034949 | 0.98141 | -0.35793 | 0.98101 | -0.36568 | 9.6013
24 | 0.017233 | 0.0043211 | -0.017228 | -0.004318 | 5.22e-06 | 3.0837e-06 | 0.02614 | 0.02614 | 0.02614 | 0.98101 | -0.36568 | 0.98069 | -0.37204 | 7.1815
25 | 0.0082172 | 0.0020596 | -0.0082159 | -0.0020591 | 1.2888e-06 | 5.4594e-07 | 0.012468 | 0.012468 | 0.012468 | 0.98069 | -0.37204 | 0.98052 | -0.37533 | 3.4254
26 | 0.085213 | 0.021618 | -0.085154 | -0.02158 | 5.8882e-05 | 3.7559e-05 | 0.12757 | 0.12757 | 0.12757 | 0.99466 | -0.10136 | 0.99391 | -0.11574 | 35.047
27 | 0.13612 | 0.03479 | -0.13586 | -0.034623 | 0.00026163 | 0.00016657 | 0.20388 | 0.20388 | 0.20388 | 0.99466 | -0.10136 | 0.99258 | -0.14118 | 28.0055
28 | 0.011068 | 0.0027741 | -0.011066 | -0.0027735 | 1.1654e-06 | 5.9557e-07 | 0.016469 | 0.016469 | 0.016469 | 1 | 0 | 0.99989 | -0.0022104 | 4.5244
29 | 0.081741 | 0.020725 | -0.08168 | -0.020686 | 6.0787e-05 | 3.8764e-05 | 0.12246 | 0.12246 | 0.12246 | 0.99391 | -0.11574 | 0.99311 | -0.13122 | 33.6433
30 | 0.1114 | 0.028494 | -0.11137 | -0.028472 | 3.488e-05 | 2.228e-05 | 0.16722 | 0.16722 | 0.16722 | 0.99258 | -0.14118 | 0.99224 | -0.14765 | 45.9387
31 | 0.0087308 | 0.0021882 | -0.0087308 | -0.0021882 | 5.9605e-09 | 2.5798e-09 | 0.012993 | 0.012993 | 0.012993 | 0.99989 | -0.0022104 | 0.99988 | -0.0022248 | 3.5695
32 | 0.077846 | 0.019725 | -0.077791 | -0.01969 | 5.5574e-05 | 3.5427e-05 | 0.11672 | 0.11672 | 0.11672 | 0.99311 | -0.13122 | 0.99233 | -0.1461 | 32.0651
33 | 0.10547 | 0.026992 | -0.105 | -0.026696 | 0.00046433 | 0.00029654 | 0.15836 | 0.15836 | 0.15836 | 0.99224 | -0.14765 | 0.98747 | -0.23902 | 43.5068
34 | 0.0055065 | 0.0013801 | -0.0055065 | -0.0013801 | 1.8103e-08 | 2.1573e-09 | 0.0081948 | 0.0081948 | 0.0081948 | 0.99988 | -0.0022248 | 0.99988 | -0.0022938 | 2.2513
35 | 0.077791 | 0.01969 | -0.077517 | -0.019515 | 0.00027319 | 0.00017415 | 0.11672 | 0.11672 | 0.11672 | 0.99233 | -0.1461 | 0.98853 | -0.21954 | 32.0651
36 | 0.080813 | 0.020629 | -0.080617 | -0.020504 | 0.00019628 | 0.00012517 | 0.12191 | 0.12191 | 0.12191 | 0.98747 | -0.23902 | 0.98485 | -0.28941 | 33.4924
37 | 0.02419 | 0.0060665 | -0.024179 | -0.0060597 | 1.0988e-05 | 6.7504e-06 | 0.036453 | 0.036453 | 0.036453 | 0.98747 | -0.23902 | 0.98698 | -0.24855 | 10.0145
38 | 0.077517 | 0.019515 | -0.07747 | -0.019485 | 4.7336e-05 | 3.0176e-05 | 0.11672 | 0.11672 | 0.11672 | 0.98853 | -0.21954 | 0.98787 | -0.23232 | 32.0651
39 | 0.072017 | 0.018119 | -0.071936 | -0.018067 | 8.1283e-05 | 5.1786e-05 | 0.1085 | 0.1085 | 0.1085 | 0.98787 | -0.23232 | 0.98665 | -0.25597 | 29.8086
40 | 0.062069 | 0.015594 | -0.062049 | -0.015581 | 2.0705e-05 | 1.3171e-05 | 0.093623 | 0.093624 | 0.093624 | 0.98665 | -0.25597 | 0.98629 | -0.26296 | 25.7207
41 | 0.056155 | 0.014104 | -0.056123 | -0.014084 | 3.1823e-05 | 2.0216e-05 | 0.084731 | 0.084731 | 0.084731 | 0.98629 | -0.26296 | 0.98568 | -0.27485 | 23.2779
42 | 0.077472 | 0.019716 | -0.077389 | -0.019663 | 8.325e-05 | 5.3074e-05 | 0.11716 | 0.11716 | 0.11716 | 0.98485 | -0.28941 | 0.98369 | -0.31173 | 32.1872
43 | 0.075424 | 0.019171 | -0.075343 | -0.019119 | 8.1579e-05 | 5.1999e-05 | 0.11419 | 0.11419 | 0.11419 | 0.98369 | -0.31173 | 0.98253 | -0.33422 | 31.3707
44 | 0.073892 | 0.018755 | -0.073849 | -0.018728 | 4.2945e-05 | 2.7369e-05 | 0.11199 | 0.11199 | 0.11199 | 0.98253 | -0.33422 | 0.98191 | -0.34631 | 30.7673
45 | 0.072557 | 0.018404 | -0.072432 | -0.018324 | 0.00012545 | 7.9941e-05 | 0.11003 | 0.11003 | 0.11003 | 0.98191 | -0.34631 | 0.98005 | -0.38234 | 30.2294
46 | 0.067818 | 0.017168 | -0.067672 | -0.017075 | 0.00014547 | 9.2641e-05 | 0.10303 | 0.10303 | 0.10303 | 0.98005 | -0.38234 | 0.97776 | -0.42712 | 28.3048
47 | 0.065559 | 0.016545 | -0.065538 | -0.016532 | 2.0693e-05 | 1.3174e-05 | 0.099813 | 0.099813 | 0.099813 | 0.97776 | -0.42712 | 0.97742 | -0.43371 | 27.4211
48 | 0.063914 | 0.016125 | -0.063843 | -0.01608 | 7.1248e-05 | 4.5348e-05 | 0.097341 | 0.097341 | 0.097341 | 0.97742 | -0.43371 | 0.97623 | -0.45702 | 26.742
49 | 0.059774 | 0.01506 | -0.059774 | -0.01506 | 6.0753e-08 | 3.8637e-08 | 0.091139 | 0.091139 | 0.091139 | 0.97623 | -0.45702 | 0.97623 | -0.45704 | 25.0381
50 | 0.053747 | 0.013549 | -0.053597 | -0.013454 | 0.00015054 | 9.5599e-05 | 0.081952 | 0.081953 | 0.081953 | 0.97623 | -0.45704 | 0.97324 | -0.51575 | 22.5145
51 | 0.051221 | 0.012858 | -0.051202 | -0.012847 | 1.8768e-05 | 1.191e-05 | 0.078321 | 0.078321 | 0.078321 | 0.97324 | -0.51575 | 0.97285 | -0.52344 | 21.5166
52 | 0.041379 | 0.010385 | -0.041351 | -0.010367 | 2.778e-05 | 1.755e-05 | 0.063295 | 0.063296 | 0.063296 | 0.97285 | -0.52344 | 0.97214 | -0.53753 | 17.3889
53 | 0.033287 | 0.008346 | -0.033278 | -0.0083402 | 9.2765e-06 | 5.8189e-06 | 0.050952 | 0.050952 | 0.050952 | 0.97214 | -0.53753 | 0.97185 | -0.54338 | 13.9979
54 | 0.012965 | 0.0032498 | -0.012963 | -0.0032488 | 1.7857e-06 | 9.8555e-07 | 0.019606 | 0.019606 | 0.019606 | 0.98396 | -0.30846 | 0.98381 | -0.31135 | 5.3864
55 | -0.020453 | -0.0051265 | 0.020471 | 0.0051374 | 1.7993e-05 | 1.0878e-05 | 0.030931 | 0.03093 | 0.030931 | 0.98396 | -0.30846 | 0.9849 | -0.29001 | 8.4974
56 | -0.033369 | -0.0083699 | 0.03338 | 0.008377 | 1.135e-05 | 7.1123e-06 | 0.050417 | 0.050417 | 0.050417 | 0.9849 | -0.29001 | 0.98527 | -0.28288 | 13.8508
57 | -0.03987 | -0.010003 | 0.039877 | 0.010008 | 7.4403e-06 | 4.6921e-06 | 0.060218 | 0.060218 | 0.060218 | 0.98527 | -0.28288 | 0.98547 | -0.27897 | 16.5434
58 | -0.050091 | -0.012568 | 0.0501 | 0.012574 | 9.8376e-06 | 6.2376e-06 | 0.075639 | 0.075639 | 0.075639 | 0.98547 | -0.27897 | 0.98568 | -0.27485 | 20.7801

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.42437 | 0.10818

## res_load
| p_mw | q_mvar
0 | 0.0077125 | 0.0019329
1 | 0.0034849 | 0.00087341
2 | 0.0041349 | 0.0010363
3 | 0.0059444 | 0.0014898
4 | 0.0049196 | 0.001233
5 | 0.011665 | 0.0029235
6 | 0.0069471 | 0.0017411
7 | 0.0038021 | 0.00095289
8 | 0.076735 | 0.019232
9 | 0.00339 | 0.0008496
10 | 0.014466 | 0.0036256
11 | 0.0040795 | 0.0010224
12 | 0.0060718 | 0.0015217
13 | 0.005807 | 0.0014554
14 | 0.0090108 | 0.0022583
15 | 0.0057552 | 0.0014424
16 | 0.0082159 | 0.0020591
17 | 0.0048165 | 0.0012071
18 | 0.0034128 | 0.00085533
19 | 0.024456 | 0.0061293
20 | 0.0023355 | 0.00058534
21 | 0.0038342 | 0.00096095
22 | 0.0059029 | 0.0014794
23 | 0.0032243 | 0.00080809
24 | 0.0055065 | 0.0013801
25 | 0.0054531 | 0.0013667
26 | 0.0098663 | 0.0024727
27 | 0.0058939 | 0.0014771
28 | 0.0031444 | 0.00078807
29 | 0.024179 | 0.0060597
30 | 0.0019649 | 0.00049245
31 | 0.0014502 | 0.00036347
32 | 0.0012922 | 0.00032384
33 | 0.0046141 | 0.0011564
34 | 0.0021138 | 0.00052977
35 | 0.0016237 | 0.00040693
36 | 0.004069 | 0.0010198
37 | 0.0060269 | 0.0015105
38 | 0.0023756 | 0.00059539
39 | 0.0098233 | 0.002462
40 | 0.008064 | 0.002021
41 | 0.033278 | 0.0083402
42 | 0.0074882 | 0.0018767
43 | 0.012963 | 0.0032488
44 | 0.012898 | 0.0032325
45 | 0.0064897 | 0.0016265
46 | 0.010213 | 0.0025597
47 | 0.0060227 | 0.0015094

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1