## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5230-1_0_7_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5230-1_0_7_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5230-1_0_7_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5230-1_0_7_node_5 | 0.4 | n |  | TRUE
4 | bus_LV_5230-1_0_7_node_7 | 0.4 | n |  | TRUE
5 | bus_LV_5230-1_0_7_node_56 | 0.4 | n |  | TRUE
6 | bus_LV_5230-1_0_7_node_3 | 0.4 | n |  | TRUE
7 | bus_LV_5230-1_0_7_node_4 | 0.4 | n |  | TRUE
8 | bus_LV_5230-1_0_7_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5230-1_0_7_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_5230-1_0_7_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_5230-1_0_7_node_17 | 0.4 | n |  | TRUE
12 | bus_LV_5230-1_0_7_node_16 | 0.4 | n |  | TRUE
13 | bus_LV_5230-1_0_7_node_24 | 0.4 | n |  | TRUE
14 | bus_LV_5230-1_0_7_node_55 | 0.4 | n |  | TRUE
15 | bus_LV_5230-1_0_7_node_23 | 0.4 | n |  | TRUE
16 | bus_LV_5230-1_0_7_node_10 | 0.4 | n |  | TRUE
17 | bus_LV_5230-1_0_7_node_11 | 0.4 | n |  | TRUE
18 | bus_LV_5230-1_0_7_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_5230-1_0_7_node_15 | 0.4 | n |  | TRUE
20 | bus_LV_5230-1_0_7_node_26 | 0.4 | n |  | TRUE
21 | bus_LV_5230-1_0_7_node_27 | 0.4 | n |  | TRUE
22 | bus_LV_5230-1_0_7_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_5230-1_0_7_node_19 | 0.4 | n |  | TRUE
24 | bus_LV_5230-1_0_7_node_20 | 0.4 | n |  | TRUE
25 | bus_LV_5230-1_0_7_node_21 | 0.4 | n |  | TRUE
26 | bus_LV_5230-1_0_7_node_25 | 0.4 | n |  | TRUE
27 | bus_LV_5230-1_0_7_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_5230-1_0_7_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_5230-1_0_7_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_5230-1_0_7_node_29 | 0.4 | n |  | TRUE
31 | bus_LV_5230-1_0_7_node_28 | 0.4 | n |  | TRUE
32 | bus_LV_5230-1_0_7_node_32 | 0.4 | n |  | TRUE
33 | bus_LV_5230-1_0_7_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_5230-1_0_7_node_41 | 0.4 | n |  | TRUE
35 | bus_LV_5230-1_0_7_node_47 | 0.4 | n |  | TRUE
36 | bus_LV_5230-1_0_7_node_39 | 0.4 | n |  | TRUE
37 | bus_LV_5230-1_0_7_node_48 | 0.4 | n |  | TRUE
38 | bus_LV_5230-1_0_7_node_49 | 0.4 | n |  | TRUE
39 | bus_LV_5230-1_0_7_node_50 | 0.4 | n |  | TRUE
40 | bus_LV_5230-1_0_7_node_33 | 0.4 | n |  | TRUE
41 | bus_LV_5230-1_0_7_node_40 | 0.4 | n |  | TRUE
42 | bus_LV_5230-1_0_7_node_34 | 0.4 | n |  | TRUE
43 | bus_LV_5230-1_0_7_node_42 | 0.4 | n |  | TRUE
44 | bus_LV_5230-1_0_7_node_35 | 0.4 | n |  | TRUE
45 | bus_LV_5230-1_0_7_node_43 | 0.4 | n |  | TRUE
46 | bus_LV_5230-1_0_7_node_36 | 0.4 | n |  | TRUE
47 | bus_LV_5230-1_0_7_node_75 | 0.4 | n |  | TRUE
48 | bus_LV_5230-1_0_7_node_93 | 0.4 | n |  | TRUE
49 | bus_LV_5230-1_0_7_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_5230-1_0_7_node_94 | 0.4 | n |  | TRUE
51 | bus_LV_5230-1_0_7_node_92 | 0.4 | n |  | TRUE
52 | bus_LV_5230-1_0_7_node_45 | 0.4 | n |  | TRUE
53 | bus_LV_5230-1_0_7_node_44 | 0.4 | n |  | TRUE
54 | bus_LV_5230-1_0_7_node_58 | 0.4 | n |  | TRUE
55 | bus_LV_5230-1_0_7_node_57 | 0.4 | n |  | TRUE
56 | bus_LV_5230-1_0_7_node_46 | 0.4 | n |  | TRUE
57 | bus_LV_5230-1_0_7_node_60 | 0.4 | n |  | TRUE
58 | bus_LV_5230-1_0_7_node_61 | 0.4 | n |  | TRUE
59 | bus_LV_5230-1_0_7_node_91 | 0.4 | n |  | TRUE
60 | bus_LV_5230-1_0_7_node_90 | 0.4 | n |  | TRUE
61 | bus_LV_5230-1_0_7_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_5230-1_0_7_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_5230-1_0_7_node_53 | 0.4 | n |  | TRUE
64 | bus_LV_5230-1_0_7_node_71 | 0.4 | n |  | TRUE
65 | bus_LV_5230-1_0_7_node_73 | 0.4 | n |  | TRUE
66 | bus_LV_5230-1_0_7_node_54 | 0.4 | n |  | TRUE
67 | bus_LV_5230-1_0_7_node_68 | 0.4 | n |  | TRUE
68 | bus_LV_5230-1_0_7_node_69 | 0.4 | n |  | TRUE
69 | bus_LV_5230-1_0_7_node_64 | 0.4 | n |  | TRUE
70 | bus_LV_5230-1_0_7_node_62 | 0.4 | n |  | TRUE
71 | bus_LV_5230-1_0_7_node_63 | 0.4 | n |  | TRUE
72 | bus_LV_5230-1_0_7_node_65 | 0.4 | n |  | TRUE
73 | bus_LV_5230-1_0_7_node_66 | 0.4 | n |  | TRUE
74 | bus_LV_5230-1_0_7_node_67 | 0.4 | n |  | TRUE
75 | bus_LV_5230-1_0_7_node_87 | 0.4 | n |  | TRUE
76 | bus_LV_5230-1_0_7_node_89 | 0.4 | n |  | TRUE
77 | bus_LV_5230-1_0_7_node_86 | 0.4 | n |  | TRUE
78 | bus_LV_5230-1_0_7_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_5230-1_0_7_node_76 | 0.4 | n |  | TRUE
80 | bus_LV_5230-1_0_7_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_5230-1_0_7_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_5230-1_0_7_node_77 | 0.4 | n |  | TRUE
83 | bus_LV_5230-1_0_7_node_79 | 0.4 | n |  | TRUE
84 | bus_LV_5230-1_0_7_node_78 | 0.4 | n |  | TRUE
85 | bus_LV_5230-1_0_7_node_80 | 0.4 | n |  | TRUE
86 | bus_LV_5230-1_0_7_node_81 | 0.4 | n |  | TRUE
87 | bus_LV_5230-1_0_7_node_82 | 0.4 | n |  | TRUE
88 | bus_LV_5230-1_0_7_node_83 | 0.4 | n |  | TRUE
89 | bus_LV_5230-1_0_7_node_84 | 0.4 | n |  | TRUE
90 | bus_LV_5230-1_0_7_node_85 | 0.4 | n |  | TRUE
91 | bus_LV_5230-1_0_7_node_88 | 0.4 | n |  | TRUE
92 | bus_MV_246_0_node_77 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5230-1_0_7_load_0 | 0 | 0.01063 | 0.002664 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5230-1_0_7_load_1 | 1 | 0.0029152 | 0.00073061 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5230-1_0_7_load_56 | 5 | 0.0037662 | 0.00094389 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5230-1_0_7_load_3 | 6 | 0.018238 | 0.0045709 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5230-1_0_7_load_4 | 7 | 0.0092048 | 0.0023069 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5230-1_0_7_load_9 | 10 | 0.0065187 | 0.0016337 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5230-1_0_7_load_17 | 11 | 0.01029 | 0.002579 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5230-1_0_7_load_16 | 12 | 0.0071243 | 0.0017855 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5230-1_0_7_load_24 | 13 | 0.0039808 | 0.00099767 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5230-1_0_7_load_55 | 14 | 0.0025408 | 0.00063679 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5230-1_0_7_load_10 | 16 | 0.012153 | 0.0030459 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5230-1_0_7_load_11 | 17 | 0.0111 | 0.0027819 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5230-1_0_7_load_13 | 18 | 0.0050938 | 0.0012766 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5230-1_0_7_load_15 | 19 | 0.0039425 | 0.00098808 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5230-1_0_7_load_26 | 20 | 0.0063652 | 0.0015953 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5230-1_0_7_load_18 | 22 | 0.0025468 | 0.00063829 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5230-1_0_7_load_19 | 23 | 0.0064113 | 0.0016068 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5230-1_0_7_load_20 | 24 | 0.003943 | 0.00098821 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5230-1_0_7_load_25 | 26 | 0.0030649 | 0.00076814 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5230-1_0_7_load_22 | 27 | 0.0074862 | 0.0018762 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5230-1_0_7_load_30 | 28 | 0.0026252 | 0.00065793 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5230-1_0_7_load_31 | 29 | 0.0013323 | 0.0003339 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5230-1_0_7_load_29 | 30 | 0.0039057 | 0.00097887 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5230-1_0_7_load_28 | 31 | 0.0082287 | 0.0020623 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5230-1_0_7_load_32 | 32 | 0.0043673 | 0.0010946 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5230-1_0_7_load_38 | 33 | 0.0028157 | 0.00070567 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5230-1_0_7_load_41 | 34 | 0.0055679 | 0.0013955 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5230-1_0_7_load_48 | 37 | 0.004836 | 0.001212 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5230-1_0_7_load_49 | 38 | 0.0076496 | 0.0019172 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5230-1_0_7_load_50 | 39 | 0.002443 | 0.00061228 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5230-1_0_7_load_40 | 41 | 0.0035229 | 0.00088293 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5230-1_0_7_load_34 | 42 | 0.0011456 | 0.0002871 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5230-1_0_7_load_42 | 43 | 0.0025888 | 0.00064881 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5230-1_0_7_load_35 | 44 | 0.0027455 | 0.00068808 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5230-1_0_7_load_93 | 48 | 0.003131 | 0.00078471 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5230-1_0_7_load_94 | 50 | 0.0040314 | 0.0010104 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5230-1_0_7_load_92 | 51 | 0.0049926 | 0.0012513 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5230-1_0_7_load_45 | 52 | 0.0040483 | 0.0010146 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5230-1_0_7_load_44 | 53 | 0.0037161 | 0.00093134 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5230-1_0_7_load_58 | 54 | 0.0026097 | 0.00065405 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5230-1_0_7_load_57 | 55 | 0.0023407 | 0.00058664 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5230-1_0_7_load_46 | 56 | 0.0040843 | 0.0010236 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5230-1_0_7_load_60 | 57 | 0.0031793 | 0.00079682 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5230-1_0_7_load_61 | 58 | 0.0022272 | 0.0005582 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5230-1_0_7_load_91 | 59 | 0.0058286 | 0.0014608 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5230-1_0_7_load_90 | 60 | 0.013651 | 0.0034211 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5230-1_0_7_load_52 | 62 | 0.015044 | 0.0037704 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5230-1_0_7_load_53 | 63 | 0.012093 | 0.0030307 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5230-1_0_7_load_71 | 64 | 0.0034578 | 0.00086661 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5230-1_0_7_load_54 | 66 | 0.0024636 | 0.00061744 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5230-1_0_7_load_68 | 67 | 0.0035527 | 0.0008904 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5230-1_0_7_load_69 | 68 | 0.0033671 | 0.00084387 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5230-1_0_7_load_62 | 70 | 0.0032359 | 0.00081099 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5230-1_0_7_load_63 | 71 | 0.0034236 | 0.00085804 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5230-1_0_7_load_65 | 72 | 0.0026975 | 0.00067605 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5230-1_0_7_load_66 | 73 | 0.010426 | 0.002613 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5230-1_0_7_load_67 | 74 | 0.010565 | 0.0026479 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5230-1_0_7_load_87 | 75 | 0.0075805 | 0.0018998 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5230-1_0_7_load_89 | 76 | 0.01183 | 0.002965 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5230-1_0_7_load_86 | 77 | 0.0093384 | 0.0023404 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5230-1_0_7_load_70 | 78 | 0.010991 | 0.0027546 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5230-1_0_7_load_76 | 79 | 0.0085894 | 0.0021527 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5230-1_0_7_load_72 | 80 | 0.0060048 | 0.0015049 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5230-1_0_7_load_77 | 82 | 0.023788 | 0.0059618 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5230-1_0_7_load_79 | 83 | 0.0090255 | 0.002262 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5230-1_0_7_load_78 | 84 | 0.016321 | 0.0040904 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5230-1_0_7_load_80 | 85 | 0.0083303 | 0.0020878 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5230-1_0_7_load_81 | 86 | 0.015797 | 0.003959 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5230-1_0_7_load_82 | 87 | 0.0086015 | 0.0021557 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5230-1_0_7_load_83 | 88 | 0.01034 | 0.0025914 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5230-1_0_7_load_84 | 89 | 0.0074363 | 0.0018637 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5230-1_0_7_load_85 | 90 | 0.0081801 | 0.0020501 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5230-1_0_7_load_88 | 91 | 0.0078217 | 0.0019603 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 50 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5230-1_0_7_line_0 |  | 0 | 1 | 0.0046545 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5230-1_0_7_line_1 |  | 1 | 2 | 0.030906 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5230-1_0_7_line_2 |  | 2 | 3 | 0.053238 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5230-1_0_7_line_3 |  | 3 | 6 | 0.025246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5230-1_0_7_line_4 |  | 3 | 4 | 0.067185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5230-1_0_7_line_5 |  | 4 | 5 | 0.011969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5230-1_0_7_line_6 |  | 5 | 14 | 0.012994 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5230-1_0_7_line_7 |  | 6 | 7 | 0.016989 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5230-1_0_7_line_8 |  | 7 | 8 | 0.014298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5230-1_0_7_line_9 |  | 8 | 9 | 0.00837 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5230-1_0_7_line_10 |  | 8 | 10 | 0.010401 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5230-1_0_7_line_11 |  | 9 | 11 | 0.012323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5230-1_0_7_line_12 |  | 9 | 12 | 0.017937 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5230-1_0_7_line_13 |  | 10 | 13 | 0.014132 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5230-1_0_7_line_14 |  | 13 | 15 | 0.047539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5230-1_0_7_line_15 |  | 14 | 66 | 0.010644 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5230-1_0_7_line_16 |  | 15 | 27 | 0.02512 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5230-1_0_7_line_17 |  | 16 | 17 | 0.022271 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5230-1_0_7_line_18 |  | 17 | 18 | 0.016619 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5230-1_0_7_line_19 |  | 18 | 19 | 0.017956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5230-1_0_7_line_20 |  | 19 | 20 | 0.02224 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5230-1_0_7_line_21 |  | 20 | 21 | 0.0091565 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5230-1_0_7_line_22 |  | 21 | 30 | 0.024739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5230-1_0_7_line_23 |  | 21 | 31 | 0.057813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5230-1_0_7_line_24 |  | 22 | 23 | 0.028501 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5230-1_0_7_line_25 |  | 22 | 24 | 0.016027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5230-1_0_7_line_26 |  | 23 | 25 | 0.005951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5230-1_0_7_line_27 |  | 25 | 26 | 0.017465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5230-1_0_7_line_28 |  | 25 | 27 | 0.02812 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5230-1_0_7_line_29 |  | 26 | 28 | 0.026699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5230-1_0_7_line_30 |  | 28 | 29 | 0.014597 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5230-1_0_7_line_31 |  | 29 | 42 | 0.0060377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5230-1_0_7_line_32 |  | 30 | 32 | 0.035162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5230-1_0_7_line_33 |  | 30 | 33 | 0.057586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5230-1_0_7_line_34 |  | 32 | 40 | 0.02301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5230-1_0_7_line_35 |  | 32 | 41 | 0.088539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5230-1_0_7_line_36 |  | 34 | 35 | 0.022328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5230-1_0_7_line_37 |  | 34 | 36 | 0.02176 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5230-1_0_7_line_38 |  | 35 | 37 | 0.029747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5230-1_0_7_line_39 |  | 35 | 38 | 0.018298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5230-1_0_7_line_40 |  | 36 | 41 | 0.03647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5230-1_0_7_line_41 |  | 37 | 39 | 0.01382 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5230-1_0_7_line_42 |  | 40 | 44 | 0.0095153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5230-1_0_7_line_43 |  | 42 | 43 | 0.01872 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5230-1_0_7_line_44 |  | 43 | 45 | 0.04345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5230-1_0_7_line_45 |  | 44 | 45 | 0.025785 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5230-1_0_7_line_46 |  | 45 | 49 | 0.032749 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
47 | LV_5230-1_0_7_line_47 |  | 46 | 47 | 0.019847 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5230-1_0_7_line_48 |  | 46 | 48 | 0.0040559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5230-1_0_7_line_49 |  | 47 | 51 | 0.025935 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5230-1_0_7_line_50 |  | 48 | 50 | 0.036674 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5230-1_0_7_line_51 |  | 49 | 50 | 0.0073682 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
52 | LV_5230-1_0_7_line_52 |  | 50 | 52 | 0.059897 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_5230-1_0_7_line_53 |  | 52 | 56 | 0.024637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_5230-1_0_7_line_54 |  | 52 | 53 | 0.011322 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5230-1_0_7_line_55 |  | 53 | 54 | 0.06841 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5230-1_0_7_line_56 |  | 54 | 55 | 0.020018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5230-1_0_7_line_57 |  | 56 | 57 | 0.0088551 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
58 | LV_5230-1_0_7_line_58 |  | 57 | 58 | 0.011796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
59 | LV_5230-1_0_7_line_59 |  | 58 | 70 | 0.0088503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
60 | LV_5230-1_0_7_line_60 |  | 59 | 60 | 0.036082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5230-1_0_7_line_61 |  | 60 | 76 | 0.0094692 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5230-1_0_7_line_62 |  | 61 | 62 | 0.0421 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5230-1_0_7_line_63 |  | 61 | 63 | 0.051862 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5230-1_0_7_line_64 |  | 63 | 64 | 0.086483 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5230-1_0_7_line_65 |  | 64 | 65 | 0.061933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5230-1_0_7_line_66 |  | 65 | 79 | 0.02696 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_5230-1_0_7_line_67 |  | 65 | 80 | 0.006016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5230-1_0_7_line_68 |  | 67 | 68 | 0.018377 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5230-1_0_7_line_69 |  | 67 | 69 | 0.013988 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5230-1_0_7_line_70 |  | 68 | 78 | 0.018519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5230-1_0_7_line_71 |  | 69 | 72 | 0.012036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_5230-1_0_7_line_72 |  | 69 | 71 | 0.013203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_5230-1_0_7_line_73 |  | 70 | 71 | 0.00023894 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
74 | LV_5230-1_0_7_line_74 |  | 72 | 73 | 0.019059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
75 | LV_5230-1_0_7_line_75 |  | 73 | 74 | 0.0088155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
76 | LV_5230-1_0_7_line_76 |  | 74 | 75 | 0.044612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
77 | LV_5230-1_0_7_line_77 |  | 75 | 76 | 0.028617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5230-1_0_7_line_78 |  | 75 | 77 | 0.010188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
79 | LV_5230-1_0_7_line_79 |  | 77 | 91 | 0.0109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
80 | LV_5230-1_0_7_line_80 |  | 79 | 83 | 0.026678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
81 | LV_5230-1_0_7_line_81 |  | 80 | 81 | 0.084454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5230-1_0_7_line_82 |  | 81 | 82 | 0.048699 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5230-1_0_7_line_83 |  | 83 | 84 | 0.027459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
84 | LV_5230-1_0_7_line_84 |  | 84 | 85 | 0.051455 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
85 | LV_5230-1_0_7_line_85 |  | 85 | 86 | 0.0072949 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
86 | LV_5230-1_0_7_line_86 |  | 86 | 87 | 0.018918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
87 | LV_5230-1_0_7_line_87 |  | 87 | 88 | 0.010114 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
88 | LV_5230-1_0_7_line_88 |  | 88 | 89 | 0.00045285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
89 | LV_5230-1_0_7_line_89 |  | 89 | 90 | 0.014018 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
90 | LV_5230-1_0_7_line_90 |  | 90 | 91 | 0.0039019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5230-1_0_7_trafo_94 | 0.63 MVA 20/0.4 kV | 92 | 50 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10
0 | 2712007.3586 | 1094045.9075 | 2712010.7827 | 1094049.0602
1 | 2712033.5197 | 1094069.9943 | 2712010.7827 | 1094049.0602
2 | 2712033.5197 | 1094069.9943 | 2712063.3434 | 1094047.2729 | 2712072.3593 | 1094060.181
3 | 2712072.3593 | 1094060.181 | 2712080.8879 | 1094075.1372 | 2712082.6613 | 1094082.9681
4 | 2712072.3593 | 1094060.181 | 2712063.3434 | 1094047.2729 | 2712034.1692 | 1094004.9068
5 | 2712034.1692 | 1094004.9068 | 2712025.1452 | 1094012.7692
6 | 2712015.3482 | 1094021.3049 | 2712025.1452 | 1094012.7692
7 | 2712082.6613 | 1094082.9681 | 2712083.3962 | 1094086.2131 | 2712083.9415 | 1094099.8644
8 | 2712087.9892 | 1094113.2716 | 2712084.165 | 1094105.4625 | 2712083.9415 | 1094099.8644
9 | 2712087.9892 | 1094113.2716 | 2712082.2651 | 1094119.3925
10 | 2712087.9892 | 1094113.2716 | 2712089.7362 | 1094113.5151 | 2712096.5997 | 1094118.7581
11 | 2712082.2651 | 1094119.3925 | 2712077.5706 | 1094113.8133 | 2712076.3587 | 1094108.921
12 | 2712082.2651 | 1094119.3925 | 2712094.7426 | 1094132.2789
13 | 2712107.8297 | 1094127.3367 | 2712096.5997 | 1094118.7581
14 | 2712151.2194 | 1094122.7437 | 2712146.4219 | 1094118.9638 | 2712143.789 | 1094118.8485 | 2712141.2507 | 1094119.4799 | 2712136.7343 | 1094122.7321 | 2712133.1332 | 1094125.5232 | 2712129.1006 | 1094127.3389 | 2712125.2075 | 1094128.3123 | 2712121.2458 | 1094128.8062 | 2712108.5293 | 1094127.8712 | 2712107.8297 | 1094127.3367
15 | 2712007.3229 | 1094028.2971 | 2712015.3482 | 1094021.3049
16 | 2712151.2194 | 1094122.7437 | 2712150.0911 | 1094133.4857 | 2712155.9726 | 1094146.5415
17 | 2712048.2012 | 1094148.9675 | 2712065.3846 | 1094163.1361
18 | 2712077.5868 | 1094174.3205 | 2712074.9119 | 1094170.9918 | 2712065.3846 | 1094163.1361
19 | 2712077.5868 | 1094174.3205 | 2712085.4051 | 1094184.0496 | 2712088.4569 | 1094188.5945
20 | 2712088.4569 | 1094188.5945 | 2712100.8552 | 1094207.0585
21 | 2712105.9597 | 1094214.6602 | 2712100.8552 | 1094207.0585
22 | 2712105.9597 | 1094214.6602 | 2712113.3731 | 1094226.1935 | 2712119.7813 | 1094235.1695
23 | 2712105.9597 | 1094214.6602 | 2712090.2136 | 1094214.9591 | 2712071.7957 | 1094211.3728 | 2712066.1061 | 1094209.3221 | 2712052.1125 | 1094199.2305
24 | 2712152.5763 | 1094170.9925 | 2712135.2649 | 1094159.1074 | 2712129.132 | 1094154.786
25 | 2712116.0309 | 1094145.5547 | 2712129.132 | 1094154.786
26 | 2712157.4823 | 1094174.3607 | 2712152.5763 | 1094170.9925
27 | 2712157.4823 | 1094174.3607 | 2712161.5835 | 1094190.2471 | 2712162.1221 | 1094191.1577
28 | 2712157.4823 | 1094174.3607 | 2712155.9152 | 1094167.3048 | 2712155.728 | 1094164.0103 | 2712155.7635 | 1094159.986 | 2712156.5745 | 1094151.3173 | 2712156.5638 | 1094148.5374 | 2712155.9803 | 1094146.5587 | 2712155.9726 | 1094146.5415
29 | 2712162.1221 | 1094191.1577 | 2712164.9881 | 1094196.0026 | 2712174.8784 | 1094210.6394 | 2712175.4828 | 1094213.9904
30 | 2712175.4828 | 1094213.9904 | 2712176.1018 | 1094217.4221 | 2712176.1898 | 1094228.5316
31 | 2712176.1898 | 1094228.5316 | 2712176.2181 | 1094232.1119 | 2712176.5829 | 1094234.542
32 | 2712119.7813 | 1094235.1695 | 2712125.5516 | 1094243.2518 | 2712137.2244 | 1094257.888 | 2712141.5842 | 1094262.723
33 | 2712119.7813 | 1094235.1695 | 2712080.9614 | 1094277.704
34 | 2712156.9933 | 1094279.8118 | 2712141.5842 | 1094262.723
35 | 2712141.5842 | 1094262.723 | 2712077.8301 | 1094324.1601
36 | 2712007.844 | 1094349.5879 | 2712015.7341 | 1094336.9358 | 2712022.2266 | 1094333.3501
37 | 2712041.2746 | 1094322.8301 | 2712022.2266 | 1094333.3501
38 | 2712007.844 | 1094349.5879 | 2711994.3533 | 1094347.7938 | 2711980.1172 | 1094340.1932 | 2711980.1172 | 1094340.1932
39 | 2712007.844 | 1094349.5879 | 2712020.5223 | 1094362.782
40 | 2712041.2746 | 1094322.8301 | 2712077.8301 | 1094324.1601
41 | 2711980.1172 | 1094340.1932 | 2711967.374 | 1094334.8439
42 | 2712156.9933 | 1094279.8118 | 2712163.398 | 1094280.0634 | 2712165.7742 | 1094282.0632
43 | 2712179.475 | 1094253.0348 | 2712179.0063 | 1094250.687 | 2712176.5829 | 1094234.542
44 | 2712186.9162 | 1094295.352 | 2712188.0747 | 1094289.2693 | 2712182.4683 | 1094268.0293 | 2712179.475 | 1094253.0348
45 | 2712186.9162 | 1094295.352 | 2712180.7826 | 1094294.694 | 2712165.7742 | 1094282.0632
46 | 2712186.9162 | 1094295.352 | 2712188.9818 | 1094306.4643 | 2712191.1241 | 1094313.8421 | 2712196.6965 | 1094326.4312
47 | 2712215.0099 | 1094388.1219 | 2712207.4127 | 1094369.7804
48 | 2712207.4127 | 1094369.7804 | 2712211.0794 | 1094368.0469
49 | 2712215.0099 | 1094388.1219 | 2712221.8896 | 1094387.8264 | 2712227.53 | 1094399.6607 | 2712231.171 | 1094404.3532
50 | 2712211.0794 | 1094368.0469 | 2712202.4596 | 1094344.6387 | 2712198.92 | 1094333.4559
51 | 2712196.6965 | 1094326.4312 | 2712198.92 | 1094333.4559
52 | 2712198.92 | 1094333.4559 | 2712255.1188 | 1094312.7357
53 | 2712255.1188 | 1094312.7357 | 2712255.3267 | 1094313.3487 | 2712263.6817 | 1094334.7174 | 2712264.2085 | 1094335.6208
54 | 2712251.4826 | 1094302.013 | 2712255.1188 | 1094312.7357
55 | 2712251.4826 | 1094302.013 | 2712297.32 | 1094251.231
56 | 2712282.3145 | 1094237.9855 | 2712285.6148 | 1094240.7254 | 2712297.32 | 1094251.231
57 | 2712268.669 | 1094343.2704 | 2712264.2085 | 1094335.6208
58 | 2712268.669 | 1094343.2704 | 2712274.6108 | 1094353.4603
59 | 2712279.5678 | 1094360.7726 | 2712276.5798 | 1094356.8371 | 2712274.6108 | 1094353.4603
60 | 2712264.1945 | 1094422.0691 | 2712259.9442 | 1094414.1243 | 2712253.8614 | 1094401.0698 | 2712246.2836 | 1094390.9166
61 | 2712264.1945 | 1094422.0691 | 2712268.6612 | 1094430.4185
62 | 2712076.4847 | 1094439.9802 | 2712069.8311 | 1094435.588 | 2712068.0624 | 1094434.4212 | 2712052.6258 | 1094430.1561 | 2712044.2045 | 1094430.0009 | 2712039.4384 | 1094435.8837
63 | 2712076.4847 | 1094439.9802 | 2712082.5259 | 1094443.9609 | 2712101.8302 | 1094464.9976 | 2712112.7007 | 1094476.8401
64 | 2712197.8725 | 1094461.8349 | 2712112.7007 | 1094476.8401
65 | 2712259.7663 | 1094464.0325 | 2712197.8725 | 1094461.8349
66 | 2712259.7663 | 1094464.0325 | 2712264.3549 | 1094463.995 | 2712267.4176 | 1094469.3662 | 2712274.5226 | 1094481.6168 | 2712275.8297 | 1094483.1654
67 | 2712259.7663 | 1094464.0325 | 2712262.3401 | 1094469.4701
68 | 2712299.6501 | 1094379.2902 | 2712310.5821 | 1094389.7983 | 2712312.9587 | 1094391.9607
69 | 2712289.5655 | 1094369.5966 | 2712299.6501 | 1094379.2902
70 | 2712312.9587 | 1094391.9607 | 2712326.6561 | 1094404.4235
71 | 2712289.5655 | 1094369.5966 | 2712295.4318 | 1094380.1065
72 | 2712289.5655 | 1094369.5966 | 2712281.9138 | 1094363.8626 | 2712279.7123 | 1094360.9629
73 | 2712279.7123 | 1094360.9629 | 2712279.5678 | 1094360.7726
74 | 2712295.4318 | 1094380.1065 | 2712304.7206 | 1094396.7484
75 | 2712309.0172 | 1094404.446 | 2712304.7206 | 1094396.7484
76 | 2712290.3446 | 1094444.9623 | 2712309.0172 | 1094404.446
77 | 2712290.3446 | 1094444.9623 | 2712289.3711 | 1094443.8765 | 2712274.1101 | 1094440.6037 | 2712268.6612 | 1094430.4185
78 | 2712296.9702 | 1094452.7012 | 2712291.4896 | 1094446.2395 | 2712290.3446 | 1094444.9623
79 | 2712296.9702 | 1094452.7012 | 2712304.0204 | 1094461.0137
80 | 2712293.0368 | 1094503.5525 | 2712275.8297 | 1094483.1654
81 | 2712291.5568 | 1094548.2986 | 2712288.4201 | 1094534.3535 | 2712286.0069 | 1094523.6127 | 2712280.0689 | 1094506.9252 | 2712262.3401 | 1094469.4701
82 | 2712291.5568 | 1094548.2986 | 2712287.5516 | 1094547.8021 | 2712273.9099 | 1094522.333 | 2712261.7992 | 1094512.147
83 | 2712310.7478 | 1094524.5365 | 2712293.0368 | 1094503.5525
84 | 2712310.7478 | 1094524.5365 | 2712317.2115 | 1094532.1948 | 2712322.0349 | 1094532.4507 | 2712326.5804 | 1094529.7106 | 2712336.494 | 1094515.7843 | 2712340.6448 | 1094507.5665 | 2712339.4013 | 1094502.7292 | 2712339.4013 | 1094502.7292
85 | 2712334.6827 | 1094497.1658 | 2712339.4013 | 1094502.7292
86 | 2712334.6827 | 1094497.1658 | 2712322.4462 | 1094482.7385
87 | 2712315.9042 | 1094475.0252 | 2712322.4462 | 1094482.7385
88 | 2712315.9042 | 1094475.0252 | 2712315.6113 | 1094474.6798
89 | 2712306.5443 | 1094463.9895 | 2712315.6113 | 1094474.6798
90 | 2712306.5443 | 1094463.9895 | 2712304.0204 | 1094461.0137

## bus_geodata
| x | y | coords
0 | 2712007.3585 | 1094045.9075
1 | 2712010.7827 | 1094049.0602
2 | 2712033.5197 | 1094069.9943
3 | 2712072.3593 | 1094060.181
4 | 2712034.1692 | 1094004.9068
5 | 2712025.1452 | 1094012.7692
6 | 2712082.6613 | 1094082.9681
7 | 2712083.9415 | 1094099.8644
8 | 2712087.9892 | 1094113.2716
9 | 2712082.2651 | 1094119.3925
10 | 2712096.5997 | 1094118.7581
11 | 2712076.3587 | 1094108.921
12 | 2712094.7426 | 1094132.2789
13 | 2712107.8297 | 1094127.3367
14 | 2712015.3482 | 1094021.3049
15 | 2712151.2194 | 1094122.7437
16 | 2712048.2012 | 1094148.9675
17 | 2712065.3846 | 1094163.1361
18 | 2712077.5868 | 1094174.3205
19 | 2712088.4569 | 1094188.5945
20 | 2712100.8552 | 1094207.0585
21 | 2712105.9597 | 1094214.6602
22 | 2712129.132 | 1094154.786
23 | 2712152.5763 | 1094170.9925
24 | 2712116.0309 | 1094145.5547
25 | 2712157.4823 | 1094174.3607
26 | 2712162.1221 | 1094191.1577
27 | 2712155.9726 | 1094146.5415
28 | 2712175.4828 | 1094213.9904
29 | 2712176.1898 | 1094228.5316
30 | 2712119.7813 | 1094235.1695
31 | 2712052.1125 | 1094199.2305
32 | 2712141.5842 | 1094262.723
33 | 2712080.9614 | 1094277.704
34 | 2712022.2266 | 1094333.3501
35 | 2712007.844 | 1094349.5879
36 | 2712041.2746 | 1094322.8301
37 | 2711980.1172 | 1094340.1932
38 | 2712020.5223 | 1094362.782
39 | 2711967.374 | 1094334.8439
40 | 2712156.9933 | 1094279.8118
41 | 2712077.8301 | 1094324.1601
42 | 2712176.5829 | 1094234.542
43 | 2712179.475 | 1094253.0348
44 | 2712165.7742 | 1094282.0632
45 | 2712186.9162 | 1094295.352
46 | 2712207.4127 | 1094369.7804
47 | 2712215.0099 | 1094388.1219
48 | 2712211.0794 | 1094368.0469
49 | 2712196.6965 | 1094326.4312
50 | 2712198.92 | 1094333.4559
51 | 2712231.171 | 1094404.3532
52 | 2712255.1188 | 1094312.7357
53 | 2712251.4826 | 1094302.013
54 | 2712297.32 | 1094251.231
55 | 2712282.3145 | 1094237.9855
56 | 2712264.2085 | 1094335.6208
57 | 2712268.669 | 1094343.2704
58 | 2712274.6108 | 1094353.4603
59 | 2712246.2836 | 1094390.9166
60 | 2712264.1945 | 1094422.0691
61 | 2712076.4847 | 1094439.9802
62 | 2712039.4384 | 1094435.8837
63 | 2712112.7007 | 1094476.8401
64 | 2712197.8725 | 1094461.8349
65 | 2712259.7663 | 1094464.0325
66 | 2712007.3229 | 1094028.2971
67 | 2712299.6501 | 1094379.2902
68 | 2712312.9587 | 1094391.9607
69 | 2712289.5655 | 1094369.5966
70 | 2712279.5678 | 1094360.7726
71 | 2712279.7123 | 1094360.9629
72 | 2712295.4318 | 1094380.1065
73 | 2712304.7206 | 1094396.7484
74 | 2712309.0172 | 1094404.446
75 | 2712290.3446 | 1094444.9623
76 | 2712268.6612 | 1094430.4185
77 | 2712296.9702 | 1094452.7012
78 | 2712326.6561 | 1094404.4235
79 | 2712275.8297 | 1094483.1654
80 | 2712262.3401 | 1094469.4701
81 | 2712291.5568 | 1094548.2986
82 | 2712261.7992 | 1094512.147
83 | 2712293.0368 | 1094503.5525
84 | 2712310.7478 | 1094524.5365
85 | 2712339.4013 | 1094502.7292
86 | 2712334.6827 | 1094497.1658
87 | 2712322.4462 | 1094482.7385
88 | 2712315.9042 | 1094475.0252
89 | 2712315.6113 | 1094474.6798
90 | 2712306.5443 | 1094463.9895
91 | 2712304.0204 | 1094461.0137
92 | 2712196.6965 | 1094326.4312

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1