## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5249-6_2_3_node_10 | 0.4 | n |  | TRUE
1 | bus_LV_5249-6_2_3_node_11 | 0.4 | n |  | TRUE
2 | bus_LV_5249-6_2_3_node_12 | 0.4 | n |  | TRUE
3 | bus_LV_5249-6_2_3_node_13 | 0.4 | n |  | TRUE
4 | bus_LV_5249-6_2_3_node_14 | 0.4 | n |  | TRUE
5 | bus_LV_5249-6_2_3_node_19 | 0.4 | n |  | TRUE
6 | bus_LV_5249-6_2_3_node_26 | 0.4 | n |  | TRUE
7 | bus_LV_5249-6_2_3_node_15 | 0.4 | n |  | TRUE
8 | bus_LV_5249-6_2_3_node_16 | 0.4 | n |  | TRUE
9 | bus_LV_5249-6_2_3_node_18 | 0.4 | n |  | TRUE
10 | bus_LV_5249-6_2_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_5249-6_2_3_node_124 | 0.4 | n |  | TRUE
12 | bus_LV_5249-6_2_3_node_128 | 0.4 | n |  | TRUE
13 | bus_LV_5249-6_2_3_node_129 | 0.4 | n |  | TRUE
14 | bus_LV_5249-6_2_3_node_144 | 0.4 | n |  | TRUE
15 | bus_LV_5249-6_2_3_node_117 | 0.4 | n |  | TRUE
16 | bus_LV_5249-6_2_3_node_21 | 0.4 | n |  | TRUE
17 | bus_LV_5249-6_2_3_node_22 | 0.4 | n |  | TRUE
18 | bus_LV_5249-6_2_3_node_23 | 0.4 | n |  | TRUE
19 | bus_LV_5249-6_2_3_node_24 | 0.4 | n |  | TRUE
20 | bus_LV_5249-6_2_3_node_127 | 0.4 | n |  | TRUE
21 | bus_LV_5249-6_2_3_node_126 | 0.4 | n |  | TRUE
22 | bus_LV_5249-6_2_3_node_84 | 0.4 | n |  | TRUE
23 | bus_LV_5249-6_2_3_node_92 | 0.4 | n |  | TRUE
24 | bus_LV_5249-6_2_3_node_91 | 0.4 | n |  | TRUE
25 | bus_LV_5249-6_2_3_node_120 | 0.4 | n |  | TRUE
26 | bus_LV_5249-6_2_3_node_119 | 0.4 | n |  | TRUE
27 | bus_LV_5249-6_2_3_node_130 | 0.4 | n |  | TRUE
28 | bus_LV_5249-6_2_3_node_86 | 0.4 | n |  | TRUE
29 | bus_LV_5249-6_2_3_node_87 | 0.4 | n |  | TRUE
30 | bus_LV_5249-6_2_3_node_82 | 0.4 | n |  | TRUE
31 | bus_LV_5249-6_2_3_node_83 | 0.4 | n |  | TRUE
32 | bus_LV_5249-6_2_3_node_85 | 0.4 | n |  | TRUE
33 | bus_LV_5249-6_2_3_node_93 | 0.4 | n |  | TRUE
34 | bus_LV_5249-6_2_3_node_94 | 0.4 | n |  | TRUE
35 | bus_LV_5249-6_2_3_node_88 | 0.4 | n |  | TRUE
36 | bus_LV_5249-6_2_3_node_100 | 0.4 | n |  | TRUE
37 | bus_LV_5249-6_2_3_node_98 | 0.4 | n |  | TRUE
38 | bus_LV_5249-6_2_3_node_95 | 0.4 | n |  | TRUE
39 | bus_LV_5249-6_2_3_node_104 | 0.4 | n |  | TRUE
40 | bus_LV_5249-6_2_3_node_105 | 0.4 | n |  | TRUE
41 | bus_LV_5249-6_2_3_node_106 | 0.4 | n |  | TRUE
42 | bus_LV_5249-6_2_3_node_96 | 0.4 | n |  | TRUE
43 | bus_LV_5249-6_2_3_node_97 | 0.4 | n |  | TRUE
44 | bus_LV_5249-6_2_3_node_99 | 0.4 | n |  | TRUE
45 | bus_LV_5249-6_2_3_node_101 | 0.4 | n |  | TRUE
46 | bus_LV_5249-6_2_3_node_102 | 0.4 | n |  | TRUE
47 | bus_LV_5249-6_2_3_node_108 | 0.4 | n |  | TRUE
48 | bus_LV_5249-6_2_3_node_103 | 0.4 | n |  | TRUE
49 | bus_LV_5249-6_2_3_node_107 | 0.4 | n |  | TRUE
50 | bus_LV_5249-6_2_3_node_113 | 0.4 | n |  | TRUE
51 | bus_LV_5249-6_2_3_node_118 | 0.4 | n |  | TRUE
52 | bus_LV_5249-6_2_3_node_112 | 0.4 | n |  | TRUE
53 | bus_LV_5249-6_2_3_node_109 | 0.4 | n |  | TRUE
54 | bus_LV_5249-6_2_3_node_110 | 0.4 | n |  | TRUE
55 | bus_LV_5249-6_2_3_node_111 | 0.4 | n |  | TRUE
56 | bus_LV_5249-6_2_3_node_116 | 0.4 | n |  | TRUE
57 | bus_LV_5249-6_2_3_node_143 | 0.4 | n |  | TRUE
58 | bus_LV_5249-6_2_3_node_114 | 0.4 | n |  | TRUE
59 | bus_LV_5249-6_2_3_node_142 | 0.4 | n |  | TRUE
60 | bus_LV_5249-6_2_3_node_115 | 0.4 | n |  | TRUE
61 | bus_LV_5249-6_2_3_node_121 | 0.4 | n |  | TRUE
62 | bus_LV_5249-6_2_3_node_122 | 0.4 | n |  | TRUE
63 | bus_LV_5249-6_2_3_node_123 | 0.4 | n |  | TRUE
64 | bus_LV_5249-6_2_3_node_125 | 0.4 | n |  | TRUE
65 | bus_LV_5249-6_2_3_node_138 | 0.4 | n |  | TRUE
66 | bus_LV_5249-6_2_3_node_131 | 0.4 | n |  | TRUE
67 | bus_LV_5249-6_2_3_node_132 | 0.4 | n |  | TRUE
68 | bus_LV_5249-6_2_3_node_133 | 0.4 | n |  | TRUE
69 | bus_LV_5249-6_2_3_node_134 | 0.4 | n |  | TRUE
70 | bus_LV_5249-6_2_3_node_135 | 0.4 | n |  | TRUE
71 | bus_LV_5249-6_2_3_node_136 | 0.4 | n |  | TRUE
72 | bus_LV_5249-6_2_3_node_137 | 0.4 | n |  | TRUE
73 | bus_LV_5249-6_2_3_node_139 | 0.4 | n |  | TRUE
74 | bus_LV_5249-6_2_3_node_140 | 0.4 | n |  | TRUE
75 | bus_LV_5249-6_2_3_node_141 | 0.4 | n |  | TRUE
76 | bus_MV_68_0_node_56 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5249-6_2_3_load_10 | 0 | 0.00092891 | 0.00023281 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5249-6_2_3_load_11 | 1 | 0.0018943 | 0.00047474 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5249-6_2_3_load_13 | 3 | 0.0015234 | 0.00038181 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5249-6_2_3_load_14 | 4 | 0.0011743 | 0.00029431 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5249-6_2_3_load_19 | 5 | 0.0033639 | 0.00084308 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5249-6_2_3_load_26 | 6 | 0.0020289 | 0.00050848 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5249-6_2_3_load_15 | 7 | 0.0016033 | 0.00040182 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5249-6_2_3_load_16 | 8 | 0.0017875 | 0.00044798 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5249-6_2_3_load_18 | 9 | 0.0014778 | 0.00037038 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5249-6_2_3_load_124 | 11 | 0.0029065 | 0.00072845 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5249-6_2_3_load_128 | 12 | 0.0031997 | 0.00080193 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5249-6_2_3_load_129 | 13 | 0.0017145 | 0.00042968 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5249-6_2_3_load_144 | 14 | 0.0037314 | 0.00093517 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5249-6_2_3_load_21 | 16 | 0.00099298 | 0.00024887 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5249-6_2_3_load_22 | 17 | 0.001359 | 0.00034059 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5249-6_2_3_load_127 | 20 | 0.0032876 | 0.00082396 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5249-6_2_3_load_92 | 23 | 0.0027579 | 0.00069119 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5249-6_2_3_load_91 | 24 | 0.0047988 | 0.0012027 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5249-6_2_3_load_120 | 25 | 0.0033617 | 0.00084251 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5249-6_2_3_load_119 | 26 | 0.0026291 | 0.00065893 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5249-6_2_3_load_130 | 27 | 0.0015532 | 0.00038926 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5249-6_2_3_load_86 | 28 | 0.0006813 | 0.00017075 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5249-6_2_3_load_82 | 30 | 0.0010951 | 0.00027445 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5249-6_2_3_load_93 | 33 | 0.0063167 | 0.0015831 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5249-6_2_3_load_88 | 35 | 0.0018308 | 0.00045883 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5249-6_2_3_load_100 | 36 | 0.0028148 | 0.00070547 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5249-6_2_3_load_95 | 38 | 0.0018107 | 0.0004538 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5249-6_2_3_load_104 | 39 | 0.0025203 | 0.00063164 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5249-6_2_3_load_105 | 40 | 0.0042629 | 0.0010684 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5249-6_2_3_load_106 | 41 | 0.0058425 | 0.0014643 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5249-6_2_3_load_96 | 42 | 0.0054302 | 0.0013609 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5249-6_2_3_load_97 | 43 | 0.0051698 | 0.0012957 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5249-6_2_3_load_99 | 44 | 0.0016615 | 0.00041641 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5249-6_2_3_load_101 | 45 | 0.003066 | 0.00076841 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5249-6_2_3_load_102 | 46 | 0.0020597 | 0.00051621 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5249-6_2_3_load_108 | 47 | 0.0018763 | 0.00047024 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5249-6_2_3_load_103 | 48 | 0.0093609 | 0.0023461 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5249-6_2_3_load_107 | 49 | 0.0042882 | 0.0010747 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5249-6_2_3_load_113 | 50 | 0.0016626 | 0.0004167 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5249-6_2_3_load_118 | 51 | 0.0024825 | 0.00062217 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5249-6_2_3_load_112 | 52 | 0.0018837 | 0.00047211 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5249-6_2_3_load_110 | 54 | 0.0030132 | 0.00075518 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5249-6_2_3_load_116 | 56 | 0.0020147 | 0.00050494 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5249-6_2_3_load_143 | 57 | 0.0020569 | 0.00051551 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5249-6_2_3_load_114 | 58 | 0.0033936 | 0.00085052 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5249-6_2_3_load_142 | 59 | 0.0029916 | 0.00074976 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5249-6_2_3_load_115 | 60 | 0.0022164 | 0.00055549 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5249-6_2_3_load_121 | 61 | 0.0016984 | 0.00042566 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5249-6_2_3_load_122 | 62 | 0.0023831 | 0.00059727 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5249-6_2_3_load_123 | 63 | 0.00092807 | 0.0002326 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5249-6_2_3_load_125 | 64 | 0.0014121 | 0.0003539 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5249-6_2_3_load_138 | 65 | 0.00058886 | 0.00014758 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5249-6_2_3_load_131 | 66 | 0.0014915 | 0.00037381 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5249-6_2_3_load_132 | 67 | 0.001166 | 0.00029223 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5249-6_2_3_load_133 | 68 | 0.0032197 | 0.00080694 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5249-6_2_3_load_134 | 69 | 0.0021408 | 0.00053652 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5249-6_2_3_load_135 | 70 | 0.0055227 | 0.0013841 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5249-6_2_3_load_136 | 71 | 0.0090212 | 0.0022609 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5249-6_2_3_load_137 | 72 | 0.0019598 | 0.00049117 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5249-6_2_3_load_139 | 73 | 0.0021819 | 0.00054683 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5249-6_2_3_load_140 | 74 | 0.0038729 | 0.00097064 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5249-6_2_3_load_141 | 75 | 0.0034691 | 0.00086944 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 59 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5249-6_2_3_line_0 |  | 0 | 1 | 0.121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5249-6_2_3_line_1 |  | 0 | 2 | 0.35752 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5249-6_2_3_line_2 |  | 1 | 3 | 0.15123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5249-6_2_3_line_3 |  | 2 | 4 | 0.086927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5249-6_2_3_line_4 |  | 3 | 5 | 0.0010635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5249-6_2_3_line_5 |  | 5 | 6 | 0.037324 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5249-6_2_3_line_6 |  | 6 | 13 | 0.025127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5249-6_2_3_line_7 |  | 7 | 8 | 0.135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5249-6_2_3_line_8 |  | 8 | 9 | 0.32472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5249-6_2_3_line_9 |  | 9 | 10 | 0.024508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5249-6_2_3_line_10 |  | 10 | 11 | 0.005218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5249-6_2_3_line_11 |  | 10 | 12 | 0.0047034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5249-6_2_3_line_12 |  | 11 | 14 | 0.016975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5249-6_2_3_line_13 |  | 11 | 15 | 0.014918 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5249-6_2_3_line_14 |  | 13 | 27 | 0.0090053 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5249-6_2_3_line_15 |  | 14 | 65 | 0.0024638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5249-6_2_3_line_16 |  | 15 | 61 | 0.0019173 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5249-6_2_3_line_17 |  | 15 | 60 | 0.0066142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5249-6_2_3_line_18 |  | 16 | 17 | 0.12727 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5249-6_2_3_line_19 |  | 17 | 18 | 0.33691 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5249-6_2_3_line_20 |  | 18 | 19 | 0.005543 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5249-6_2_3_line_21 |  | 19 | 20 | 0.04236 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5249-6_2_3_line_22 |  | 20 | 21 | 0.0097583 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5249-6_2_3_line_23 |  | 21 | 64 | 0.012748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5249-6_2_3_line_24 |  | 22 | 23 | 0.03171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5249-6_2_3_line_25 |  | 22 | 24 | 0.076659 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5249-6_2_3_line_26 |  | 23 | 34 | 0.0052337 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5249-6_2_3_line_27 |  | 25 | 26 | 0.037835 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5249-6_2_3_line_28 |  | 26 | 51 | 0.0011522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5249-6_2_3_line_29 |  | 27 | 66 | 0.0046327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5249-6_2_3_line_30 |  | 28 | 29 | 0.45529 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5249-6_2_3_line_31 |  | 29 | 35 | 0.031561 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5249-6_2_3_line_32 |  | 30 | 31 | 0.54014 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5249-6_2_3_line_33 |  | 31 | 32 | 0.025492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5249-6_2_3_line_34 |  | 32 | 33 | 0.065116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5249-6_2_3_line_35 |  | 33 | 34 | 0.029554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5249-6_2_3_line_36 |  | 34 | 38 | 0.0028459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5249-6_2_3_line_37 |  | 35 | 36 | 0.03525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5249-6_2_3_line_38 |  | 36 | 37 | 0.011269 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5249-6_2_3_line_39 |  | 37 | 45 | 0.045427 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5249-6_2_3_line_40 |  | 37 | 42 | 0.059965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5249-6_2_3_line_41 |  | 38 | 39 | 0.023303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5249-6_2_3_line_42 |  | 39 | 40 | 0.007712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5249-6_2_3_line_43 |  | 39 | 41 | 0.019596 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5249-6_2_3_line_44 |  | 40 | 50 | 0.0044468 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5249-6_2_3_line_45 |  | 41 | 51 | 0.00046584 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5249-6_2_3_line_46 |  | 42 | 43 | 0.012938 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5249-6_2_3_line_47 |  | 43 | 44 | 0.0013637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5249-6_2_3_line_48 |  | 44 | 46 | 0.013868 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5249-6_2_3_line_49 |  | 45 | 47 | 0.016331 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5249-6_2_3_line_50 |  | 46 | 48 | 0.0018998 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5249-6_2_3_line_51 |  | 47 | 49 | 0.017191 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5249-6_2_3_line_52 |  | 49 | 53 | 0.0087075 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5249-6_2_3_line_53 |  | 50 | 52 | 0.0068092 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5249-6_2_3_line_54 |  | 52 | 54 | 0.013777 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5249-6_2_3_line_55 |  | 53 | 54 | 0.0075747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5249-6_2_3_line_56 |  | 53 | 55 | 0.003203 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5249-6_2_3_line_57 |  | 55 | 56 | 0.0036761 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5249-6_2_3_line_58 |  | 55 | 57 | 0.014657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_5249-6_2_3_line_59 |  | 56 | 58 | 0.010566 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5249-6_2_3_line_60 |  | 57 | 59 | 0.0020205 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_5249-6_2_3_line_61 |  | 58 | 60 | 0.0035589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5249-6_2_3_line_62 |  | 59 | 74 | 0.013228 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5249-6_2_3_line_63 |  | 61 | 62 | 0.0026668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5249-6_2_3_line_64 |  | 62 | 63 | 0.022082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5249-6_2_3_line_65 |  | 63 | 64 | 0.0037303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5249-6_2_3_line_66 |  | 65 | 72 | 0.0067879 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5249-6_2_3_line_67 |  | 66 | 67 | 0.0040846 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5249-6_2_3_line_68 |  | 67 | 68 | 0.011475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5249-6_2_3_line_69 |  | 68 | 69 | 0.00046641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5249-6_2_3_line_70 |  | 69 | 70 | 0.013452 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5249-6_2_3_line_71 |  | 70 | 71 | 0.015623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5249-6_2_3_line_72 |  | 71 | 72 | 0.0014041 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5249-6_2_3_line_73 |  | 73 | 74 | 0.012326 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5249-6_2_3_line_74 |  | 73 | 75 | 0.0041368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5249-6_2_3_trafo_142 | 0.63 MVA 20/0.4 kV | 76 | 59 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21 | x22 | y22 | x23 | y23 | x24 | y24 | x25 | y25 | x26 | y26 | x27 | y27 | x28 | y28 | x29 | y29 | x30 | y30 | x31 | y31 | x32 | y32 | x33 | y33 | x34 | y34 | x35 | y35 | x36 | y36 | x37 | y37 | x38 | y38 | x39 | y39 | x40 | y40 | x41 | y41 | x42 | y42
0 | 2722956.7022 | 1082308.2672 | 2723031.2214 | 1082322.2037 | 2723071.4829 | 1082342.7124
1 | 2722760.1655 | 1082265.8295 | 2722827.6664 | 1082250.4453 | 2722909.4654 | 1082246.5696 | 2722979.4464 | 1082210.7001 | 2723000.0803 | 1082218.0219 | 2722957.5105 | 1082268.2435 | 2722956.7022 | 1082308.2672 | 2722956.7022 | 1082308.2672
2 | 2723215.8962 | 1082370.0311 | 2723127.1894 | 1082371.0886 | 2723071.4829 | 1082342.7124
3 | 2722676.3685 | 1082245.1603 | 2722692.1443 | 1082244.2328 | 2722760.1655 | 1082265.8295
4 | 2723215.8962 | 1082370.0311 | 2723216.9597 | 1082370.0184
5 | 2723216.9597 | 1082370.0184 | 2723228.1767 | 1082369.8847 | 2723254.2518 | 1082371.1575 | 2723254.2518 | 1082371.1575
6 | 2723254.2518 | 1082371.1575 | 2723271.5156 | 1082365.3803 | 2723277.7932 | 1082362.4625
7 | 2723131.6896 | 1082794.9645 | 2723136.4815 | 1082786.7324 | 2723187.3808 | 1082710.4505 | 2723187.932 | 1082676.6817
8 | 2723187.932 | 1082676.6817 | 2723187.932 | 1082676.6817 | 2723319.0632 | 1082539.9576 | 2723363.5771 | 1082427.5773 | 2723364.2092 | 1082423.9764 | 2723363.8144 | 1082418.1642 | 2723362.9734 | 1082413.3178
9 | 2723356.4847 | 1082389.7397 | 2723357.6597 | 1082396.5239 | 2723360.1502 | 1082404.3022 | 2723362.8269 | 1082412.4734 | 2723362.9734 | 1082413.3178
10 | 2723356.4847 | 1082389.7397 | 2723352.6664 | 1082386.1709
11 | 2723356.4847 | 1082389.7397 | 2723358.8463 | 1082390.4658 | 2723360.1926 | 1082392.2469
12 | 2723352.6664 | 1082386.1709 | 2723349.0006 | 1082382.7387 | 2723339.5761 | 1082375.3862
13 | 2723364.678 | 1082377.4522 | 2723355.7527 | 1082382.9422 | 2723352.6664 | 1082386.1709
14 | 2723277.7932 | 1082362.4625 | 2723285.9596 | 1082358.6668
15 | 2723339.5761 | 1082375.3862 | 2723337.6335 | 1082373.8707
16 | 2723364.678 | 1082377.4522 | 2723365.5245 | 1082379.1725
17 | 2723364.678 | 1082377.4522 | 2723363.2581 | 1082373.9432 | 2723362.3339 | 1082371.2697
18 | 2723517.0364 | 1082693.0643 | 2723513.2805 | 1082694.2254 | 2723502.8407 | 1082696.293 | 2723488.3617 | 1082697.6561 | 2723414.684 | 1082699.1755 | 2723405.7306 | 1082699.1719 | 2723401.0118 | 1082699.0429 | 2723397.9406 | 1082699.2364 | 2723395.2423 | 1082699.8044 | 2723392.182 | 1082700.9878 | 2723390.7217 | 1082701.7925
19 | 2723385.9629 | 1082474.4645 | 2723385.4429 | 1082522.3553 | 2723386.5195 | 1082551.2314 | 2723385.9371 | 1082557.7465 | 2723384.9153 | 1082562.1846 | 2723383.2013 | 1082566.6754 | 2723380.1475 | 1082572.5178 | 2723361.5061 | 1082606.4538 | 2723357.6129 | 1082615.0145 | 2723355.1275 | 1082622.703 | 2723352.9091 | 1082631.3978 | 2723351.0892 | 1082642.6468 | 2723348.6436 | 1082661.0217 | 2723347.4949 | 1082664.4454 | 2723346.0806 | 1082667.1743 | 2723343.5925 | 1082670.0149 | 2723339.6259 | 1082673.3926 | 2723334.774 | 1082677.9199 | 2723332.8646 | 1082680.1717 | 2723331.8727 | 1082681.9863 | 2723331.1548 | 1082684.4624 | 2723331.1233 | 1082687.1638 | 2723331.4233 | 1082694.2083 | 2723332.4702 | 1082706.9275 | 2723332.0906 | 1082711.1007 | 2723330.7448 | 1082718.501 | 2723330.3118 | 1082723.3958 | 2723330.8796 | 1082726.7986 | 2723331.8277 | 1082729.0639 | 2723333.5999 | 1082730.5119 | 2723335.7274 | 1082731.2889 | 2723338.7761 | 1082731.4396 | 2723342.6815 | 1082730.3178 | 2723345.7825 | 1082728.6572 | 2723372.565 | 1082711.7983 | 2723390.7217 | 1082701.7925
20 | 2723385.9629 | 1082474.4645 | 2723385.8267 | 1082468.9244
21 | 2723385.8267 | 1082468.9244 | 2723385.7467 | 1082465.9762 | 2723385.2397 | 1082449.9877 | 2723384.6023 | 1082436.9876 | 2723383.1934 | 1082426.6847
22 | 2723381.5423 | 1082417.0779 | 2723382.3366 | 1082420.4186 | 2723383.1934 | 1082426.6847
23 | 2723381.5423 | 1082417.0779 | 2723380.7022 | 1082414.081 | 2723379.1083 | 1082409.1896 | 2723377.4329 | 1082405.0228
24 | 2723398.9508 | 1082282.6887 | 2723397.5557 | 1082284.8509 | 2723396.1858 | 1082297.2655 | 2723393.9876 | 1082313.7662
25 | 2723398.9508 | 1082282.6887 | 2723404.1929 | 1082272.721 | 2723461.3867 | 1082241.0103
26 | 2723390.4459 | 1082317.6195 | 2723393.9876 | 1082313.7662
27 | 2723391.9633 | 1082360.0758 | 2723393.4551 | 1082365.3372 | 2723398.4788 | 1082368.4412 | 2723400.7842 | 1082391.4824 | 2723401.5771 | 1082394.6902
28 | 2723391.7032 | 1082358.9535 | 2723391.933 | 1082359.9692 | 2723391.9633 | 1082360.0758
29 | 2723285.9596 | 1082358.6668 | 2723290.1607 | 1082356.7141
30 | 2723212.6072 | 1082331.4643 | 2723190.5158 | 1082326.7364 | 2723153.3734 | 1082318.98 | 2723140.7177 | 1082317.3119 | 2723135.4607 | 1082316.1382 | 2723131.2346 | 1082314.6739 | 2723122.3263 | 1082310.4909 | 2723101.6019 | 1082301.1432 | 2723089.0789 | 1082296.3646 | 2723086.7469 | 1082294.9386 | 2723084.8299 | 1082292.576 | 2723083.947 | 1082289.7672 | 2723083.8231 | 1082287.0628 | 2723084.6353 | 1082283.3765 | 2723086.0132 | 1082280.5245 | 2723087.5424 | 1082278.2538 | 2723089.6987 | 1082276.4627 | 2723094.2509 | 1082274.0863 | 2723105.2144 | 1082270.7275 | 2723118.6031 | 1082264.5714 | 2723129.472 | 1082258.2086 | 2723135.3058 | 1082253.5231 | 2723149.8417 | 1082236.3377 | 2723153.4041 | 1082230.6834 | 2723156.1898 | 1082225.0356 | 2723158.4987 | 1082219.545 | 2723160.4352 | 1082212.1121 | 2723161.4168 | 1082205.0491 | 2723162.5265 | 1082180.1312 | 2723162.4419 | 1082165.8859 | 2723156.2348 | 1082143.333 | 2723150.5775 | 1082119.7016 | 2723152.4633 | 1082109.3989 | 2723156.2137 | 1082096.3764 | 2723159.5872 | 1082078.565 | 2723159.92 | 1082073.2457 | 2723159.8101 | 1082068.6957 | 2723159.0605 | 1082064.2885 | 2723156.1097 | 1082055.8227 | 2723153.716 | 1082051.3044 | 2723150.171 | 1082046.1068 | 2723142.3709 | 1082036.6423 | 2723129.6263 | 1082023.168
31 | 2723212.6072 | 1082331.4643 | 2723231.7839 | 1082334.0095 | 2723242.035 | 1082335.151 | 2723243.9323 | 1082335.2757
32 | 2723336.2323 | 1082255.8995 | 2723330.4486 | 1082249.2888 | 2723321.6931 | 1082257.1172 | 2723284.6596 | 1082295.3622 | 2723248.9429 | 1082308.0933 | 2723202.4616 | 1082308.9873 | 2723180.0563 | 1082310.1797 | 2723156.1782 | 1082300.1008 | 2723125.4313 | 1082292.5073 | 2723146.8393 | 1082282.2658 | 2723154.5365 | 1082270.3016 | 2723167.6849 | 1082245.316 | 2723180.5587 | 1082213.1752 | 2723179.9456 | 1082183.2078 | 2723174.082 | 1082144.8282 | 2723183.459 | 1082100.1298 | 2723185.1053 | 1082064.4372 | 2723190.513 | 1082023.239 | 2723189.1588 | 1082013.9604
33 | 2723316.137 | 1082271.0927 | 2723321.8272 | 1082264.3029 | 2723336.2323 | 1082255.8995
34 | 2723316.137 | 1082271.0927 | 2723376.4794 | 1082295.5652
35 | 2723390.4459 | 1082317.6195 | 2723391.341 | 1082315.2248 | 2723392.3942 | 1082311.9215 | 2723392.0755 | 1082309.6356 | 2723391.2284 | 1082307.7505 | 2723379.0817 | 1082298.2087 | 2723376.4794 | 1082295.5652
36 | 2723390.4459 | 1082317.6195 | 2723388.5205 | 1082319.7152
37 | 2723243.9323 | 1082335.2757 | 2723251.8069 | 1082335.7935 | 2723257.6613 | 1082335.8453 | 2723262.1484 | 1082335.1578 | 2723266.231 | 1082334.1174 | 2723271.8783 | 1082332.1191 | 2723278.0884 | 1082329.4471
38 | 2723288.4396 | 1082324.9935 | 2723278.0884 | 1082329.4471
39 | 2723288.4396 | 1082324.9935 | 2723310.5158 | 1082317.0455 | 2723316.5375 | 1082315.3551 | 2723319.7986 | 1082314.9986 | 2723322.9593 | 1082315.385 | 2723327.285 | 1082316.529 | 2723331.2672 | 1082318.1441 | 2723331.6958 | 1082318.3445
40 | 2723288.4396 | 1082324.9935 | 2723293.075 | 1082319.2831 | 2723301.2608 | 1082311.1985 | 2723305.8215 | 1082307.6437 | 2723310.6179 | 1082304.7164 | 2723313.9126 | 1082303.4711 | 2723316.3218 | 1082302.9973 | 2723318.8287 | 1082303.0703 | 2723321.5342 | 1082303.6922 | 2723333.191 | 1082307.1306 | 2723339.1698 | 1082309.08
41 | 2723388.8782 | 1082339.4147 | 2723382.7363 | 1082325.9584 | 2723384.2678 | 1082324.3438 | 2723388.5205 | 1082319.7152
42 | 2723388.8782 | 1082339.4147 | 2723381.8183 | 1082342.5184 | 2723381.8183 | 1082342.5184
43 | 2723388.8782 | 1082339.4147 | 2723390.3858 | 1082344.3488 | 2723391.5771 | 1082351.8561 | 2723390.7855 | 1082354.8979 | 2723391.6004 | 1082358.4992
44 | 2723378.2281 | 1082339.8946 | 2723381.8183 | 1082342.5184
45 | 2723391.6004 | 1082358.4992 | 2723391.7032 | 1082358.9535
46 | 2723339.1698 | 1082309.08 | 2723351.4709 | 1082313.091
47 | 2723352.7674 | 1082313.5137 | 2723351.4709 | 1082313.091
48 | 2723352.7674 | 1082313.5137 | 2723353.0801 | 1082313.6157 | 2723364.3699 | 1082321.0894
49 | 2723331.6958 | 1082318.3445 | 2723334.9445 | 1082319.8642 | 2723340.3072 | 1082323.4865 | 2723341.8243 | 1082324.8849 | 2723342.8387 | 1082326.5622 | 2723343.6233 | 1082328.6705
50 | 2723365.9541 | 1082322.138 | 2723364.3699 | 1082321.0894
51 | 2723348.9448 | 1082344.8934 | 2723347.848 | 1082343.031 | 2723346.6377 | 1082340.6715 | 2723343.8477 | 1082329.2734 | 2723343.6233 | 1082328.6705
52 | 2723353.6415 | 1082352.2216 | 2723350.5056 | 1082347.5437 | 2723348.9448 | 1082344.8934
53 | 2723378.2281 | 1082339.8946 | 2723377.2804 | 1082339.2019 | 2723372.3368 | 1082341.907
54 | 2723360.2687 | 1082348.5534 | 2723367.0324 | 1082344.8096 | 2723372.3368 | 1082341.907
55 | 2723353.6415 | 1082352.2216 | 2723360.2687 | 1082348.5534
56 | 2723355.2943 | 1082354.9682 | 2723353.6415 | 1082352.2216
57 | 2723355.2943 | 1082354.9682 | 2723357.0271 | 1082358.2102
58 | 2723355.2943 | 1082354.9682 | 2723350.1657 | 1082353.2075 | 2723341.6175 | 1082349.7139
59 | 2723357.0271 | 1082358.2102 | 2723358.4967 | 1082360.9596 | 2723359.8983 | 1082364.2237 | 2723361.1712 | 1082367.906
60 | 2723341.6175 | 1082349.7139 | 2723339.7471 | 1082348.9494
61 | 2723362.3339 | 1082371.2697 | 2723361.1712 | 1082367.906
62 | 2723339.7471 | 1082348.9494 | 2723337.3418 | 1082347.9664 | 2723331.5498 | 1082347.5155 | 2723326.8938 | 1082346.2696
63 | 2723365.5245 | 1082379.1725 | 2723366.7019 | 1082381.5654
64 | 2723376.0413 | 1082401.5619 | 2723373.8074 | 1082396.0061 | 2723366.7019 | 1082381.5654
65 | 2723376.0413 | 1082401.5619 | 2723377.4329 | 1082405.0228
66 | 2723337.6335 | 1082373.8707 | 2723332.4951 | 1082369.8619 | 2723332.2591 | 1082369.7294
67 | 2723293.9214 | 1082355.147 | 2723292.9725 | 1082355.4072 | 2723290.1607 | 1082356.7141
68 | 2723293.9214 | 1082355.147 | 2723298.0329 | 1082354.0197 | 2723301.7643 | 1082353.8284 | 2723304.9273 | 1082355.2682
69 | 2723305.3518 | 1082355.4614 | 2723304.9273 | 1082355.2682
70 | 2723305.3518 | 1082355.4614 | 2723313.2682 | 1082359.065 | 2723317.4129 | 1082361.3925
71 | 2723331.0348 | 1082369.0419 | 2723317.4129 | 1082361.3925
72 | 2723331.0348 | 1082369.0419 | 2723332.2591 | 1082369.7294
73 | 2723314.9255 | 1082343.3386 | 2723319.7708 | 1082344.3637 | 2723326.8938 | 1082346.2696
74 | 2723310.8782 | 1082342.4824 | 2723314.9255 | 1082343.3386

## bus_geodata
| x | y | coords
0 | 2722956.7022 | 1082308.2672
1 | 2723071.4829 | 1082342.7124
2 | 2722760.1655 | 1082265.8295
3 | 2723215.8962 | 1082370.0311
4 | 2722676.3685 | 1082245.1603
5 | 2723216.9597 | 1082370.0184
6 | 2723254.2518 | 1082371.1575
7 | 2723131.6896 | 1082794.9645
8 | 2723187.932 | 1082676.6817
9 | 2723362.9734 | 1082413.3178
10 | 2723356.4847 | 1082389.7397
11 | 2723352.6664 | 1082386.1709
12 | 2723360.1926 | 1082392.2469
13 | 2723277.7932 | 1082362.4625
14 | 2723339.5761 | 1082375.3862
15 | 2723364.678 | 1082377.4522
16 | 2723517.0364 | 1082693.0643
17 | 2723390.7217 | 1082701.7925
18 | 2723385.9629 | 1082474.4645
19 | 2723385.8267 | 1082468.9244
20 | 2723383.1934 | 1082426.6847
21 | 2723381.5423 | 1082417.0779
22 | 2723398.9508 | 1082282.6887
23 | 2723393.9876 | 1082313.7662
24 | 2723461.3867 | 1082241.0103
25 | 2723401.5771 | 1082394.6902
26 | 2723391.9633 | 1082360.0758
27 | 2723285.9596 | 1082358.6668
28 | 2723129.6263 | 1082023.168
29 | 2723212.6072 | 1082331.4643
30 | 2723189.1588 | 1082013.9604
31 | 2723336.2323 | 1082255.8995
32 | 2723316.137 | 1082271.0927
33 | 2723376.4794 | 1082295.5652
34 | 2723390.4459 | 1082317.6195
35 | 2723243.9323 | 1082335.2757
36 | 2723278.0884 | 1082329.4471
37 | 2723288.4396 | 1082324.9935
38 | 2723388.5205 | 1082319.7152
39 | 2723388.8782 | 1082339.4147
40 | 2723381.8183 | 1082342.5184
41 | 2723391.6004 | 1082358.4992
42 | 2723339.1698 | 1082309.08
43 | 2723351.4709 | 1082313.091
44 | 2723352.7674 | 1082313.5137
45 | 2723331.6958 | 1082318.3445
46 | 2723364.3699 | 1082321.0894
47 | 2723343.6233 | 1082328.6705
48 | 2723365.9541 | 1082322.138
49 | 2723348.9448 | 1082344.8934
50 | 2723378.2281 | 1082339.8946
51 | 2723391.7032 | 1082358.9535
52 | 2723372.3368 | 1082341.907
53 | 2723353.6415 | 1082352.2216
54 | 2723360.2687 | 1082348.5534
55 | 2723355.2943 | 1082354.9682
56 | 2723357.0271 | 1082358.2102
57 | 2723341.6175 | 1082349.7139
58 | 2723361.1712 | 1082367.906
59 | 2723339.7471 | 1082348.9494
60 | 2723362.3339 | 1082371.2697
61 | 2723365.5245 | 1082379.1725
62 | 2723366.7019 | 1082381.5654
63 | 2723376.0413 | 1082401.5619
64 | 2723377.4329 | 1082405.0228
65 | 2723337.6335 | 1082373.8707
66 | 2723290.1607 | 1082356.7141
67 | 2723293.9214 | 1082355.147
68 | 2723304.9273 | 1082355.2682
69 | 2723305.3518 | 1082355.4614
70 | 2723317.4129 | 1082361.3925
71 | 2723331.0348 | 1082369.0419
72 | 2723332.2591 | 1082369.7294
73 | 2723314.9255 | 1082343.3386
74 | 2723326.8938 | 1082346.2696
75 | 2723310.8782 | 1082342.4824
76 | 2723355.2943 | 1082354.9682

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1