## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5263-1_0_2_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5263-1_0_2_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5263-1_0_2_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5263-1_0_2_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5263-1_0_2_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5263-1_0_2_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_5263-1_0_2_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_5263-1_0_2_node_5 | 0.4 | n |  | TRUE
8 | bus_LV_5263-1_0_2_node_6 | 0.4 | n |  | TRUE
9 | bus_LV_5263-1_0_2_node_7 | 0.4 | n |  | TRUE
10 | bus_LV_5263-1_0_2_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_5263-1_0_2_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_5263-1_0_2_node_40 | 0.4 | n |  | TRUE
13 | bus_LV_5263-1_0_2_node_38 | 0.4 | n |  | TRUE
14 | bus_LV_5263-1_0_2_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_5263-1_0_2_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_5263-1_0_2_node_13 | 0.4 | n |  | TRUE
17 | bus_LV_5263-1_0_2_node_14 | 0.4 | n |  | TRUE
18 | bus_LV_5263-1_0_2_node_32 | 0.4 | n |  | TRUE
19 | bus_LV_5263-1_0_2_node_51 | 0.4 | n |  | TRUE
20 | bus_LV_5263-1_0_2_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_5263-1_0_2_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_5263-1_0_2_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_5263-1_0_2_node_28 | 0.4 | n |  | TRUE
24 | bus_LV_5263-1_0_2_node_19 | 0.4 | n |  | TRUE
25 | bus_LV_5263-1_0_2_node_20 | 0.4 | n |  | TRUE
26 | bus_LV_5263-1_0_2_node_21 | 0.4 | n |  | TRUE
27 | bus_LV_5263-1_0_2_node_22 | 0.4 | n |  | TRUE
28 | bus_LV_5263-1_0_2_node_23 | 0.4 | n |  | TRUE
29 | bus_LV_5263-1_0_2_node_52 | 0.4 | n |  | TRUE
30 | bus_LV_5263-1_0_2_node_24 | 0.4 | n |  | TRUE
31 | bus_LV_5263-1_0_2_node_25 | 0.4 | n |  | TRUE
32 | bus_LV_5263-1_0_2_node_26 | 0.4 | n |  | TRUE
33 | bus_LV_5263-1_0_2_node_27 | 0.4 | n |  | TRUE
34 | bus_LV_5263-1_0_2_node_29 | 0.4 | n |  | TRUE
35 | bus_LV_5263-1_0_2_node_37 | 0.4 | n |  | TRUE
36 | bus_LV_5263-1_0_2_node_33 | 0.4 | n |  | TRUE
37 | bus_LV_5263-1_0_2_node_30 | 0.4 | n |  | TRUE
38 | bus_LV_5263-1_0_2_node_31 | 0.4 | n |  | TRUE
39 | bus_LV_5263-1_0_2_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_5263-1_0_2_node_34 | 0.4 | n |  | TRUE
41 | bus_LV_5263-1_0_2_node_35 | 0.4 | n |  | TRUE
42 | bus_LV_5263-1_0_2_node_44 | 0.4 | n |  | TRUE
43 | bus_LV_5263-1_0_2_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_5263-1_0_2_node_39 | 0.4 | n |  | TRUE
45 | bus_LV_5263-1_0_2_node_41 | 0.4 | n |  | TRUE
46 | bus_LV_5263-1_0_2_node_42 | 0.4 | n |  | TRUE
47 | bus_LV_5263-1_0_2_node_46 | 0.4 | n |  | TRUE
48 | bus_LV_5263-1_0_2_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_5263-1_0_2_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_5263-1_0_2_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_5263-1_0_2_node_137 | 0.4 | n |  | TRUE
52 | bus_LV_5263-1_0_2_node_48 | 0.4 | n |  | TRUE
53 | bus_LV_5263-1_0_2_node_49 | 0.4 | n |  | TRUE
54 | bus_LV_5263-1_0_2_node_131 | 0.4 | n |  | TRUE
55 | bus_LV_5263-1_0_2_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_5263-1_0_2_node_101 | 0.4 | n |  | TRUE
57 | bus_LV_5263-1_0_2_node_54 | 0.4 | n |  | TRUE
58 | bus_LV_5263-1_0_2_node_98 | 0.4 | n |  | TRUE
59 | bus_LV_5263-1_0_2_node_55 | 0.4 | n |  | TRUE
60 | bus_LV_5263-1_0_2_node_56 | 0.4 | n |  | TRUE
61 | bus_LV_5263-1_0_2_node_57 | 0.4 | n |  | TRUE
62 | bus_LV_5263-1_0_2_node_61 | 0.4 | n |  | TRUE
63 | bus_LV_5263-1_0_2_node_58 | 0.4 | n |  | TRUE
64 | bus_LV_5263-1_0_2_node_60 | 0.4 | n |  | TRUE
65 | bus_LV_5263-1_0_2_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_5263-1_0_2_node_97 | 0.4 | n |  | TRUE
67 | bus_LV_5263-1_0_2_node_63 | 0.4 | n |  | TRUE
68 | bus_LV_5263-1_0_2_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_5263-1_0_2_node_95 | 0.4 | n |  | TRUE
70 | bus_LV_5263-1_0_2_node_96 | 0.4 | n |  | TRUE
71 | bus_LV_5263-1_0_2_node_99 | 0.4 | n |  | TRUE
72 | bus_LV_5263-1_0_2_node_100 | 0.4 | n |  | TRUE
73 | bus_LV_5263-1_0_2_node_132 | 0.4 | n |  | TRUE
74 | bus_LV_5263-1_0_2_node_133 | 0.4 | n |  | TRUE
75 | bus_LV_5263-1_0_2_node_134 | 0.4 | n |  | TRUE
76 | bus_LV_5263-1_0_2_node_135 | 0.4 | n |  | TRUE
77 | bus_LV_5263-1_0_2_node_136 | 0.4 | n |  | TRUE
78 | bus_MV_76_1_node_120 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5263-1_0_2_load_0 | 0 | 0.00093363 | 0.00023399 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5263-1_0_2_load_1 | 1 | 0.0070224 | 0.00176 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5263-1_0_2_load_2 | 2 | 0.00066905 | 0.00016768 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5263-1_0_2_load_4 | 4 | 0.0011558 | 0.00028968 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5263-1_0_2_load_11 | 6 | 0.0038033 | 0.00095318 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5263-1_0_2_load_5 | 7 | 0.0014558 | 0.00036485 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5263-1_0_2_load_6 | 8 | 0.00056487 | 0.00014157 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5263-1_0_2_load_7 | 9 | 0.00134 | 0.00033583 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5263-1_0_2_load_8 | 10 | 0.0011871 | 0.00029751 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5263-1_0_2_load_9 | 11 | 0.002252 | 0.0005644 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5263-1_0_2_load_38 | 13 | 0.0034695 | 0.00086954 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5263-1_0_2_load_12 | 15 | 0.0092713 | 0.0023236 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5263-1_0_2_load_13 | 16 | 0.0083749 | 0.0020989 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5263-1_0_2_load_14 | 17 | 0.0093648 | 0.002347 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5263-1_0_2_load_51 | 19 | 0.0037928 | 0.00095056 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5263-1_0_2_load_16 | 20 | 0.0037885 | 0.00094949 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5263-1_0_2_load_17 | 21 | 0.0070175 | 0.0017588 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5263-1_0_2_load_28 | 23 | 0.0080553 | 0.0020189 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5263-1_0_2_load_19 | 24 | 0.0052818 | 0.0013237 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5263-1_0_2_load_21 | 26 | 0.0065332 | 0.0016374 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5263-1_0_2_load_22 | 27 | 0.0044909 | 0.0011255 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5263-1_0_2_load_23 | 28 | 0.0032999 | 0.00082703 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5263-1_0_2_load_52 | 29 | 0.0057246 | 0.0014347 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5263-1_0_2_load_24 | 30 | 0.0035369 | 0.00088644 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5263-1_0_2_load_25 | 31 | 0.0046832 | 0.0011737 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5263-1_0_2_load_26 | 32 | 0.017193 | 0.004309 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5263-1_0_2_load_27 | 33 | 0.0010481 | 0.00026267 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5263-1_0_2_load_37 | 35 | 0.00096314 | 0.00024139 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5263-1_0_2_load_33 | 36 | 0.0058447 | 0.0014648 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5263-1_0_2_load_30 | 37 | 0.0075053 | 0.001881 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5263-1_0_2_load_31 | 38 | 0.0025748 | 0.0006453 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5263-1_0_2_load_36 | 39 | 0.001996 | 0.00050023 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5263-1_0_2_load_44 | 42 | 0.0055904 | 0.0014011 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5263-1_0_2_load_43 | 43 | 0.0022662 | 0.00056796 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5263-1_0_2_load_39 | 44 | 0.0021707 | 0.00054404 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5263-1_0_2_load_41 | 45 | 0.0007336 | 0.00018386 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5263-1_0_2_load_42 | 46 | 0.00026677 | 6.686e-05 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5263-1_0_2_load_46 | 47 | 0.0043157 | 0.0010816 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5263-1_0_2_load_50 | 48 | 0.00039336 | 9.8586e-05 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5263-1_0_2_load_45 | 49 | 0.00179 | 0.00044862 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5263-1_0_2_load_47 | 50 | 0.0010275 | 0.00025751 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5263-1_0_2_load_137 | 51 | 0.00082809 | 0.00020754 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5263-1_0_2_load_48 | 52 | 0.0033762 | 0.00084616 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5263-1_0_2_load_53 | 55 | 0.004659 | 0.0011677 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5263-1_0_2_load_101 | 56 | 0.0038074 | 0.00095423 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5263-1_0_2_load_54 | 57 | 0.0027054 | 0.00067805 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5263-1_0_2_load_98 | 58 | 0.0027049 | 0.00067791 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5263-1_0_2_load_55 | 59 | 0.0026805 | 0.00067179 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5263-1_0_2_load_56 | 60 | 0.0047007 | 0.0011781 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5263-1_0_2_load_61 | 62 | 0.010751 | 0.0026946 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5263-1_0_2_load_58 | 63 | 0.0072153 | 0.0018083 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5263-1_0_2_load_60 | 64 | 0.0022488 | 0.00056361 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5263-1_0_2_load_62 | 65 | 0.0050183 | 0.0012577 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5263-1_0_2_load_97 | 66 | 0.0027054 | 0.00067805 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5263-1_0_2_load_63 | 67 | 0.0034564 | 0.00086626 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5263-1_0_2_load_65 | 68 | 0.0014368 | 0.0003601 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5263-1_0_2_load_95 | 69 | 0.004837 | 0.0012123 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5263-1_0_2_load_100 | 72 | 0.0030638 | 0.00076786 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5263-1_0_2_load_132 | 73 | 0.0016143 | 0.00040457 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5263-1_0_2_load_133 | 74 | 0.0010879 | 0.00027265 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5263-1_0_2_load_134 | 75 | 0.00038841 | 9.7345e-05 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5263-1_0_2_load_135 | 76 | 0.00077268 | 0.00019365 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5263-1_0_2_load_136 | 77 | 0.00063008 | 0.00015791 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 44 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5263-1_0_2_line_0 |  | 0 | 1 | 0.0012686 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5263-1_0_2_line_1 |  | 0 | 2 | 0.02369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5263-1_0_2_line_2 |  | 1 | 3 | 0.046796 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5263-1_0_2_line_3 |  | 2 | 4 | 0.038408 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5263-1_0_2_line_4 |  | 3 | 5 | 0.008312 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5263-1_0_2_line_5 |  | 4 | 6 | 0.0073675 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5263-1_0_2_line_6 |  | 5 | 14 | 0.021123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5263-1_0_2_line_7 |  | 6 | 15 | 0.0032623 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5263-1_0_2_line_8 |  | 7 | 8 | 0.005933 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5263-1_0_2_line_9 |  | 7 | 9 | 0.0007671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5263-1_0_2_line_10 |  | 8 | 10 | 0.042063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5263-1_0_2_line_11 |  | 9 | 11 | 0.0060593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5263-1_0_2_line_12 |  | 10 | 12 | 0.021653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5263-1_0_2_line_13 |  | 11 | 13 | 0.020554 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5263-1_0_2_line_14 |  | 12 | 45 | 0.013764 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5263-1_0_2_line_15 |  | 12 | 46 | 0.043267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5263-1_0_2_line_16 |  | 13 | 18 | 0.024198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5263-1_0_2_line_17 |  | 14 | 19 | 0.014348 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5263-1_0_2_line_18 |  | 15 | 16 | 0.021703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5263-1_0_2_line_19 |  | 17 | 18 | 0.02676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5263-1_0_2_line_20 |  | 18 | 39 | 0.026008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5263-1_0_2_line_21 |  | 18 | 38 | 0.029943 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5263-1_0_2_line_22 |  | 19 | 53 | 0.021433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5263-1_0_2_line_23 |  | 20 | 21 | 0.026975 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5263-1_0_2_line_24 |  | 20 | 22 | 0.019592 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5263-1_0_2_line_25 |  | 21 | 23 | 0.042883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5263-1_0_2_line_26 |  | 22 | 24 | 0.015613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5263-1_0_2_line_27 |  | 23 | 32 | 0.0088902 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5263-1_0_2_line_28 |  | 24 | 25 | 0.016883 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5263-1_0_2_line_29 |  | 25 | 26 | 0.034033 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5263-1_0_2_line_30 |  | 25 | 27 | 0.0039736 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5263-1_0_2_line_31 |  | 26 | 28 | 0.0012977 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5263-1_0_2_line_32 |  | 27 | 29 | 0.014068 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5263-1_0_2_line_33 |  | 28 | 30 | 0.016874 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5263-1_0_2_line_34 |  | 29 | 55 | 0.0085107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5263-1_0_2_line_35 |  | 29 | 56 | 0.047905 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5263-1_0_2_line_36 |  | 31 | 32 | 0.0051283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5263-1_0_2_line_37 |  | 31 | 33 | 0.01274 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5263-1_0_2_line_38 |  | 33 | 34 | 0.014288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5263-1_0_2_line_39 |  | 34 | 35 | 0.024237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
40 | LV_5263-1_0_2_line_40 |  | 34 | 36 | 0.018376 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
41 | LV_5263-1_0_2_line_41 |  | 35 | 44 | 0.020375 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
42 | LV_5263-1_0_2_line_42 |  | 36 | 40 | 0.027029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
43 | LV_5263-1_0_2_line_43 |  | 37 | 38 | 0.03446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5263-1_0_2_line_44 |  | 39 | 40 | 0.015196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
45 | LV_5263-1_0_2_line_45 |  | 40 | 41 | 0.031398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5263-1_0_2_line_46 |  | 41 | 42 | 0.050707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5263-1_0_2_line_47 |  | 41 | 43 | 0.027711 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5263-1_0_2_line_48 |  | 42 | 49 | 0.024516 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5263-1_0_2_line_49 |  | 45 | 47 | 0.010968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5263-1_0_2_line_50 |  | 46 | 48 | 0.029587 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5263-1_0_2_line_51 |  | 47 | 50 | 0.02617 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5263-1_0_2_line_52 |  | 50 | 51 | 0.044352 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5263-1_0_2_line_53 |  | 51 | 77 | 0.029656 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5263-1_0_2_line_54 |  | 52 | 53 | 0.02286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5263-1_0_2_line_55 |  | 53 | 54 | 0.043559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5263-1_0_2_line_56 |  | 54 | 73 | 0.024968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_5263-1_0_2_line_57 |  | 55 | 57 | 0.015162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_5263-1_0_2_line_58 |  | 56 | 72 | 0.0099997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_5263-1_0_2_line_59 |  | 57 | 58 | 0.0051876 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5263-1_0_2_line_60 |  | 58 | 66 | 0.0094531 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_5263-1_0_2_line_61 |  | 59 | 60 | 0.018734 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5263-1_0_2_line_62 |  | 59 | 61 | 0.015694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_5263-1_0_2_line_63 |  | 59 | 62 | 0.026135 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_5263-1_0_2_line_64 |  | 60 | 63 | 0.034681 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_5263-1_0_2_line_65 |  | 61 | 64 | 0.0218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_5263-1_0_2_line_66 |  | 63 | 65 | 0.02511 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_5263-1_0_2_line_67 |  | 64 | 66 | 0.011184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_5263-1_0_2_line_68 |  | 65 | 67 | 0.003751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_5263-1_0_2_line_69 |  | 67 | 68 | 0.002138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_5263-1_0_2_line_70 |  | 69 | 70 | 0.011071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5263-1_0_2_line_71 |  | 70 | 71 | 0.04414 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5263-1_0_2_line_72 |  | 71 | 72 | 0.047979 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5263-1_0_2_line_73 |  | 73 | 74 | 0.0010638 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5263-1_0_2_line_74 |  | 74 | 75 | 0.018907 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5263-1_0_2_line_75 |  | 75 | 76 | 0.012722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5263-1_0_2_line_76 |  | 76 | 77 | 0.0025712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5263-1_0_2_trafo_39 | 0.63 MVA 20/0.4 kV | 78 | 44 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2719283.7205 | 1084476.9532 | 2719283.7901 | 1084478.2199
1 | 2719283.7205 | 1084476.9532 | 2719283.7125 | 1084476.8081 | 2719283.3197 | 1084460.411 | 2719283.3423 | 1084453.2678
2 | 2719279.0853 | 1084524.3734 | 2719282.4927 | 1084511.7201 | 2719284.7711 | 1084496.0758 | 2719283.7901 | 1084478.2199
3 | 2719283.3423 | 1084453.2678 | 2719283.3542 | 1084449.5373 | 2719284.5786 | 1084441.7225 | 2719287.5538 | 1084436.0767 | 2719304.8054 | 1084431.6003 | 2719307.2402 | 1084430.8022
4 | 2719279.0853 | 1084524.3734 | 2719270.9172 | 1084526.0369
5 | 2719314.2412 | 1084428.5075 | 2719307.2402 | 1084430.8022
6 | 2719270.9172 | 1084526.0369 | 2719255.1639 | 1084529.731 | 2719250.3521 | 1084530.8599
7 | 2719317.3413 | 1084427.4914 | 2719314.2412 | 1084428.5075
8 | 2719236.2945 | 1084357.8235 | 2719237.4906 | 1084363.6347
9 | 2719236.1399 | 1084357.0722 | 2719236.2945 | 1084357.8235
10 | 2719237.4906 | 1084363.6347 | 2719245.9705 | 1084404.8339
11 | 2719236.1399 | 1084357.0722 | 2719234.9183 | 1084351.1373
12 | 2719224.5658 | 1084401.5635 | 2719245.9705 | 1084404.8339
13 | 2719214.4269 | 1084349.5349 | 2719234.9183 | 1084351.1373
14 | 2719224.5658 | 1084401.5635 | 2719210.8015 | 1084401.5477
15 | 2719224.5658 | 1084401.5635 | 2719231.9568 | 1084444.1941
16 | 2719206.2195 | 1084327.9524 | 2719210.9585 | 1084331.7367 | 2719214.4269 | 1084349.5349
17 | 2719250.3521 | 1084530.8599 | 2719236.1794 | 1084533.0924
18 | 2719317.3413 | 1084427.4914 | 2719325.3228 | 1084424.8752 | 2719338.0876 | 1084421.1272
19 | 2719206.2195 | 1084327.9524 | 2719226.5696 | 1084310.5756
20 | 2719206.2195 | 1084327.9524 | 2719180.4802 | 1084331.6804
21 | 2719206.2195 | 1084327.9524 | 2719201.2965 | 1084298.417
22 | 2719215.0076 | 1084536.4275 | 2719236.1794 | 1084533.0924
23 | 2719055.9236 | 1084264.9324 | 2719082.3689 | 1084270.253
24 | 2719036.7162 | 1084261.0681 | 2719055.9236 | 1084264.9324
25 | 2719082.3689 | 1084270.253 | 2719125.1386 | 1084273.372
26 | 2719036.7162 | 1084261.0681 | 2719032.2722 | 1084276.0355
27 | 2719125.1386 | 1084273.372 | 2719126.1854 | 1084282.2003
28 | 2719027.4667 | 1084292.2205 | 2719032.2722 | 1084276.0355
29 | 2719027.4667 | 1084292.2205 | 2719060.689 | 1084299.6043
30 | 2719027.4667 | 1084292.2205 | 2719026.3357 | 1084296.0297
31 | 2719061.9558 | 1084299.8858 | 2719060.689 | 1084299.6043
32 | 2719022.3314 | 1084309.5161 | 2719026.3357 | 1084296.0297
33 | 2719078.4274 | 1084303.5467 | 2719061.9558 | 1084299.8858
34 | 2719022.3314 | 1084309.5161 | 2719019.9089 | 1084317.6747
35 | 2719022.3314 | 1084309.5161 | 2718978.6277 | 1084289.8981
36 | 2719126.7893 | 1084287.293 | 2719126.1854 | 1084282.2003
37 | 2719126.7893 | 1084287.293 | 2719127.9705 | 1084297.2554 | 2719129.7098 | 1084299.3308
38 | 2719141.2908 | 1084306.4446 | 2719134.1759 | 1084304.6598 | 2719129.7098 | 1084299.3308
39 | 2719141.2908 | 1084306.4446 | 2719136.1345 | 1084330.1265
40 | 2719141.2908 | 1084306.4446 | 2719159.6384 | 1084307.4598
41 | 2719136.1345 | 1084330.1265 | 2719131.7998 | 1084350.0347
42 | 2719165.4408 | 1084333.8587 | 2719159.6384 | 1084307.4598
43 | 2719195.6308 | 1084264.4255 | 2719201.2965 | 1084298.417
44 | 2719165.4408 | 1084333.8587 | 2719180.4802 | 1084331.6804
45 | 2719165.4408 | 1084333.8587 | 2719171.7946 | 1084364.6047
46 | 2719171.7946 | 1084364.6047 | 2719176.2332 | 1084386.1068 | 2719148.3419 | 1084379.1271
47 | 2719171.7946 | 1084364.6047 | 2719144.8385 | 1084358.1804
48 | 2719124.5595 | 1084373.1758 | 2719148.3419 | 1084379.1271
49 | 2719199.8334 | 1084401.5351 | 2719210.8015 | 1084401.5477
50 | 2719243.4078 | 1084471.4756 | 2719231.9568 | 1084444.1941
51 | 2719199.8334 | 1084401.5351 | 2719199.8334 | 1084401.5351 | 2719198.8114 | 1084427.6854
52 | 2719195.0868 | 1084471.8809 | 2719198.8114 | 1084427.6854
53 | 2719195.0868 | 1084471.8809 | 2719184.6765 | 1084470.3094 | 2719181.9632 | 1084489.2439
54 | 2719215.0076 | 1084536.4275 | 2719219.5859 | 1084514.0307
55 | 2719173.4192 | 1084548.8669 | 2719178.5993 | 1084547.9565 | 2719207.4779 | 1084537.6032 | 2719215.0076 | 1084536.4275
56 | 2719173.4192 | 1084548.8669 | 2719176.961 | 1084524.1512
57 | 2719015.5934 | 1084332.2093 | 2719019.9089 | 1084317.6747
58 | 2718978.6277 | 1084289.8981 | 2718969.1104 | 1084286.8298
59 | 2719013.7401 | 1084337.0355 | 2719014.81 | 1084334.8478 | 2719015.5934 | 1084332.2093
60 | 2719009.5869 | 1084345.5274 | 2719013.7401 | 1084337.0355
61 | 2719028.388 | 1084383.9293 | 2719010.2721 | 1084379.1563
62 | 2718995.0956 | 1084375.1578 | 2719010.2721 | 1084379.1563
63 | 2719010.2721 | 1084379.1563 | 2719007.9136 | 1084405.1851
64 | 2719061.9246 | 1084392.765 | 2719028.388 | 1084383.9293
65 | 2718995.0956 | 1084375.1578 | 2719004.6734 | 1084355.5742
66 | 2719061.9246 | 1084392.765 | 2719058.989 | 1084417.7029
67 | 2719009.5869 | 1084345.5274 | 2719004.6734 | 1084355.5742
68 | 2719062.6321 | 1084418.5958 | 2719058.989 | 1084417.7029
69 | 2719064.7087 | 1084419.1048 | 2719062.6321 | 1084418.5958
70 | 2718919.8537 | 1084316.0911 | 2718918.7804 | 1084327.11
71 | 2718919.8537 | 1084316.0911 | 2718923.4456 | 1084272.1079
72 | 2718923.4456 | 1084272.1079 | 2718969.1104 | 1084286.8298
73 | 2719176.961 | 1084524.1512 | 2719177.1119 | 1084523.0981
74 | 2719179.7938 | 1084504.3823 | 2719177.1119 | 1084523.0981
75 | 2719179.7938 | 1084504.3823 | 2719181.5984 | 1084491.7891
76 | 2719181.5984 | 1084491.7891 | 2719181.9632 | 1084489.2439

## bus_geodata
| x | y | coords
0 | 2719283.7205 | 1084476.9532
1 | 2719283.7901 | 1084478.2199
2 | 2719283.3423 | 1084453.2678
3 | 2719279.0853 | 1084524.3734
4 | 2719307.2402 | 1084430.8022
5 | 2719270.9172 | 1084526.0369
6 | 2719314.2412 | 1084428.5075
7 | 2719236.2945 | 1084357.8235
8 | 2719237.4906 | 1084363.6347
9 | 2719236.1399 | 1084357.0722
10 | 2719245.9705 | 1084404.8339
11 | 2719234.9183 | 1084351.1373
12 | 2719224.5658 | 1084401.5635
13 | 2719214.4269 | 1084349.5349
14 | 2719250.3521 | 1084530.8599
15 | 2719317.3413 | 1084427.4914
16 | 2719338.0876 | 1084421.1272
17 | 2719226.5696 | 1084310.5756
18 | 2719206.2195 | 1084327.9524
19 | 2719236.1794 | 1084533.0924
20 | 2719055.9236 | 1084264.9324
21 | 2719082.3689 | 1084270.253
22 | 2719036.7162 | 1084261.0681
23 | 2719125.1386 | 1084273.372
24 | 2719032.2722 | 1084276.0355
25 | 2719027.4667 | 1084292.2205
26 | 2719060.689 | 1084299.6043
27 | 2719026.3357 | 1084296.0297
28 | 2719061.9558 | 1084299.8858
29 | 2719022.3314 | 1084309.5161
30 | 2719078.4274 | 1084303.5467
31 | 2719126.7893 | 1084287.293
32 | 2719126.1854 | 1084282.2003
33 | 2719129.7098 | 1084299.3308
34 | 2719141.2908 | 1084306.4446
35 | 2719136.1345 | 1084330.1265
36 | 2719159.6384 | 1084307.4598
37 | 2719195.6308 | 1084264.4255
38 | 2719201.2965 | 1084298.417
39 | 2719180.4802 | 1084331.6804
40 | 2719165.4408 | 1084333.8587
41 | 2719171.7946 | 1084364.6047
42 | 2719148.3419 | 1084379.1271
43 | 2719144.8385 | 1084358.1804
44 | 2719131.7998 | 1084350.0347
45 | 2719210.8015 | 1084401.5477
46 | 2719231.9568 | 1084444.1941
47 | 2719199.8334 | 1084401.5351
48 | 2719243.4078 | 1084471.4756
49 | 2719124.5595 | 1084373.1758
50 | 2719198.8114 | 1084427.6854
51 | 2719195.0868 | 1084471.8809
52 | 2719219.5859 | 1084514.0307
53 | 2719215.0076 | 1084536.4275
54 | 2719173.4192 | 1084548.8669
55 | 2719019.9089 | 1084317.6747
56 | 2718978.6277 | 1084289.8981
57 | 2719015.5934 | 1084332.2094
58 | 2719013.7401 | 1084337.0355
59 | 2719010.2721 | 1084379.1563
60 | 2719028.388 | 1084383.9293
61 | 2718995.0956 | 1084375.1578
62 | 2719007.9136 | 1084405.1851
63 | 2719061.9246 | 1084392.765
64 | 2719004.6734 | 1084355.5742
65 | 2719058.989 | 1084417.7029
66 | 2719009.5869 | 1084345.5274
67 | 2719062.6321 | 1084418.5958
68 | 2719064.7087 | 1084419.1048
69 | 2718918.7804 | 1084327.11
70 | 2718919.8537 | 1084316.0911
71 | 2718923.4456 | 1084272.1079
72 | 2718969.1104 | 1084286.8298
73 | 2719176.961 | 1084524.1512
74 | 2719177.1119 | 1084523.0981
75 | 2719179.7938 | 1084504.3823
76 | 2719181.5984 | 1084491.7891
77 | 2719181.9632 | 1084489.2439
78 | 2719130.7223 | 1084354.9834

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1