## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_587-11_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_587-11_0_4_node_7 | 0.4 | n |  | TRUE
2 | bus_LV_587-11_0_4_node_5 | 0.4 | n |  | TRUE
3 | bus_LV_587-11_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_587-11_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_587-11_0_4_node_6 | 0.4 | n |  | TRUE
6 | bus_LV_587-11_0_4_node_12 | 0.4 | n |  | TRUE
7 | bus_LV_587-11_0_4_node_24 | 0.4 | n |  | TRUE
8 | bus_LV_587-11_0_4_node_10 | 0.4 | n |  | TRUE
9 | bus_LV_587-11_0_4_node_8 | 0.4 | n |  | TRUE
10 | bus_LV_587-11_0_4_node_9 | 0.4 | n |  | TRUE
11 | bus_LV_587-11_0_4_node_11 | 0.4 | n |  | TRUE
12 | bus_LV_587-11_0_4_node_14 | 0.4 | n |  | TRUE
13 | bus_LV_587-11_0_4_node_27 | 0.4 | n |  | TRUE
14 | bus_LV_587-11_0_4_node_15 | 0.4 | n |  | TRUE
15 | bus_LV_587-11_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_587-11_0_4_node_28 | 0.4 | n |  | TRUE
17 | bus_LV_587-11_0_4_node_25 | 0.4 | n |  | TRUE
18 | bus_LV_587-11_0_4_node_72 | 0.4 | n |  | TRUE
19 | bus_LV_587-11_0_4_node_18 | 0.4 | n |  | TRUE
20 | bus_LV_587-11_0_4_node_16 | 0.4 | n |  | TRUE
21 | bus_LV_587-11_0_4_node_17 | 0.4 | n |  | TRUE
22 | bus_LV_587-11_0_4_node_19 | 0.4 | n |  | TRUE
23 | bus_LV_587-11_0_4_node_20 | 0.4 | n |  | TRUE
24 | bus_LV_587-11_0_4_node_21 | 0.4 | n |  | TRUE
25 | bus_LV_587-11_0_4_node_23 | 0.4 | n |  | TRUE
26 | bus_LV_587-11_0_4_node_69 | 0.4 | n |  | TRUE
27 | bus_LV_587-11_0_4_node_29 | 0.4 | n |  | TRUE
28 | bus_LV_587-11_0_4_node_30 | 0.4 | n |  | TRUE
29 | bus_LV_587-11_0_4_node_31 | 0.4 | n |  | TRUE
30 | bus_LV_587-11_0_4_node_91 | 0.4 | n |  | TRUE
31 | bus_LV_587-11_0_4_node_90 | 0.4 | n |  | TRUE
32 | bus_LV_587-11_0_4_node_46 | 0.4 | n |  | TRUE
33 | bus_LV_587-11_0_4_node_47 | 0.4 | n |  | TRUE
34 | bus_LV_587-11_0_4_node_48 | 0.4 | n |  | TRUE
35 | bus_LV_587-11_0_4_node_49 | 0.4 | n |  | TRUE
36 | bus_LV_587-11_0_4_node_50 | 0.4 | n |  | TRUE
37 | bus_LV_587-11_0_4_node_51 | 0.4 | n |  | TRUE
38 | bus_LV_587-11_0_4_node_122 | 0.4 | n |  | TRUE
39 | bus_LV_587-11_0_4_node_87 | 0.4 | n |  | TRUE
40 | bus_LV_587-11_0_4_node_117 | 0.4 | n |  | TRUE
41 | bus_LV_587-11_0_4_node_107 | 0.4 | n |  | TRUE
42 | bus_LV_587-11_0_4_node_52 | 0.4 | n |  | TRUE
43 | bus_LV_587-11_0_4_node_53 | 0.4 | n |  | TRUE
44 | bus_LV_587-11_0_4_node_54 | 0.4 | n |  | TRUE
45 | bus_LV_587-11_0_4_node_55 | 0.4 | n |  | TRUE
46 | bus_LV_587-11_0_4_node_56 | 0.4 | n |  | TRUE
47 | bus_LV_587-11_0_4_node_57 | 0.4 | n |  | TRUE
48 | bus_LV_587-11_0_4_node_121 | 0.4 | n |  | TRUE
49 | bus_LV_587-11_0_4_node_119 | 0.4 | n |  | TRUE
50 | bus_LV_587-11_0_4_node_113 | 0.4 | n |  | TRUE
51 | bus_LV_587-11_0_4_node_61 | 0.4 | n |  | TRUE
52 | bus_LV_587-11_0_4_node_118 | 0.4 | n |  | TRUE
53 | bus_LV_587-11_0_4_node_114 | 0.4 | n |  | TRUE
54 | bus_LV_587-11_0_4_node_59 | 0.4 | n |  | TRUE
55 | bus_LV_587-11_0_4_node_60 | 0.4 | n |  | TRUE
56 | bus_LV_587-11_0_4_node_62 | 0.4 | n |  | TRUE
57 | bus_LV_587-11_0_4_node_68 | 0.4 | n |  | TRUE
58 | bus_LV_587-11_0_4_node_70 | 0.4 | n |  | TRUE
59 | bus_LV_587-11_0_4_node_71 | 0.4 | n |  | TRUE
60 | bus_LV_587-11_0_4_node_104 | 0.4 | n |  | TRUE
61 | bus_LV_587-11_0_4_node_105 | 0.4 | n |  | TRUE
62 | bus_LV_587-11_0_4_node_78 | 0.4 | n |  | TRUE
63 | bus_LV_587-11_0_4_node_79 | 0.4 | n |  | TRUE
64 | bus_LV_587-11_0_4_node_80 | 0.4 | n |  | TRUE
65 | bus_LV_587-11_0_4_node_81 | 0.4 | n |  | TRUE
66 | bus_LV_587-11_0_4_node_82 | 0.4 | n |  | TRUE
67 | bus_LV_587-11_0_4_node_96 | 0.4 | n |  | TRUE
68 | bus_LV_587-11_0_4_node_92 | 0.4 | n |  | TRUE
69 | bus_LV_587-11_0_4_node_89 | 0.4 | n |  | TRUE
70 | bus_LV_587-11_0_4_node_95 | 0.4 | n |  | TRUE
71 | bus_LV_587-11_0_4_node_97 | 0.4 | n |  | TRUE
72 | bus_LV_587-11_0_4_node_98 | 0.4 | n |  | TRUE
73 | bus_LV_587-11_0_4_node_106 | 0.4 | n |  | TRUE
74 | bus_LV_587-11_0_4_node_120 | 0.4 | n |  | TRUE
75 | bus_MV_83_0_node_117 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_587-11_0_4_load_0 | 0 | 0.0035296 | 0.0008846 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_587-11_0_4_load_7 | 1 | 0.0025337 | 0.000635 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_587-11_0_4_load_3 | 3 | 0.0018933 | 0.00047451 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_587-11_0_4_load_4 | 4 | 0.0017106 | 0.00042873 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_587-11_0_4_load_6 | 5 | 0.010802 | 0.0027072 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_587-11_0_4_load_10 | 8 | 0.0048333 | 0.0012113 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_587-11_0_4_load_8 | 9 | 0.0056984 | 0.0014282 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_587-11_0_4_load_9 | 10 | 0.0021223 | 0.00053189 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_587-11_0_4_load_15 | 14 | 0.0014684 | 0.00036802 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_587-11_0_4_load_13 | 15 | 0.0033375 | 0.00083646 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_587-11_0_4_load_25 | 17 | 0.0069569 | 0.0017436 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_587-11_0_4_load_72 | 18 | 0.041991 | 0.010524 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_587-11_0_4_load_18 | 19 | 0.0035288 | 0.00088441 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_587-11_0_4_load_16 | 20 | 0.0032816 | 0.00082245 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_587-11_0_4_load_17 | 21 | 0.0025679 | 0.00064358 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_587-11_0_4_load_20 | 23 | 0.0037136 | 0.00093071 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_587-11_0_4_load_21 | 24 | 0.002529 | 0.00063382 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_587-11_0_4_load_23 | 25 | 0.010526 | 0.002638 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_587-11_0_4_load_29 | 27 | 0.0023581 | 0.000591 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_587-11_0_4_load_30 | 28 | 0.0031482 | 0.000789 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_587-11_0_4_load_31 | 29 | 0.0035965 | 0.00090136 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_587-11_0_4_load_46 | 32 | 0.0036607 | 0.00091746 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_587-11_0_4_load_47 | 33 | 0.0043804 | 0.0010978 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_587-11_0_4_load_49 | 35 | 0.0015583 | 0.00039055 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_587-11_0_4_load_50 | 36 | 0.0068659 | 0.0017207 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_587-11_0_4_load_51 | 37 | 0.0051467 | 0.0012899 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_587-11_0_4_load_122 | 38 | 0.013216 | 0.0033122 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_587-11_0_4_load_87 | 39 | 0.0013767 | 0.00034503 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_587-11_0_4_load_117 | 40 | 0.0019549 | 0.00048995 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_587-11_0_4_load_107 | 41 | 0.002809 | 0.000704 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_587-11_0_4_load_52 | 42 | 0.003228 | 0.00080901 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_587-11_0_4_load_53 | 43 | 0.0029107 | 0.0007295 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_587-11_0_4_load_56 | 46 | 0.0019067 | 0.00047787 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_587-11_0_4_load_57 | 47 | 0.0020956 | 0.00052521 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_587-11_0_4_load_121 | 48 | 0.006751 | 0.001692 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_587-11_0_4_load_119 | 49 | 0.0032972 | 0.00082636 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_587-11_0_4_load_113 | 50 | 0.0036773 | 0.00092163 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_587-11_0_4_load_61 | 51 | 0.0016411 | 0.00041131 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_587-11_0_4_load_118 | 52 | 0.0029813 | 0.00074718 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_587-11_0_4_load_114 | 53 | 0.0026895 | 0.00067405 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_587-11_0_4_load_59 | 54 | 0.0016347 | 0.0004097 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_587-11_0_4_load_60 | 55 | 0.001642 | 0.00041152 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_587-11_0_4_load_62 | 56 | 0.010245 | 0.0025675 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_587-11_0_4_load_68 | 57 | 0.042444 | 0.010638 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_587-11_0_4_load_70 | 58 | 0.0056854 | 0.0014249 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_587-11_0_4_load_104 | 60 | 0.0019012 | 0.00047649 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_587-11_0_4_load_105 | 61 | 0.0018988 | 0.00047588 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_587-11_0_4_load_78 | 62 | 0.0013157 | 0.00032976 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_587-11_0_4_load_79 | 63 | 0.0013167 | 0.00032999 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_587-11_0_4_load_80 | 64 | 0.0016919 | 0.00042402 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_587-11_0_4_load_81 | 65 | 0.0016938 | 0.00042451 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_587-11_0_4_load_96 | 67 | 0.001302 | 0.0003263 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_587-11_0_4_load_92 | 68 | 0.0039718 | 0.00099543 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_587-11_0_4_load_89 | 69 | 0.0022266 | 0.00055805 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_587-11_0_4_load_95 | 70 | 0.0012959 | 0.00032477 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_587-11_0_4_load_97 | 71 | 0.0012961 | 0.00032482 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_587-11_0_4_load_98 | 72 | 0.0036058 | 0.0009037 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_587-11_0_4_load_106 | 73 | 0.0056865 | 0.0014252 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_587-11_0_4_load_120 | 74 | 0.004115 | 0.0010313 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 53 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_587-11_0_4_line_0 |  | 0 | 1 | 0.074891 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_587-11_0_4_line_1 |  | 1 | 2 | 0.025035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_587-11_0_4_line_2 |  | 2 | 3 | 0.020158 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_587-11_0_4_line_3 |  | 3 | 4 | 0.0071593 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_587-11_0_4_line_4 |  | 4 | 5 | 0.0032838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_587-11_0_4_line_5 |  | 5 | 6 | 0.019646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_587-11_0_4_line_6 |  | 6 | 7 | 0.032365 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
7 | LV_587-11_0_4_line_7 |  | 6 | 8 | 0.015342 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
8 | LV_587-11_0_4_line_8 |  | 7 | 18 | 0.034095 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_587-11_0_4_line_9 |  | 8 | 9 | 0.014898 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
10 | LV_587-11_0_4_line_10 |  | 9 | 10 | 0.051992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
11 | LV_587-11_0_4_line_11 |  | 10 | 11 | 0.0092965 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
12 | LV_587-11_0_4_line_12 |  | 11 | 12 | 0.009589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_587-11_0_4_line_13 |  | 11 | 13 | 0.037218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
14 | LV_587-11_0_4_line_14 |  | 12 | 14 | 0.027179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_587-11_0_4_line_15 |  | 12 | 15 | 0.024807 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_587-11_0_4_line_16 |  | 13 | 16 | 0.031201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
17 | LV_587-11_0_4_line_17 |  | 13 | 17 | 0.031739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_587-11_0_4_line_18 |  | 14 | 19 | 0.0094117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_587-11_0_4_line_19 |  | 16 | 27 | 0.0068403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
20 | LV_587-11_0_4_line_20 |  | 18 | 26 | 0.012192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_587-11_0_4_line_21 |  | 19 | 20 | 0.0010661 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_587-11_0_4_line_22 |  | 20 | 21 | 0.022319 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_587-11_0_4_line_23 |  | 21 | 22 | 0.0013562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_587-11_0_4_line_24 |  | 22 | 23 | 0.020432 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_587-11_0_4_line_25 |  | 22 | 24 | 0.010219 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_587-11_0_4_line_26 |  | 24 | 25 | 0.0074568 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_587-11_0_4_line_27 |  | 26 | 57 | 0.0098613 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_587-11_0_4_line_28 |  | 27 | 28 | 0.019822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
29 | LV_587-11_0_4_line_29 |  | 28 | 29 | 0.027458 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
30 | LV_587-11_0_4_line_30 |  | 29 | 30 | 0.0012296 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
31 | LV_587-11_0_4_line_31 |  | 30 | 31 | 0.035131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
32 | LV_587-11_0_4_line_32 |  | 31 | 69 | 0.03934 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
33 | LV_587-11_0_4_line_33 |  | 32 | 33 | 0.025103 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_587-11_0_4_line_34 |  | 32 | 34 | 0.022811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_587-11_0_4_line_35 |  | 33 | 35 | 0.0013218 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_587-11_0_4_line_36 |  | 34 | 36 | 0.012155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_587-11_0_4_line_37 |  | 34 | 37 | 0.0081671 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_587-11_0_4_line_38 |  | 35 | 38 | 0.005181 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_587-11_0_4_line_39 |  | 36 | 39 | 0.0023391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_587-11_0_4_line_40 |  | 37 | 40 | 0.01216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_587-11_0_4_line_41 |  | 40 | 41 | 0.022815 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_587-11_0_4_line_42 |  | 41 | 59 | 0.0028527 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_587-11_0_4_line_43 |  | 42 | 43 | 0.019746 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
44 | LV_587-11_0_4_line_44 |  | 42 | 44 | 0.0080997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
45 | LV_587-11_0_4_line_45 |  | 43 | 45 | 0.017987 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
46 | LV_587-11_0_4_line_46 |  | 44 | 46 | 0.014131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
47 | LV_587-11_0_4_line_47 |  | 44 | 47 | 0.027232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_587-11_0_4_line_48 |  | 45 | 48 | 0.019992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_587-11_0_4_line_49 |  | 45 | 49 | 0.015374 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
50 | LV_587-11_0_4_line_50 |  | 46 | 50 | 0.0014637 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
51 | LV_587-11_0_4_line_51 |  | 47 | 51 | 0.006747 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_587-11_0_4_line_52 |  | 49 | 52 | 0.0062783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
53 | LV_587-11_0_4_line_53 |  | 50 | 53 | 0.017286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
54 | LV_587-11_0_4_line_54 |  | 51 | 54 | 0.0052358 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_587-11_0_4_line_55 |  | 52 | 72 | 0.022464 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
56 | LV_587-11_0_4_line_56 |  | 53 | 74 | 0.04183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_587-11_0_4_line_57 |  | 54 | 55 | 0.0052395 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_587-11_0_4_line_58 |  | 55 | 56 | 0.0053162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_587-11_0_4_line_59 |  | 58 | 59 | 0.01912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_587-11_0_4_line_60 |  | 59 | 60 | 0.025059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_587-11_0_4_line_61 |  | 60 | 61 | 0.0077076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_587-11_0_4_line_62 |  | 61 | 73 | 0.011751 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_587-11_0_4_line_63 |  | 62 | 63 | 0.00018992 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
64 | LV_587-11_0_4_line_64 |  | 62 | 64 | 1.9623e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
65 | LV_587-11_0_4_line_65 |  | 63 | 65 | 0.025328 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
66 | LV_587-11_0_4_line_66 |  | 64 | 66 | 0.0095694 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
67 | LV_587-11_0_4_line_67 |  | 65 | 67 | 0.0001926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
68 | LV_587-11_0_4_line_68 |  | 66 | 68 | 0.033609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_587-11_0_4_line_69 |  | 66 | 69 | 0.033996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
70 | LV_587-11_0_4_line_70 |  | 67 | 70 | 0.00036302 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
71 | LV_587-11_0_4_line_71 |  | 70 | 71 | 0.00013615 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
72 | LV_587-11_0_4_line_72 |  | 71 | 72 | 0.0020178 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 3 | cs | TRUE
73 | LV_587-11_0_4_line_73 |  | 73 | 74 | 0.0080406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_587-11_0_4_trafo_114 | 0.63 MVA 20/0.4 kV | 75 | 53 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3
0 | 2632579.0249 | 1169763.4109 | 2632513.9048 | 1169800.3973
1 | 2632579.0249 | 1169763.4109 | 2632603.2991 | 1169757.0169
2 | 2632603.2991 | 1169757.0169 | 2632599.4693 | 1169742.2552 | 2632598.7253 | 1169737.404
3 | 2632598.7253 | 1169737.404 | 2632597.64 | 1169730.3275
4 | 2632597.3503 | 1169727.061 | 2632597.437 | 1169729.004 | 2632597.64 | 1169730.3275
5 | 2632598.9688 | 1169707.5568 | 2632597.9492 | 1169713.5655 | 2632597.0822 | 1169721.0536 | 2632597.3503 | 1169727.061
6 | 2632598.9688 | 1169707.5568 | 2632594.6497 | 1169705.4212 | 2632589.0099 | 1169702.7115 | 2632572.3485 | 1169689.3588
7 | 2632598.9688 | 1169707.5568 | 2632601.7216 | 1169699.412 | 2632604.7179 | 1169693.3699
8 | 2632572.3485 | 1169689.3588 | 2632549.8072 | 1169663.778
9 | 2632611.6123 | 1169680.1648 | 2632609.7795 | 1169683.7254 | 2632605.8836 | 1169691.0191 | 2632604.7179 | 1169693.3699
10 | 2632611.6123 | 1169680.1648 | 2632614.2647 | 1169675.0119 | 2632633.0804 | 1169632.821
11 | 2632636.8669 | 1169624.3306 | 2632633.0804 | 1169632.821
12 | 2632636.8669 | 1169624.3306 | 2632646.0096 | 1169627.304
13 | 2632652.3996 | 1169590.4975 | 2632636.8669 | 1169624.3306
14 | 2632646.0096 | 1169627.304 | 2632649.9808 | 1169649.8371 | 2632650.3699 | 1169654.118
15 | 2632646.0096 | 1169627.304 | 2632647.8305 | 1169625.9354 | 2632669.7238 | 1169631.2485
16 | 2632652.3996 | 1169590.4975 | 2632665.1413 | 1169562.0076
17 | 2632652.3996 | 1169590.4975 | 2632658.4043 | 1169592.2532 | 2632665.0048 | 1169594.179 | 2632682.8395 | 1169599.4832
18 | 2632651.2217 | 1169663.4911 | 2632650.3699 | 1169654.118
19 | 2632665.1413 | 1169562.0076 | 2632667.8808 | 1169555.7399
20 | 2632541.7469 | 1169654.6309 | 2632549.8072 | 1169663.778
21 | 2632651.2217 | 1169663.4911 | 2632651.3182 | 1169664.5528
22 | 2632651.3182 | 1169664.5528 | 2632653.3382 | 1169686.7806
23 | 2632653.4609 | 1169688.1313 | 2632653.3382 | 1169686.7806
24 | 2632653.4609 | 1169688.1313 | 2632654.8551 | 1169696.2764 | 2632656.0241 | 1169708.389
25 | 2632653.4609 | 1169688.1313 | 2632663.5327 | 1169689.857
26 | 2632670.8824 | 1169691.1163 | 2632663.5327 | 1169689.857
27 | 2632541.7469 | 1169654.6309 | 2632535.6246 | 1169646.9003
28 | 2632667.8808 | 1169555.7399 | 2632675.8192 | 1169537.5774
29 | 2632686.816 | 1169512.4175 | 2632675.8192 | 1169537.5774
30 | 2632687.3084 | 1169511.2908 | 2632686.816 | 1169512.4175
31 | 2632701.3867 | 1169479.0952 | 2632687.3084 | 1169511.2908
32 | 2632701.3867 | 1169479.0952 | 2632662.6473 | 1169472.2475
33 | 2632525.6982 | 1169524.0117 | 2632550.7887 | 1169523.2192
34 | 2632502.8984 | 1169524.7318 | 2632525.6982 | 1169524.0117
35 | 2632552.1099 | 1169523.1775 | 2632550.7887 | 1169523.2192
36 | 2632502.8984 | 1169524.7318 | 2632497.4351 | 1169513.8736
37 | 2632502.8984 | 1169524.7318 | 2632504.734 | 1169532.69
38 | 2632557.2883 | 1169523.0139 | 2632552.1099 | 1169523.1775
39 | 2632497.4351 | 1169513.8736 | 2632496.3837 | 1169511.784
40 | 2632504.734 | 1169532.69 | 2632507.4669 | 1169544.539
41 | 2632509.3402 | 1169567.1372 | 2632509.373 | 1169552.8034 | 2632507.4669 | 1169544.539
42 | 2632509.3336 | 1169569.9899 | 2632509.3402 | 1169567.1372
43 | 2632623.9327 | 1169585.7689 | 2632623.6344 | 1169566.0249
44 | 2632624.0551 | 1169593.8677 | 2632623.9327 | 1169585.7689
45 | 2632623.3626 | 1169548.0403 | 2632623.6344 | 1169566.0249
46 | 2632624.0551 | 1169593.8677 | 2632610.0278 | 1169592.162
47 | 2632624.0551 | 1169593.8677 | 2632624.0935 | 1169596.6582 | 2632622.572 | 1169607.7334 | 2632618.6097 | 1169620.3894
48 | 2632623.3626 | 1169548.0403 | 2632603.3694 | 1169546.5312
49 | 2632623.3626 | 1169548.0403 | 2632624.749 | 1169532.7289
50 | 2632610.0278 | 1169592.162 | 2632608.5748 | 1169591.9854
51 | 2632618.6097 | 1169620.3894 | 2632618.4373 | 1169620.94 | 2632616.262 | 1169626.7139
52 | 2632625.3152 | 1169526.4761 | 2632624.749 | 1169532.7289
53 | 2632592.0875 | 1169593.7165 | 2632598.0262 | 1169590.7027 | 2632608.5748 | 1169591.9854
54 | 2632614.4161 | 1169631.6135 | 2632616.262 | 1169626.7139
55 | 2632625.3152 | 1169526.4761 | 2632627.237 | 1169505.2505 | 2632627.2942 | 1169504.1001
56 | 2632592.0875 | 1169593.7165 | 2632561.5441 | 1169565.1364
57 | 2632614.4161 | 1169631.6135 | 2632612.5689 | 1169636.5166
58 | 2632612.5689 | 1169636.5166 | 2632610.6946 | 1169641.4915
59 | 2632509.3336 | 1169569.9899 | 2632508.3108 | 1169589.0823
60 | 2632509.3336 | 1169569.9899 | 2632530.8169 | 1169566.2152 | 2632534.0615 | 1169566.1013
61 | 2632541.7644 | 1169565.8308 | 2632534.0615 | 1169566.1013
62 | 2632541.7644 | 1169565.8308 | 2632553.5084 | 1169565.4185
63 | 2632628.6848 | 1169476.0968 | 2632628.6943 | 1169475.9071
64 | 2632628.6943 | 1169475.9071 | 2632628.6952 | 1169475.8875
65 | 2632628.6848 | 1169476.0968 | 2632627.4286 | 1169501.3938
66 | 2632629.1699 | 1169466.3298 | 2632628.6952 | 1169475.8875
67 | 2632627.419 | 1169501.5862 | 2632627.4286 | 1169501.3938
68 | 2632629.1699 | 1169466.3298 | 2632628.7068 | 1169454.3767 | 2632630.0613 | 1169432.7726
69 | 2632629.1699 | 1169466.3298 | 2632662.6473 | 1169472.2475
70 | 2632627.401 | 1169501.9488 | 2632627.419 | 1169501.5862
71 | 2632627.3942 | 1169502.0848 | 2632627.401 | 1169501.9488
72 | 2632627.3942 | 1169502.0848 | 2632627.2942 | 1169504.1001
73 | 2632561.5441 | 1169565.1364 | 2632553.5084 | 1169565.4185

## bus_geodata
| x | y | coords
0 | 2632513.9048 | 1169800.3973
1 | 2632579.0249 | 1169763.4109
2 | 2632603.2991 | 1169757.0169
3 | 2632598.7253 | 1169737.404
4 | 2632597.64 | 1169730.3275
5 | 2632597.3503 | 1169727.061
6 | 2632598.9688 | 1169707.5568
7 | 2632572.3485 | 1169689.3588
8 | 2632604.7179 | 1169693.3699
9 | 2632611.6123 | 1169680.1648
10 | 2632633.0804 | 1169632.821
11 | 2632636.8669 | 1169624.3306
12 | 2632646.0096 | 1169627.304
13 | 2632652.3996 | 1169590.4975
14 | 2632650.3699 | 1169654.118
15 | 2632669.7238 | 1169631.2485
16 | 2632665.1413 | 1169562.0076
17 | 2632682.8395 | 1169599.4832
18 | 2632549.8072 | 1169663.778
19 | 2632651.2217 | 1169663.4911
20 | 2632651.3182 | 1169664.5528
21 | 2632653.3382 | 1169686.7806
22 | 2632653.4609 | 1169688.1313
23 | 2632656.0241 | 1169708.389
24 | 2632663.5327 | 1169689.857
25 | 2632670.8824 | 1169691.1163
26 | 2632541.7469 | 1169654.6309
27 | 2632667.8808 | 1169555.7399
28 | 2632675.8192 | 1169537.5774
29 | 2632686.816 | 1169512.4175
30 | 2632687.3084 | 1169511.2908
31 | 2632701.3867 | 1169479.0952
32 | 2632525.6982 | 1169524.0117
33 | 2632550.7887 | 1169523.2192
34 | 2632502.8984 | 1169524.7318
35 | 2632552.1099 | 1169523.1775
36 | 2632497.4351 | 1169513.8736
37 | 2632504.734 | 1169532.69
38 | 2632557.2883 | 1169523.0139
39 | 2632496.3837 | 1169511.784
40 | 2632507.4669 | 1169544.539
41 | 2632509.3402 | 1169567.1372
42 | 2632623.9327 | 1169585.7689
43 | 2632623.6344 | 1169566.0249
44 | 2632624.0551 | 1169593.8677
45 | 2632623.3626 | 1169548.0403
46 | 2632610.0278 | 1169592.162
47 | 2632618.6097 | 1169620.3894
48 | 2632603.3694 | 1169546.5312
49 | 2632624.749 | 1169532.7289
50 | 2632608.5748 | 1169591.9854
51 | 2632616.262 | 1169626.7139
52 | 2632625.3152 | 1169526.4761
53 | 2632592.0875 | 1169593.7165
54 | 2632614.4161 | 1169631.6135
55 | 2632612.5689 | 1169636.5166
56 | 2632610.6946 | 1169641.4915
57 | 2632535.6246 | 1169646.9003
58 | 2632508.3108 | 1169589.0823
59 | 2632509.3337 | 1169569.9899
60 | 2632534.0615 | 1169566.1013
61 | 2632541.7644 | 1169565.8308
62 | 2632628.6943 | 1169475.9071
63 | 2632628.6849 | 1169476.0968
64 | 2632628.6952 | 1169475.8875
65 | 2632627.4286 | 1169501.3938
66 | 2632629.1699 | 1169466.3298
67 | 2632627.419 | 1169501.5862
68 | 2632630.0613 | 1169432.7726
69 | 2632662.6473 | 1169472.2475
70 | 2632627.401 | 1169501.9488
71 | 2632627.3942 | 1169502.0848
72 | 2632627.2942 | 1169504.1001
73 | 2632553.5084 | 1169565.4185
74 | 2632561.5441 | 1169565.1364
75 | 2632624.0551 | 1169593.8677

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1