## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5886-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_5886-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_5886-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_5886-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_5886-1_0_4_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_5886-1_0_4_node_45 | 0.4 | n |  | TRUE
6 | bus_LV_5886-1_0_4_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_5886-1_0_4_node_58 | 0.4 | n |  | TRUE
8 | bus_LV_5886-1_0_4_node_55 | 0.4 | n |  | TRUE
9 | bus_LV_5886-1_0_4_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_5886-1_0_4_node_8 | 0.4 | n |  | TRUE
11 | bus_LV_5886-1_0_4_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_5886-1_0_4_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_5886-1_0_4_node_9 | 0.4 | n |  | TRUE
14 | bus_LV_5886-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_5886-1_0_4_node_57 | 0.4 | n |  | TRUE
16 | bus_LV_5886-1_0_4_node_19 | 0.4 | n |  | TRUE
17 | bus_LV_5886-1_0_4_node_12 | 0.4 | n |  | TRUE
18 | bus_LV_5886-1_0_4_node_13 | 0.4 | n |  | TRUE
19 | bus_LV_5886-1_0_4_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_5886-1_0_4_node_15 | 0.4 | n |  | TRUE
21 | bus_LV_5886-1_0_4_node_16 | 0.4 | n |  | TRUE
22 | bus_LV_5886-1_0_4_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_5886-1_0_4_node_24 | 0.4 | n |  | TRUE
24 | bus_LV_5886-1_0_4_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_5886-1_0_4_node_29 | 0.4 | n |  | TRUE
26 | bus_LV_5886-1_0_4_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_5886-1_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_5886-1_0_4_node_22 | 0.4 | n |  | TRUE
29 | bus_LV_5886-1_0_4_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_5886-1_0_4_node_41 | 0.4 | n |  | TRUE
31 | bus_LV_5886-1_0_4_node_26 | 0.4 | n |  | TRUE
32 | bus_LV_5886-1_0_4_node_25 | 0.4 | n |  | TRUE
33 | bus_LV_5886-1_0_4_node_38 | 0.4 | n |  | TRUE
34 | bus_LV_5886-1_0_4_node_30 | 0.4 | n |  | TRUE
35 | bus_LV_5886-1_0_4_node_31 | 0.4 | n |  | TRUE
36 | bus_LV_5886-1_0_4_node_32 | 0.4 | n |  | TRUE
37 | bus_LV_5886-1_0_4_node_33 | 0.4 | n |  | TRUE
38 | bus_LV_5886-1_0_4_node_34 | 0.4 | n |  | TRUE
39 | bus_LV_5886-1_0_4_node_36 | 0.4 | n |  | TRUE
40 | bus_LV_5886-1_0_4_node_49 | 0.4 | n |  | TRUE
41 | bus_LV_5886-1_0_4_node_47 | 0.4 | n |  | TRUE
42 | bus_LV_5886-1_0_4_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_5886-1_0_4_node_43 | 0.4 | n |  | TRUE
44 | bus_LV_5886-1_0_4_node_59 | 0.4 | n |  | TRUE
45 | bus_LV_5886-1_0_4_node_60 | 0.4 | n |  | TRUE
46 | bus_LV_5886-1_0_4_node_48 | 0.4 | n |  | TRUE
47 | bus_LV_5886-1_0_4_node_44 | 0.4 | n |  | TRUE
48 | bus_LV_5886-1_0_4_node_52 | 0.4 | n |  | TRUE
49 | bus_LV_5886-1_0_4_node_37 | 0.4 | n |  | TRUE
50 | bus_LV_5886-1_0_4_node_39 | 0.4 | n |  | TRUE
51 | bus_LV_5886-1_0_4_node_40 | 0.4 | n |  | TRUE
52 | bus_LV_5886-1_0_4_node_54 | 0.4 | n |  | TRUE
53 | bus_LV_5886-1_0_4_node_50 | 0.4 | n |  | TRUE
54 | bus_LV_5886-1_0_4_node_51 | 0.4 | n |  | TRUE
55 | bus_LV_5886-1_0_4_node_53 | 0.4 | n |  | TRUE
56 | bus_LV_5886-1_0_4_node_56 | 0.4 | n |  | TRUE
57 | bus_LV_5886-1_0_4_node_61 | 0.4 | n |  | TRUE
58 | bus_MV_260_0_node_144 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5886-1_0_4_load_0 | 0 | 0.02102 | 0.0052681 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5886-1_0_4_load_3 | 3 | 0.019303 | 0.0048378 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5886-1_0_4_load_45 | 5 | 0.012818 | 0.0032124 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5886-1_0_4_load_58 | 7 | 0.05964 | 0.014947 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5886-1_0_4_load_55 | 8 | 0.0021254 | 0.00053268 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5886-1_0_4_load_21 | 9 | 0.011742 | 0.0029429 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5886-1_0_4_load_6 | 11 | 0.014922 | 0.0037399 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5886-1_0_4_load_7 | 12 | 0.01979 | 0.0049599 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5886-1_0_4_load_9 | 13 | 0.01638 | 0.0041053 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5886-1_0_4_load_10 | 14 | 0.01543 | 0.0038672 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5886-1_0_4_load_57 | 15 | 0.00093642 | 0.00023469 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5886-1_0_4_load_19 | 16 | 0.0014088 | 0.00035309 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5886-1_0_4_load_12 | 17 | 0.0031966 | 0.00080115 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5886-1_0_4_load_13 | 18 | 0.0045076 | 0.0011297 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5886-1_0_4_load_14 | 19 | 0.0017115 | 0.00042894 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5886-1_0_4_load_16 | 21 | 0.0038312 | 0.00096019 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5886-1_0_4_load_29 | 25 | 0.0040405 | 0.0010127 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5886-1_0_4_load_18 | 26 | 0.00025351 | 6.3536e-05 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5886-1_0_4_load_20 | 27 | 0.0018041 | 0.00045215 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5886-1_0_4_load_22 | 28 | 0.006352 | 0.001592 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5886-1_0_4_load_35 | 29 | 0.0035987 | 0.00090191 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5886-1_0_4_load_41 | 30 | 0.0072558 | 0.0018185 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5886-1_0_4_load_25 | 32 | 0.0022572 | 0.00056572 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5886-1_0_4_load_30 | 34 | 0.0018478 | 0.0004631 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5886-1_0_4_load_31 | 35 | 0.00041717 | 0.00010455 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5886-1_0_4_load_32 | 36 | 0.0014872 | 0.00037273 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5886-1_0_4_load_33 | 37 | 0.0015375 | 0.00038534 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5886-1_0_4_load_47 | 41 | 0.00045615 | 0.00011432 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5886-1_0_4_load_42 | 42 | 0.00099133 | 0.00024845 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5886-1_0_4_load_43 | 43 | 0.0021427 | 0.000537 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5886-1_0_4_load_59 | 44 | 0.0015878 | 0.00039793 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5886-1_0_4_load_60 | 45 | 0.0011845 | 0.00029686 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5886-1_0_4_load_48 | 46 | 0.0014305 | 0.00035852 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5886-1_0_4_load_44 | 47 | 0.00044746 | 0.00011214 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5886-1_0_4_load_37 | 49 | 0.0022462 | 0.00056296 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5886-1_0_4_load_39 | 50 | 0.0012613 | 0.00031611 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5886-1_0_4_load_40 | 51 | 0.002053 | 0.00051452 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5886-1_0_4_load_50 | 53 | 0.00091302 | 0.00022882 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5886-1_0_4_load_51 | 54 | 0.00043591 | 0.00010925 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5886-1_0_4_load_53 | 55 | 0.001206 | 0.00030224 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5886-1_0_4_load_56 | 56 | 0.0092532 | 0.0023191 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5886-1_0_4_load_61 | 57 | 0.0028898 | 0.00072425 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 6 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5886-1_0_4_line_0 |  | 0 | 1 | 0.012813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5886-1_0_4_line_1 |  | 0 | 2 | 0.14204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5886-1_0_4_line_2 |  | 1 | 3 | 0.11492 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_5886-1_0_4_line_3 |  | 1 | 4 | 0.12799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5886-1_0_4_line_4 |  | 2 | 5 | 0.076739 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5886-1_0_4_line_5 |  | 3 | 6 | 0.024838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5886-1_0_4_line_6 |  | 4 | 7 | 0.004941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5886-1_0_4_line_7 |  | 6 | 8 | 0.072213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5886-1_0_4_line_8 |  | 6 | 9 | 0.066279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5886-1_0_4_line_9 |  | 6 | 10 | 0.092266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5886-1_0_4_line_10 |  | 8 | 15 | 0.014804 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5886-1_0_4_line_11 |  | 9 | 16 | 0.10919 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5886-1_0_4_line_12 |  | 10 | 14 | 0.037369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5886-1_0_4_line_13 |  | 10 | 11 | 0.0088586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5886-1_0_4_line_14 |  | 11 | 12 | 0.03595 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5886-1_0_4_line_15 |  | 12 | 13 | 0.014478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5886-1_0_4_line_16 |  | 15 | 23 | 0.06909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5886-1_0_4_line_17 |  | 16 | 26 | 0.028059 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5886-1_0_4_line_18 |  | 17 | 18 | 0.16726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5886-1_0_4_line_19 |  | 17 | 19 | 0.018655 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5886-1_0_4_line_20 |  | 18 | 20 | 0.0099107 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5886-1_0_4_line_21 |  | 19 | 21 | 0.030074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5886-1_0_4_line_22 |  | 20 | 22 | 0.05117 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5886-1_0_4_line_23 |  | 20 | 23 | 0.026941 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5886-1_0_4_line_24 |  | 22 | 24 | 0.02241 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5886-1_0_4_line_25 |  | 22 | 25 | 0.050499 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5886-1_0_4_line_26 |  | 24 | 30 | 0.081789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5886-1_0_4_line_27 |  | 24 | 31 | 0.01954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5886-1_0_4_line_28 |  | 26 | 27 | 0.038298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5886-1_0_4_line_29 |  | 27 | 28 | 0.065153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5886-1_0_4_line_30 |  | 28 | 29 | 0.090137 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5886-1_0_4_line_31 |  | 30 | 33 | 0.009213 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5886-1_0_4_line_32 |  | 31 | 32 | 0.038045 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5886-1_0_4_line_33 |  | 33 | 51 | 0.038188 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5886-1_0_4_line_34 |  | 33 | 49 | 0.065633 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5886-1_0_4_line_35 |  | 34 | 35 | 0.019143 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5886-1_0_4_line_36 |  | 34 | 36 | 0.0075336 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5886-1_0_4_line_37 |  | 35 | 37 | 0.0093034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5886-1_0_4_line_38 |  | 36 | 38 | 0.026124 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5886-1_0_4_line_39 |  | 37 | 39 | 0.041789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5886-1_0_4_line_40 |  | 38 | 40 | 0.002048 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5886-1_0_4_line_41 |  | 38 | 41 | 0.011378 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5886-1_0_4_line_42 |  | 39 | 42 | 0.022192 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5886-1_0_4_line_43 |  | 39 | 43 | 0.074769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5886-1_0_4_line_44 |  | 40 | 44 | 0.02605 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5886-1_0_4_line_45 |  | 40 | 45 | 0.059426 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5886-1_0_4_line_46 |  | 41 | 46 | 0.015149 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5886-1_0_4_line_47 |  | 42 | 47 | 0.018797 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5886-1_0_4_line_48 |  | 43 | 48 | 0.059487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5886-1_0_4_line_49 |  | 47 | 51 | 0.0097474 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5886-1_0_4_line_50 |  | 48 | 52 | 0.18956 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5886-1_0_4_line_51 |  | 48 | 53 | 0.0266 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5886-1_0_4_line_52 |  | 49 | 50 | 0.016016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5886-1_0_4_line_53 |  | 52 | 57 | 0.040097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5886-1_0_4_line_54 |  | 53 | 54 | 0.014828 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_5886-1_0_4_line_55 |  | 54 | 55 | 0.043838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_5886-1_0_4_line_56 |  | 55 | 56 | 0.035131 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5886-1_0_4_trafo_11 | 0.63 MVA 20/0.4 kV | 58 | 6 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2557109.7342 | 1144120.4872 | 2557097.4254 | 1144124.0448
1 | 2557003.2088 | 1144055.1362 | 2557011.74 | 1144059.6554 | 2557016.7325 | 1144067.935 | 2557024.3441 | 1144083.5665 | 2557047.477 | 1144131.3369 | 2557049.7803 | 1144133.2214 | 2557053.3393 | 1144134.4633 | 2557058.4265 | 1144134.4937 | 2557064.1453 | 1144133.6635 | 2557097.4254 | 1144124.0448
2 | 2557109.7342 | 1144120.4872 | 2557116.244 | 1144122.8087 | 2557122.9698 | 1144129.5642 | 2557132.5201 | 1144140.1794 | 2557167.0115 | 1144174.2734 | 2557193.9313 | 1144197.7137
3 | 2557109.7342 | 1144120.4872 | 2557123.4442 | 1144112.0407 | 2557130.0485 | 1144110.3817 | 2557125.5729 | 1144098.0517 | 2557120.3758 | 1144085.8492 | 2557136.5179 | 1144097.3401 | 2557140.0939 | 1144100.9609 | 2557138.9146 | 1144081.048 | 2557136.4869 | 1144072.5054 | 2557139.3268 | 1144076.3426 | 2557153.2835 | 1144082.0239 | 2557156.1263 | 1144086.2837
4 | 2557003.2088 | 1144055.1362 | 2556985.4643 | 1143980.477
5 | 2557211.8686 | 1144214.8528 | 2557203.6849 | 1144206.2066 | 2557193.9313 | 1144197.7137
6 | 2557156.1263 | 1144086.2837 | 2557157.6429 | 1144090.9864
7 | 2557211.8686 | 1144214.8528 | 2557234.8263 | 1144211.2656 | 2557253.8401 | 1144214.9546 | 2557272.6057 | 1144221.5802 | 2557281.8989 | 1144224.3843
8 | 2557211.8686 | 1144214.8528 | 2557215.1081 | 1144231.694 | 2557212.8845 | 1144245.3279 | 2557211.9054 | 1144255.6735 | 2557213.6994 | 1144264.821 | 2557222.1626 | 1144277.9269
9 | 2557170.6249 | 1144259.7693 | 2557153.2352 | 1144235.9475 | 2557180.6028 | 1144230.1053 | 2557211.8686 | 1144214.8528
10 | 2557296.6039 | 1144222.7549 | 2557296.6039 | 1144222.7549 | 2557282.0005 | 1144224.415 | 2557281.8989 | 1144224.3843
11 | 2557222.1626 | 1144277.9269 | 2557247.2564 | 1144316.7868 | 2557262.8676 | 1144338.0312 | 2557275.8094 | 1144354.5367 | 2557287.4274 | 1144364.9431
12 | 2557170.6249 | 1144259.7693 | 2557139.9082 | 1144281.0511
13 | 2557170.6249 | 1144259.7693 | 2557175.8471 | 1144266.925
14 | 2557175.8471 | 1144266.925 | 2557181.8999 | 1144275.2192 | 2557184.2622 | 1144281.0831 | 2557184.9357 | 1144287.1703 | 2557183.5023 | 1144293.0613 | 2557178.9003 | 1144298.5636
15 | 2557166.5732 | 1144306.1569 | 2557178.9003 | 1144298.5636 | 2557178.9003 | 1144298.5636
16 | 2557355.3058 | 1144186.3199 | 2557306.1822 | 1144216.8061 | 2557296.6039 | 1144222.7549
17 | 2557309.6248 | 1144382.1013 | 2557288.283 | 1144365.7094 | 2557287.4274 | 1144364.9431
18 | 2557280.396 | 1144026.0285 | 2557285.5392 | 1144037.8166 | 2557325.9916 | 1144074.9041 | 2557343.5541 | 1144113.3659 | 2557361.6408 | 1144148.8336 | 2557371.7619 | 1144163.0108
19 | 2557272.9357 | 1144008.9301 | 2557280.396 | 1144026.0285
20 | 2557377.5203 | 1144171.077 | 2557371.7619 | 1144163.0108
21 | 2557272.9357 | 1144008.9301 | 2557260.9091 | 1143981.3661
22 | 2557418.2044 | 1144140.162 | 2557403.1915 | 1144149.1395 | 2557377.5203 | 1144171.077
23 | 2557355.3058 | 1144186.3199 | 2557364.6887 | 1144179.8835 | 2557377.5203 | 1144171.077
24 | 2557418.2044 | 1144140.162 | 2557432.2329 | 1144131.0692 | 2557437.0059 | 1144127.9672
25 | 2557418.2044 | 1144140.162 | 2557405.014 | 1144128.7161 | 2557398.6526 | 1144109.3513 | 2557389.6869 | 1144100.4245
26 | 2557437.0059 | 1144127.9672 | 2557437.5396 | 1144149.0964 | 2557438.5552 | 1144166.6427 | 2557440.7852 | 1144185.3253 | 2557446.6583 | 1144196.5229 | 2557454.144 | 1144205.4078
27 | 2557452.1018 | 1144115.5096 | 2557437.0059 | 1144127.9672
28 | 2557337.9868 | 1144407.5856 | 2557327.7785 | 1144396.0447 | 2557309.6248 | 1144382.1013
29 | 2557383.1752 | 1144454.4681 | 2557354.6804 | 1144426.4584 | 2557337.9868 | 1144407.5856
30 | 2557383.1752 | 1144454.4681 | 2557419.4683 | 1144490.1433 | 2557430.3196 | 1144502.3283 | 2557445.5739 | 1144519.4472
31 | 2557459.8966 | 1144212.6041 | 2557454.144 | 1144205.4078
32 | 2557452.1018 | 1144115.5096 | 2557439.0864 | 1144096.2029 | 2557431.4117 | 1144083.5945
33 | 2557459.8966 | 1144212.6041 | 2557482.8068 | 1144243.1566
34 | 2557459.8966 | 1144212.6041 | 2557414.2181 | 1144245.6775 | 2557406.2344 | 1144250.3252
35 | 2557454.0235 | 1144320.8734 | 2557463.1716 | 1144317.1122 | 2557471.0267 | 1144312.2249
36 | 2557454.0235 | 1144320.8734 | 2557447.0559 | 1144323.7382
37 | 2557471.0267 | 1144312.2249 | 2557478.7324 | 1144307.4306 | 2557478.9204 | 1144307.3016
38 | 2557422.894 | 1144333.6723 | 2557447.0559 | 1144323.7382
39 | 2557513.373 | 1144283.6515 | 2557478.9204 | 1144307.3016
40 | 2557421.0095 | 1144334.486 | 2557422.894 | 1144333.6723
41 | 2557422.894 | 1144333.6723 | 2557422.3502 | 1144340.4351 | 2557419.0492 | 1144343.6297
42 | 2557513.373 | 1144283.6515 | 2557507.0373 | 1144275.4699 | 2557499.9314 | 1144265.9937
43 | 2557513.373 | 1144283.6515 | 2557520.4841 | 1144292.8394 | 2557527.5968 | 1144313.1218 | 2557533.2587 | 1144333.6256 | 2557546.3277 | 1144349.2716
44 | 2557421.0095 | 1144334.486 | 2557396.8522 | 1144344.4065
45 | 2557421.0095 | 1144334.486 | 2557390.6873 | 1144283.3412
46 | 2557408.1629 | 1144354.1648 | 2557419.0492 | 1144343.6297
47 | 2557488.6545 | 1144250.9551 | 2557499.9314 | 1144265.9937
48 | 2557582.9463 | 1144396.1404 | 2557580.6434 | 1144393.1996 | 2557554.7402 | 1144359.3428 | 2557546.3277 | 1144349.2716
49 | 2557488.6545 | 1144250.9551 | 2557482.8068 | 1144243.1566
50 | 2557566.4818 | 1144504.2452 | 2557595.7113 | 1144481.4385 | 2557612.7868 | 1144488.2662 | 2557645.0368 | 1144461.1585 | 2557640.6111 | 1144447.0158 | 2557617.4561 | 1144426.8685 | 2557598.5928 | 1144412.7942 | 2557588.8934 | 1144403.7357 | 2557582.9463 | 1144396.1404
51 | 2557582.9463 | 1144396.1404 | 2557569.7175 | 1144409.6184 | 2557563.5887 | 1144414.3039
52 | 2557392.393 | 1144258.383 | 2557406.2344 | 1144250.3252
53 | 2557566.4818 | 1144504.2452 | 2557547.896 | 1144517.4831 | 2557530.6287 | 1144519.3837
54 | 2557563.5887 | 1144414.3039 | 2557551.809 | 1144423.3097
55 | 2557510.7228 | 1144438.1392 | 2557539.9274 | 1144429.2497 | 2557550.7408 | 1144424.1263 | 2557551.809 | 1144423.3097
56 | 2557479.5884 | 1144430.6765 | 2557493.1523 | 1144440.7303 | 2557498.4622 | 1144441.8711 | 2557510.7228 | 1144438.1392

## bus_geodata
| x | y | coords
0 | 2557097.4254 | 1144124.0448
1 | 2557109.7342 | 1144120.4872
2 | 2557003.2088 | 1144055.1362
3 | 2557193.9313 | 1144197.7137
4 | 2557156.1263 | 1144086.2837
5 | 2556985.4643 | 1143980.477
6 | 2557211.8686 | 1144214.8528
7 | 2557157.6429 | 1144090.9864
8 | 2557281.8989 | 1144224.3843
9 | 2557222.1626 | 1144277.9269
10 | 2557170.6249 | 1144259.7693
11 | 2557175.8471 | 1144266.925
12 | 2557178.9003 | 1144298.5636
13 | 2557166.5732 | 1144306.1569
14 | 2557139.9082 | 1144281.0511
15 | 2557296.6039 | 1144222.7549
16 | 2557287.4274 | 1144364.9431
17 | 2557280.396 | 1144026.0285
18 | 2557371.7619 | 1144163.0108
19 | 2557272.9357 | 1144008.9301
20 | 2557377.5203 | 1144171.077
21 | 2557260.9091 | 1143981.3661
22 | 2557418.2044 | 1144140.162
23 | 2557355.3058 | 1144186.3199
24 | 2557437.0059 | 1144127.9672
25 | 2557389.6869 | 1144100.4245
26 | 2557309.6248 | 1144382.1013
27 | 2557337.9868 | 1144407.5856
28 | 2557383.1752 | 1144454.4681
29 | 2557445.5739 | 1144519.4472
30 | 2557454.144 | 1144205.4078
31 | 2557452.1018 | 1144115.5096
32 | 2557431.4117 | 1144083.5945
33 | 2557459.8966 | 1144212.6041
34 | 2557454.0235 | 1144320.8734
35 | 2557471.0267 | 1144312.2249
36 | 2557447.0559 | 1144323.7382
37 | 2557478.9204 | 1144307.3016
38 | 2557422.894 | 1144333.6723
39 | 2557513.373 | 1144283.6515
40 | 2557421.0095 | 1144334.486
41 | 2557419.0492 | 1144343.6297
42 | 2557499.9314 | 1144265.9937
43 | 2557546.3277 | 1144349.2716
44 | 2557396.8522 | 1144344.4065
45 | 2557390.6873 | 1144283.3412
46 | 2557408.1629 | 1144354.1648
47 | 2557488.6545 | 1144250.9551
48 | 2557582.9463 | 1144396.1404
49 | 2557406.2344 | 1144250.3252
50 | 2557392.393 | 1144258.383
51 | 2557482.8068 | 1144243.1566
52 | 2557566.4818 | 1144504.2452
53 | 2557563.5887 | 1144414.3039
54 | 2557551.809 | 1144423.3097
55 | 2557510.7228 | 1144438.1392
56 | 2557479.5884 | 1144430.6765
57 | 2557530.6287 | 1144519.3837
58 | 2557153.2352 | 1144235.9475

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1