## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_5892-24_1_3_node_152 | 0.4 | n |  | TRUE
1 | bus_LV_5892-24_1_3_node_164 | 0.4 | n |  | TRUE
2 | bus_LV_5892-24_1_3_node_150 | 0.4 | n |  | TRUE
3 | bus_LV_5892-24_1_3_node_10 | 0.4 | n |  | TRUE
4 | bus_LV_5892-24_1_3_node_11 | 0.4 | n |  | TRUE
5 | bus_LV_5892-24_1_3_node_12 | 0.4 | n |  | TRUE
6 | bus_LV_5892-24_1_3_node_13 | 0.4 | n |  | TRUE
7 | bus_LV_5892-24_1_3_node_14 | 0.4 | n |  | TRUE
8 | bus_LV_5892-24_1_3_node_15 | 0.4 | n |  | TRUE
9 | bus_LV_5892-24_1_3_node_21 | 0.4 | n |  | TRUE
10 | bus_LV_5892-24_1_3_node_20 | 0.4 | n |  | TRUE
11 | bus_LV_5892-24_1_3_node_36 | 0.4 | n |  | TRUE
12 | bus_LV_5892-24_1_3_node_31 | 0.4 | n |  | TRUE
13 | bus_LV_5892-24_1_3_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_5892-24_1_3_node_27 | 0.4 | n |  | TRUE
15 | bus_LV_5892-24_1_3_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_5892-24_1_3_node_17 | 0.4 | n |  | TRUE
17 | bus_LV_5892-24_1_3_node_18 | 0.4 | n |  | TRUE
18 | bus_LV_5892-24_1_3_node_19 | 0.4 | n |  | TRUE
19 | bus_LV_5892-24_1_3_node_25 | 0.4 | n |  | TRUE
20 | bus_LV_5892-24_1_3_node_22 | 0.4 | n |  | TRUE
21 | bus_LV_5892-24_1_3_node_26 | 0.4 | n |  | TRUE
22 | bus_LV_5892-24_1_3_node_23 | 0.4 | n |  | TRUE
23 | bus_LV_5892-24_1_3_node_33 | 0.4 | n |  | TRUE
24 | bus_LV_5892-24_1_3_node_34 | 0.4 | n |  | TRUE
25 | bus_LV_5892-24_1_3_node_35 | 0.4 | n |  | TRUE
26 | bus_LV_5892-24_1_3_node_28 | 0.4 | n |  | TRUE
27 | bus_LV_5892-24_1_3_node_37 | 0.4 | n |  | TRUE
28 | bus_LV_5892-24_1_3_node_29 | 0.4 | n |  | TRUE
29 | bus_LV_5892-24_1_3_node_131 | 0.4 | n |  | TRUE
30 | bus_LV_5892-24_1_3_node_130 | 0.4 | n |  | TRUE
31 | bus_LV_5892-24_1_3_node_138 | 0.4 | n |  | TRUE
32 | bus_LV_5892-24_1_3_node_139 | 0.4 | n |  | TRUE
33 | bus_LV_5892-24_1_3_node_122 | 0.4 | n |  | TRUE
34 | bus_LV_5892-24_1_3_node_128 | 0.4 | n |  | TRUE
35 | bus_LV_5892-24_1_3_node_129 | 0.4 | n |  | TRUE
36 | bus_LV_5892-24_1_3_node_127 | 0.4 | n |  | TRUE
37 | bus_LV_5892-24_1_3_node_72 | 0.4 | n |  | TRUE
38 | bus_LV_5892-24_1_3_node_73 | 0.4 | n |  | TRUE
39 | bus_LV_5892-24_1_3_node_74 | 0.4 | n |  | TRUE
40 | bus_LV_5892-24_1_3_node_75 | 0.4 | n |  | TRUE
41 | bus_LV_5892-24_1_3_node_77 | 0.4 | n |  | TRUE
42 | bus_LV_5892-24_1_3_node_112 | 0.4 | n |  | TRUE
43 | bus_LV_5892-24_1_3_node_78 | 0.4 | n |  | TRUE
44 | bus_LV_5892-24_1_3_node_134 | 0.4 | n |  | TRUE
45 | bus_LV_5892-24_1_3_node_88 | 0.4 | n |  | TRUE
46 | bus_LV_5892-24_1_3_node_89 | 0.4 | n |  | TRUE
47 | bus_LV_5892-24_1_3_node_135 | 0.4 | n |  | TRUE
48 | bus_LV_5892-24_1_3_node_115 | 0.4 | n |  | TRUE
49 | bus_LV_5892-24_1_3_node_79 | 0.4 | n |  | TRUE
50 | bus_LV_5892-24_1_3_node_80 | 0.4 | n |  | TRUE
51 | bus_LV_5892-24_1_3_node_81 | 0.4 | n |  | TRUE
52 | bus_LV_5892-24_1_3_node_118 | 0.4 | n |  | TRUE
53 | bus_LV_5892-24_1_3_node_119 | 0.4 | n |  | TRUE
54 | bus_LV_5892-24_1_3_node_120 | 0.4 | n |  | TRUE
55 | bus_LV_5892-24_1_3_node_121 | 0.4 | n |  | TRUE
56 | bus_LV_5892-24_1_3_node_123 | 0.4 | n |  | TRUE
57 | bus_LV_5892-24_1_3_node_124 | 0.4 | n |  | TRUE
58 | bus_LV_5892-24_1_3_node_137 | 0.4 | n |  | TRUE
59 | bus_LV_5892-24_1_3_node_125 | 0.4 | n |  | TRUE
60 | bus_LV_5892-24_1_3_node_132 | 0.4 | n |  | TRUE
61 | bus_LV_5892-24_1_3_node_133 | 0.4 | n |  | TRUE
62 | bus_LV_5892-24_1_3_node_126 | 0.4 | n |  | TRUE
63 | bus_LV_5892-24_1_3_node_141 | 0.4 | n |  | TRUE
64 | bus_LV_5892-24_1_3_node_142 | 0.4 | n |  | TRUE
65 | bus_LV_5892-24_1_3_node_140 | 0.4 | n |  | TRUE
66 | bus_LV_5892-24_1_3_node_143 | 0.4 | n |  | TRUE
67 | bus_LV_5892-24_1_3_node_144 | 0.4 | n |  | TRUE
68 | bus_LV_5892-24_1_3_node_136 | 0.4 | n |  | TRUE
69 | bus_LV_5892-24_1_3_node_145 | 0.4 | n |  | TRUE
70 | bus_LV_5892-24_1_3_node_146 | 0.4 | n |  | TRUE
71 | bus_LV_5892-24_1_3_node_147 | 0.4 | n |  | TRUE
72 | bus_LV_5892-24_1_3_node_148 | 0.4 | n |  | TRUE
73 | bus_LV_5892-24_1_3_node_149 | 0.4 | n |  | TRUE
74 | bus_LV_5892-24_1_3_node_151 | 0.4 | n |  | TRUE
75 | bus_LV_5892-24_1_3_node_162 | 0.4 | n |  | TRUE
76 | bus_LV_5892-24_1_3_node_161 | 0.4 | n |  | TRUE
77 | bus_LV_5892-24_1_3_node_153 | 0.4 | n |  | TRUE
78 | bus_LV_5892-24_1_3_node_154 | 0.4 | n |  | TRUE
79 | bus_LV_5892-24_1_3_node_155 | 0.4 | n |  | TRUE
80 | bus_LV_5892-24_1_3_node_156 | 0.4 | n |  | TRUE
81 | bus_LV_5892-24_1_3_node_157 | 0.4 | n |  | TRUE
82 | bus_LV_5892-24_1_3_node_158 | 0.4 | n |  | TRUE
83 | bus_LV_5892-24_1_3_node_159 | 0.4 | n |  | TRUE
84 | bus_LV_5892-24_1_3_node_160 | 0.4 | n |  | TRUE
85 | bus_LV_5892-24_1_3_node_163 | 0.4 | n |  | TRUE
86 | bus_MV_260_0_node_97 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_5892-24_1_3_load_152 | 0 | 0.0039457 | 0.00098888 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_5892-24_1_3_load_164 | 1 | 0.0036998 | 0.00092727 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_5892-24_1_3_load_150 | 2 | 0.0039078 | 0.00097939 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_5892-24_1_3_load_10 | 3 | 0.0093135 | 0.0023342 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_5892-24_1_3_load_11 | 4 | 0.0028009 | 0.00070198 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_5892-24_1_3_load_12 | 5 | 0.0030972 | 0.00077622 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_5892-24_1_3_load_14 | 7 | 0.0080063 | 0.0020066 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_5892-24_1_3_load_15 | 8 | 0.0041221 | 0.0010331 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_5892-24_1_3_load_21 | 9 | 0.0076651 | 0.0019211 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_5892-24_1_3_load_36 | 11 | 0.0068829 | 0.001725 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_5892-24_1_3_load_32 | 13 | 0.0030787 | 0.0007716 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_5892-24_1_3_load_16 | 15 | 0.0045571 | 0.0011421 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_5892-24_1_3_load_17 | 16 | 0.0038673 | 0.00096925 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_5892-24_1_3_load_18 | 17 | 0.00059936 | 0.00015021 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_5892-24_1_3_load_25 | 19 | 0.0016436 | 0.00041192 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_5892-24_1_3_load_22 | 20 | 0.0038484 | 0.00096449 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_5892-24_1_3_load_26 | 21 | 0.0027205 | 0.00068182 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_5892-24_1_3_load_23 | 22 | 0.001643 | 0.00041177 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_5892-24_1_3_load_33 | 23 | 0.00426 | 0.0010676 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_5892-24_1_3_load_34 | 24 | 0.0018118 | 0.00045407 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_5892-24_1_3_load_35 | 25 | 0.0085799 | 0.0021503 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_5892-24_1_3_load_28 | 26 | 0.0030669 | 0.00076864 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_5892-24_1_3_load_37 | 27 | 0.0025196 | 0.00063147 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_5892-24_1_3_load_29 | 28 | 0.0036704 | 0.00091988 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_5892-24_1_3_load_131 | 29 | 0.0056007 | 0.0014037 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_5892-24_1_3_load_130 | 30 | 0.004127 | 0.0010343 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_5892-24_1_3_load_138 | 31 | 0.0055155 | 0.0013823 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_5892-24_1_3_load_139 | 32 | 0.0028887 | 0.00072399 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_5892-24_1_3_load_122 | 33 | 0.0046478 | 0.0011648 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_5892-24_1_3_load_128 | 34 | 0.0017133 | 0.0004294 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_5892-24_1_3_load_129 | 35 | 0.0010032 | 0.00025143 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_5892-24_1_3_load_127 | 36 | 0.0021129 | 0.00052954 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_5892-24_1_3_load_72 | 37 | 0.0025486 | 0.00063873 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_5892-24_1_3_load_73 | 38 | 0.001234 | 0.00030927 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_5892-24_1_3_load_75 | 40 | 0.0024319 | 0.0006095 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_5892-24_1_3_load_112 | 42 | 0.0018184 | 0.00045573 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_5892-24_1_3_load_134 | 44 | 0.0042205 | 0.0010578 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_5892-24_1_3_load_88 | 45 | 0.0036428 | 0.00091298 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_5892-24_1_3_load_89 | 46 | 0.003328 | 0.00083408 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_5892-24_1_3_load_135 | 47 | 0.0045923 | 0.0011509 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_5892-24_1_3_load_115 | 48 | 0.0060672 | 0.0015206 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_5892-24_1_3_load_80 | 50 | 0.0048622 | 0.0012186 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_5892-24_1_3_load_81 | 51 | 0.0065026 | 0.0016297 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_5892-24_1_3_load_118 | 52 | 0.0047397 | 0.0011879 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_5892-24_1_3_load_119 | 53 | 0.0036729 | 0.00092052 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_5892-24_1_3_load_120 | 54 | 0.0067401 | 0.0016892 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_5892-24_1_3_load_121 | 55 | 0.0051684 | 0.0012953 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_5892-24_1_3_load_123 | 56 | 0.0027975 | 0.00070112 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_5892-24_1_3_load_124 | 57 | 0.0041763 | 0.0010467 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_5892-24_1_3_load_137 | 58 | 0.0040528 | 0.0010157 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_5892-24_1_3_load_125 | 59 | 0.0022065 | 0.00055301 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_5892-24_1_3_load_132 | 60 | 0.0021188 | 0.00053101 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_5892-24_1_3_load_133 | 61 | 0.0023492 | 0.00058876 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_5892-24_1_3_load_126 | 62 | 0.0021251 | 0.0005326 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_5892-24_1_3_load_141 | 63 | 0.0023422 | 0.00058702 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_5892-24_1_3_load_142 | 64 | 0.005751 | 0.0014413 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_5892-24_1_3_load_143 | 66 | 0.0033993 | 0.00085196 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_5892-24_1_3_load_144 | 67 | 0.0027412 | 0.000687 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_5892-24_1_3_load_136 | 68 | 0.0026199 | 0.00065662 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_5892-24_1_3_load_145 | 69 | 0.0022771 | 0.00057069 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_5892-24_1_3_load_146 | 70 | 0.0028427 | 0.00071245 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_5892-24_1_3_load_147 | 71 | 0.004648 | 0.0011649 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_5892-24_1_3_load_151 | 74 | 0.0019444 | 0.0004873 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_5892-24_1_3_load_162 | 75 | 0.0029874 | 0.00074872 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_5892-24_1_3_load_161 | 76 | 0.004429 | 0.00111 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_5892-24_1_3_load_153 | 77 | 0.0032215 | 0.00080739 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_5892-24_1_3_load_154 | 78 | 0.0032228 | 0.0008077 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_5892-24_1_3_load_155 | 79 | 0.0059054 | 0.00148 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_5892-24_1_3_load_156 | 80 | 0.0059046 | 0.0014798 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_5892-24_1_3_load_157 | 81 | 0.0032228 | 0.0008077 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_5892-24_1_3_load_158 | 82 | 0.0032251 | 0.00080829 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_5892-24_1_3_load_159 | 83 | 0.0044648 | 0.001119 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_5892-24_1_3_load_160 | 84 | 0.003225 | 0.00080827 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_5892-24_1_3_load_163 | 85 | 0.0032251 | 0.00080828 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 52 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_5892-24_1_3_line_0 |  | 0 | 1 | 0.058109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_5892-24_1_3_line_1 |  | 0 | 2 | 0.036578 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_5892-24_1_3_line_2 |  | 1 | 69 | 0.021717 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
3 | LV_5892-24_1_3_line_3 |  | 2 | 72 | 0.036704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_5892-24_1_3_line_4 |  | 3 | 4 | 0.028472 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_5892-24_1_3_line_5 |  | 3 | 5 | 0.028424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_5892-24_1_3_line_6 |  | 4 | 6 | 0.00032982 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_5892-24_1_3_line_7 |  | 5 | 7 | 0.025354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_5892-24_1_3_line_8 |  | 6 | 8 | 0.027653 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_5892-24_1_3_line_9 |  | 7 | 9 | 0.075848 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_5892-24_1_3_line_10 |  | 8 | 10 | 0.031316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_5892-24_1_3_line_11 |  | 9 | 11 | 0.1415 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_5892-24_1_3_line_12 |  | 10 | 12 | 0.036359 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_5892-24_1_3_line_13 |  | 10 | 13 | 0.03034 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_5892-24_1_3_line_14 |  | 10 | 14 | 0.041171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_5892-24_1_3_line_15 |  | 11 | 27 | 0.034667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_5892-24_1_3_line_16 |  | 12 | 23 | 0.019123 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_5892-24_1_3_line_17 |  | 12 | 24 | 0.0080353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_5892-24_1_3_line_18 |  | 13 | 25 | 0.020255 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_5892-24_1_3_line_19 |  | 14 | 26 | 0.015381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_5892-24_1_3_line_20 |  | 14 | 21 | 0.021286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_5892-24_1_3_line_21 |  | 15 | 16 | 0.019346 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_5892-24_1_3_line_22 |  | 16 | 17 | 0.0029867 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_5892-24_1_3_line_23 |  | 17 | 18 | 0.0034251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_5892-24_1_3_line_24 |  | 18 | 19 | 0.012345 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_5892-24_1_3_line_25 |  | 18 | 20 | 0.030454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_5892-24_1_3_line_26 |  | 19 | 21 | 0.039416 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_5892-24_1_3_line_27 |  | 20 | 22 | 0.045742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_5892-24_1_3_line_28 |  | 23 | 29 | 0.010463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_5892-24_1_3_line_29 |  | 24 | 30 | 0.01981 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_5892-24_1_3_line_30 |  | 25 | 31 | 0.069174 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_5892-24_1_3_line_31 |  | 26 | 28 | 0.054069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_5892-24_1_3_line_32 |  | 29 | 32 | 0.006993 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_5892-24_1_3_line_33 |  | 30 | 33 | 0.01973 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_5892-24_1_3_line_34 |  | 31 | 35 | 0.01667 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_5892-24_1_3_line_35 |  | 33 | 50 | 0.019273 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_5892-24_1_3_line_36 |  | 34 | 35 | 0.00030733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_5892-24_1_3_line_37 |  | 34 | 36 | 0.028953 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_5892-24_1_3_line_38 |  | 36 | 62 | 0.02367 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_5892-24_1_3_line_39 |  | 37 | 38 | 0.053344 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_5892-24_1_3_line_40 |  | 37 | 39 | 0.029097 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_5892-24_1_3_line_41 |  | 38 | 40 | 0.0046591 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_5892-24_1_3_line_42 |  | 39 | 41 | 0.037056 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_5892-24_1_3_line_43 |  | 39 | 42 | 0.03784 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_5892-24_1_3_line_44 |  | 40 | 43 | 0.022055 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_5892-24_1_3_line_45 |  | 41 | 44 | 0.070896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_5892-24_1_3_line_46 |  | 43 | 45 | 0.066071 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_5892-24_1_3_line_47 |  | 43 | 46 | 0.023245 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_5892-24_1_3_line_48 |  | 44 | 47 | 0.0060356 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_5892-24_1_3_line_49 |  | 46 | 48 | 0.010039 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_5892-24_1_3_line_50 |  | 47 | 68 | 0.049023 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_5892-24_1_3_line_51 |  | 49 | 50 | 0.041508 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_5892-24_1_3_line_52 |  | 49 | 51 | 0.023759 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_5892-24_1_3_line_53 |  | 51 | 52 | 0.0073017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_5892-24_1_3_line_54 |  | 52 | 53 | 0.041581 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
55 | LV_5892-24_1_3_line_55 |  | 53 | 54 | 0.0061968 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
56 | LV_5892-24_1_3_line_56 |  | 54 | 55 | 0.018463 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
57 | LV_5892-24_1_3_line_57 |  | 55 | 56 | 0.00065799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
58 | LV_5892-24_1_3_line_58 |  | 56 | 57 | 0.055947 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
59 | LV_5892-24_1_3_line_59 |  | 56 | 58 | 0.040786 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_5892-24_1_3_line_60 |  | 57 | 59 | 0.030776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
61 | LV_5892-24_1_3_line_61 |  | 58 | 68 | 0.027528 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_5892-24_1_3_line_62 |  | 59 | 60 | 0.027286 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
63 | LV_5892-24_1_3_line_63 |  | 60 | 61 | 0.0020275 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
64 | LV_5892-24_1_3_line_64 |  | 61 | 65 | 0.053327 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
65 | LV_5892-24_1_3_line_65 |  | 63 | 64 | 0.014417 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
66 | LV_5892-24_1_3_line_66 |  | 63 | 65 | 0.048333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
67 | LV_5892-24_1_3_line_67 |  | 64 | 66 | 0.00085145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
68 | LV_5892-24_1_3_line_68 |  | 66 | 67 | 0.02562 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
69 | LV_5892-24_1_3_line_69 |  | 67 | 69 | 0.017971 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
70 | LV_5892-24_1_3_line_70 |  | 70 | 71 | 0.029794 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_5892-24_1_3_line_71 |  | 70 | 72 | 0.018748 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_5892-24_1_3_line_72 |  | 72 | 73 | 0.010403 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_5892-24_1_3_line_73 |  | 73 | 74 | 0.038303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_5892-24_1_3_line_74 |  | 74 | 75 | 0.022657 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_5892-24_1_3_line_75 |  | 75 | 76 | 0.033429 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_5892-24_1_3_line_76 |  | 76 | 84 | 0.052413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_5892-24_1_3_line_77 |  | 77 | 78 | 0.012253 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_5892-24_1_3_line_78 |  | 77 | 79 | 0.0066951 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_5892-24_1_3_line_79 |  | 78 | 80 | 0.014654 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_5892-24_1_3_line_80 |  | 79 | 81 | 0.014177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_5892-24_1_3_line_81 |  | 80 | 82 | 0.0054413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_5892-24_1_3_line_82 |  | 81 | 83 | 0.012503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_5892-24_1_3_line_83 |  | 82 | 84 | 0.0079546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_5892-24_1_3_line_84 |  | 83 | 85 | 0.0051522 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_5892-24_1_3_trafo_118 | 0.63 MVA 20/0.4 kV | 86 | 52 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15
0 | 2558539.465 | 1146744.2518 | 2558523.6721 | 1146688.3305
1 | 2558513.133 | 1146769.6077 | 2558519.2509 | 1146764.4555 | 2558539.465 | 1146744.2518
2 | 2558523.6721 | 1146688.3305 | 2558504.6546 | 1146695.0874 | 2558503.2439 | 1146695.6922
3 | 2558489.905 | 1146797.108 | 2558492.3837 | 1146790.1095 | 2558500.9768 | 1146779.845 | 2558513.133 | 1146769.6077
4 | 2558163.7931 | 1146818.0248 | 2558160.4991 | 1146822.7259 | 2558150.0257 | 1146837.5174 | 2558147.2263 | 1146841.1775
5 | 2558129.2888 | 1146863.205 | 2558137.5885 | 1146853.779 | 2558147.2263 | 1146841.1775
6 | 2558163.7931 | 1146818.0248 | 2558163.9823 | 1146817.7547
7 | 2558112.4474 | 1146882.1574 | 2558125.632 | 1146867.3581 | 2558129.2888 | 1146863.205
8 | 2558163.9823 | 1146817.7547 | 2558174.143 | 1146803.2544 | 2558180.208 | 1146795.37
9 | 2558112.4474 | 1146882.1574 | 2558151.2816 | 1146947.3093
10 | 2558194.8139 | 1146769.271 | 2558195.3515 | 1146775.8929 | 2558191.2091 | 1146781.0688 | 2558180.208 | 1146795.37
11 | 2558151.2816 | 1146947.3093 | 2558088.6126 | 1147074.1701
12 | 2558194.8139 | 1146769.271 | 2558205.5327 | 1146774.2658 | 2558217.1533 | 1146781.9334 | 2558225.297 | 1146788.847
13 | 2558194.8139 | 1146769.271 | 2558196.1562 | 1146766.8049 | 2558209.5421 | 1146756.5955 | 2558216.9268 | 1146757.0778 | 2558220.2062 | 1146757.4171
14 | 2558194.8139 | 1146769.271 | 2558182.7598 | 1146768.8657 | 2558171.1878 | 1146768.2126 | 2558164.2779 | 1146765.3147 | 2558154.9034 | 1146761.4557
15 | 2558088.6126 | 1147074.1701 | 2558098.9231 | 1147077.3849 | 2558120.5324 | 1147087.5167
16 | 2558225.297 | 1146788.847 | 2558223.8109 | 1146796.0499 | 2558215.2562 | 1146804.1315
17 | 2558225.297 | 1146788.847 | 2558231.4262 | 1146794.043
18 | 2558236.9828 | 1146748.4119 | 2558230.2761 | 1146754.8617 | 2558225.182 | 1146757.932 | 2558220.2062 | 1146757.4171
19 | 2558154.9034 | 1146761.4557 | 2558163.058 | 1146748.4146
20 | 2558154.9034 | 1146761.4557 | 2558140.9674 | 1146777.5456
21 | 2558110.123 | 1146779.2921 | 2558103.1317 | 1146797.3307
22 | 2558102.0524 | 1146800.1156 | 2558103.1317 | 1146797.3307
23 | 2558100.8146 | 1146803.3092 | 2558102.0524 | 1146800.1156
24 | 2558100.8146 | 1146803.3092 | 2558112.4025 | 1146805.1628 | 2558112.9044 | 1146804.8172
25 | 2558100.8146 | 1146803.3092 | 2558091.848 | 1146820.5027 | 2558086.1553 | 1146829.9886
26 | 2558140.9674 | 1146777.5456 | 2558123.9146 | 1146797.2341 | 2558112.9044 | 1146804.8172
27 | 2558086.1553 | 1146829.9886 | 2558080.1707 | 1146839.9607 | 2558063.797 | 1146869.8866
28 | 2558207.6504 | 1146811.3166 | 2558215.2562 | 1146804.1315
29 | 2558242.1337 | 1146810.475 | 2558242.091 | 1146810.3859 | 2558234.3368 | 1146796.5104 | 2558231.4262 | 1146794.043
30 | 2558236.9828 | 1146748.4119 | 2558288.8182 | 1146702.6065
31 | 2558189.5093 | 1146701.3456 | 2558179.2346 | 1146722.5443 | 2558163.058 | 1146748.4146
32 | 2558202.567 | 1146816.1189 | 2558207.6504 | 1146811.3166
33 | 2558242.1337 | 1146810.475 | 2558250.6564 | 1146828.2689
34 | 2558288.8182 | 1146702.6065 | 2558297.5238 | 1146688.3901
35 | 2558264.9141 | 1146841.2372 | 2558250.6564 | 1146828.2689 | 2558250.6564 | 1146828.2689
36 | 2558297.6843 | 1146688.128 | 2558297.5238 | 1146688.3901
37 | 2558297.6843 | 1146688.128 | 2558297.7878 | 1146687.959 | 2558309.8032 | 1146668.3657 | 2558312.9353 | 1146663.519
38 | 2558312.9353 | 1146663.519 | 2558325.7829 | 1146643.6387
39 | 2558351.4507 | 1146955.8183 | 2558328.0374 | 1146961.9005 | 2558303.2372 | 1146977.2264
40 | 2558379.6357 | 1146948.592 | 2558366.6398 | 1146951.8725 | 2558351.4507 | 1146955.8183
41 | 2558299.2739 | 1146979.6757 | 2558303.2372 | 1146977.2264
42 | 2558379.6357 | 1146948.592 | 2558403.1005 | 1146938.669 | 2558401.3563 | 1146935.2349 | 2558399.3691 | 1146927.767
43 | 2558379.6357 | 1146948.592 | 2558404.3616 | 1146977.2359
44 | 2558287.7606 | 1146998.4874 | 2558299.2739 | 1146979.6757 | 2558299.2739 | 1146979.6757
45 | 2558399.3691 | 1146927.767 | 2558398.2224 | 1146921.8831 | 2558389.9132 | 1146862.1545 | 2558389.427 | 1146857.5823
46 | 2558287.7606 | 1146998.4874 | 2558282.1031 | 1147004.4519 | 2558278.1787 | 1147011.1492 | 2558275.5552 | 1147025.9972 | 2558271.0667 | 1147057.6445 | 2558270.6634 | 1147060.6635
47 | 2558287.7606 | 1146998.4874 | 2558297.7898 | 1147015.9601 | 2558299.7369 | 1147018.3706
48 | 2558388.7887 | 1146851.5806 | 2558389.427 | 1146857.5823
49 | 2558299.7369 | 1147018.3706 | 2558306.0449 | 1147026.1799
50 | 2558388.7887 | 1146851.5806 | 2558388.648 | 1146850.2571 | 2558388.951 | 1146831.9012 | 2558389.9065 | 1146813.4852 | 2558390.7149 | 1146802.6223
51 | 2558300.277 | 1146861.8751 | 2558276.6742 | 1146851.9338 | 2558264.9141 | 1146841.2372
52 | 2558300.277 | 1146861.8751 | 2558311.3998 | 1146840.88
53 | 2558314.8181 | 1146834.4279 | 2558311.3998 | 1146840.88
54 | 2558340.5706 | 1146802.2474 | 2558327.2792 | 1146817.0873 | 2558320.9366 | 1146822.8787 | 2558314.8181 | 1146834.4279
55 | 2558340.5706 | 1146802.2474 | 2558344.705 | 1146797.6314
56 | 2558344.705 | 1146797.6314 | 2558348.7499 | 1146793.1152 | 2558354.5818 | 1146782.1724
57 | 2558354.5818 | 1146782.1724 | 2558354.8913 | 1146781.5918
58 | 2558354.8913 | 1146781.5918 | 2558365.9238 | 1146760.8909 | 2558375.9682 | 1146737.276 | 2558378.4582 | 1146730.9184
59 | 2558354.8913 | 1146781.5918 | 2558395.2243 | 1146775.5283
60 | 2558386.7391 | 1146701.5381 | 2558385.4856 | 1146712.9755 | 2558378.4582 | 1146730.9184
61 | 2558390.7149 | 1146802.6223 | 2558391.0379 | 1146798.2807 | 2558392.8268 | 1146784.8614 | 2558395.2243 | 1146775.5283
62 | 2558397.6966 | 1146677.0572 | 2558396.9813 | 1146678.1893 | 2558389.848 | 1146688.5106 | 2558386.8366 | 1146700.6487 | 2558386.7391 | 1146701.5381
63 | 2558397.6966 | 1146677.0572 | 2558398.7796 | 1146675.3432
64 | 2558398.7796 | 1146675.3432 | 2558451.9272 | 1146670.9724
65 | 2558462.3966 | 1146713.2045 | 2558459.9839 | 1146714.2389 | 2558455.3069 | 1146715.4385 | 2558452.8896 | 1146715.7665 | 2558451.0306 | 1146715.7237 | 2558448.5054 | 1146714.8741 | 2558448.5054 | 1146714.8741
66 | 2558451.9272 | 1146670.9724 | 2558451.0084 | 1146682.5069 | 2558443.2555 | 1146700.9921 | 2558442.3074 | 1146704.9563 | 2558442.4855 | 1146708.4902 | 2558443.5793 | 1146711.1618 | 2558445.6519 | 1146713.204 | 2558448.5054 | 1146714.8741
67 | 2558463.1792 | 1146712.869 | 2558462.3966 | 1146713.2045
68 | 2558463.1792 | 1146712.869 | 2558486.7266 | 1146702.7736
69 | 2558486.7266 | 1146702.7736 | 2558503.2439 | 1146695.6922
70 | 2558474.0637 | 1146807.1347 | 2558454.2836 | 1146819.6544 | 2558449.3468 | 1146823.7036
71 | 2558489.905 | 1146797.108 | 2558474.0637 | 1146807.1347
72 | 2558498.6916 | 1146791.5 | 2558489.905 | 1146797.108
73 | 2558498.6916 | 1146791.5 | 2558494.2322 | 1146806.4273 | 2558489.0507 | 1146821.3263 | 2558487.346 | 1146828.0637
74 | 2558487.346 | 1146828.0637 | 2558487.346 | 1146828.0637 | 2558486.1857 | 1146834.664 | 2558484.7701 | 1146843.2226 | 2558484.3845 | 1146850.4933
75 | 2558489.9559 | 1146883.3664 | 2558489.0437 | 1146880.3676 | 2558486.7226 | 1146870.1451 | 2558484.977 | 1146857.6063 | 2558484.3148 | 1146851.8079 | 2558484.3845 | 1146850.4933
76 | 2558520.6777 | 1146901.9925 | 2558520.5113 | 1146902.5841 | 2558518.5365 | 1146906.911 | 2558516.8052 | 1146909.8022 | 2558515.5241 | 1146911.1451 | 2558514.4142 | 1146911.6863 | 2558512.7499 | 1146912.0313 | 2558510.79 | 1146911.8448 | 2558508.6744 | 1146911.348 | 2558506.4022 | 1146910.4299 | 2558504.0958 | 1146908.9895 | 2558500.9613 | 1146905.5427 | 2558497.0137 | 1146900.0227 | 2558493.0099 | 1146891.9128 | 2558490.8356 | 1146886.2583 | 2558489.9559 | 1146883.3664
77 | 2558518.4194 | 1146862.0356 | 2558519.7513 | 1146874.2161
78 | 2558518.4194 | 1146862.0356 | 2558517.6916 | 1146855.3802
79 | 2558519.7513 | 1146874.2161 | 2558521.3443 | 1146888.7831
80 | 2558516.1505 | 1146841.2871 | 2558517.6916 | 1146855.3802
81 | 2558521.9357 | 1146894.1922 | 2558521.9357 | 1146894.1922 | 2558521.3443 | 1146888.7831
82 | 2558516.1505 | 1146841.2871 | 2558515.8938 | 1146838.9389 | 2558516.7371 | 1146833.1524 | 2558518.053 | 1146829.0655
83 | 2558520.6777 | 1146901.9925 | 2558521.7707 | 1146898.1064 | 2558521.9357 | 1146894.1922
84 | 2558519.6322 | 1146824.1612 | 2558518.053 | 1146829.0655

## bus_geodata
| x | y | coords
0 | 2558539.465 | 1146744.2518
1 | 2558523.6721 | 1146688.3305
2 | 2558513.133 | 1146769.6077
3 | 2558147.2263 | 1146841.1775
4 | 2558163.7931 | 1146818.0248
5 | 2558129.2888 | 1146863.205
6 | 2558163.9823 | 1146817.7547
7 | 2558112.4474 | 1146882.1574
8 | 2558180.208 | 1146795.37
9 | 2558151.2816 | 1146947.3093
10 | 2558194.8139 | 1146769.271
11 | 2558088.6126 | 1147074.1701
12 | 2558225.297 | 1146788.847
13 | 2558220.2062 | 1146757.4171
14 | 2558154.9034 | 1146761.4557
15 | 2558110.123 | 1146779.2921
16 | 2558103.1317 | 1146797.3307
17 | 2558102.0524 | 1146800.1156
18 | 2558100.8146 | 1146803.3092
19 | 2558112.9044 | 1146804.8172
20 | 2558086.1553 | 1146829.9886
21 | 2558140.9674 | 1146777.5456
22 | 2558063.797 | 1146869.8866
23 | 2558215.2562 | 1146804.1315
24 | 2558231.4262 | 1146794.043
25 | 2558236.9828 | 1146748.4119
26 | 2558163.058 | 1146748.4146
27 | 2558120.5324 | 1147087.5167
28 | 2558189.5093 | 1146701.3456
29 | 2558207.6504 | 1146811.3166
30 | 2558242.1337 | 1146810.475
31 | 2558288.8182 | 1146702.6065
32 | 2558202.567 | 1146816.1189
33 | 2558250.6564 | 1146828.2689
34 | 2558297.6843 | 1146688.128
35 | 2558297.5238 | 1146688.3901
36 | 2558312.9353 | 1146663.519
37 | 2558351.4507 | 1146955.8183
38 | 2558303.2372 | 1146977.2264
39 | 2558379.6357 | 1146948.592
40 | 2558299.2739 | 1146979.6757
41 | 2558399.3691 | 1146927.767
42 | 2558404.3616 | 1146977.2359
43 | 2558287.7606 | 1146998.4874
44 | 2558389.427 | 1146857.5823
45 | 2558270.6634 | 1147060.6635
46 | 2558299.7369 | 1147018.3706
47 | 2558388.7887 | 1146851.5806
48 | 2558306.0449 | 1147026.1799
49 | 2558300.277 | 1146861.8751
50 | 2558264.9141 | 1146841.2372
51 | 2558311.3998 | 1146840.88
52 | 2558314.8181 | 1146834.4279
53 | 2558340.5706 | 1146802.2474
54 | 2558344.705 | 1146797.6314
55 | 2558354.5818 | 1146782.1724
56 | 2558354.8913 | 1146781.5918
57 | 2558378.4582 | 1146730.9184
58 | 2558395.2243 | 1146775.5283
59 | 2558386.7391 | 1146701.5381
60 | 2558397.6966 | 1146677.0572
61 | 2558398.7796 | 1146675.3432
62 | 2558325.7829 | 1146643.6387
63 | 2558448.5054 | 1146714.8741
64 | 2558462.3966 | 1146713.2045
65 | 2558451.9272 | 1146670.9724
66 | 2558463.1792 | 1146712.869
67 | 2558486.7266 | 1146702.7736
68 | 2558390.7149 | 1146802.6223
69 | 2558503.2439 | 1146695.6922
70 | 2558474.0637 | 1146807.1347
71 | 2558449.3468 | 1146823.7036
72 | 2558489.905 | 1146797.108
73 | 2558498.6916 | 1146791.5
74 | 2558487.346 | 1146828.0637
75 | 2558484.3845 | 1146850.4933
76 | 2558489.9559 | 1146883.3664
77 | 2558518.4194 | 1146862.0356
78 | 2558519.7513 | 1146874.2161
79 | 2558517.6916 | 1146855.3802
80 | 2558521.3443 | 1146888.7831
81 | 2558516.1505 | 1146841.2871
82 | 2558521.9357 | 1146894.1922
83 | 2558518.053 | 1146829.0655
84 | 2558520.6777 | 1146901.9925
85 | 2558519.6322 | 1146824.1612
86 | 2558300.277 | 1146861.8751

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1