## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_593-12_0_3_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_593-12_0_3_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_593-12_0_3_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_593-12_0_3_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_593-12_0_3_node_42 | 0.4 | n |  | TRUE
5 | bus_LV_593-12_0_3_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_593-12_0_3_node_61 | 0.4 | n |  | TRUE
7 | bus_LV_593-12_0_3_node_6 | 0.4 | n |  | TRUE
8 | bus_LV_593-12_0_3_node_7 | 0.4 | n |  | TRUE
9 | bus_LV_593-12_0_3_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_593-12_0_3_node_13 | 0.4 | n |  | TRUE
11 | bus_LV_593-12_0_3_node_9 | 0.4 | n |  | TRUE
12 | bus_LV_593-12_0_3_node_8 | 0.4 | n |  | TRUE
13 | bus_LV_593-12_0_3_node_10 | 0.4 | n |  | TRUE
14 | bus_LV_593-12_0_3_node_11 | 0.4 | n |  | TRUE
15 | bus_LV_593-12_0_3_node_12 | 0.4 | n |  | TRUE
16 | bus_LV_593-12_0_3_node_26 | 0.4 | n |  | TRUE
17 | bus_LV_593-12_0_3_node_24 | 0.4 | n |  | TRUE
18 | bus_LV_593-12_0_3_node_17 | 0.4 | n |  | TRUE
19 | bus_LV_593-12_0_3_node_14 | 0.4 | n |  | TRUE
20 | bus_LV_593-12_0_3_node_29 | 0.4 | n |  | TRUE
21 | bus_LV_593-12_0_3_node_25 | 0.4 | n |  | TRUE
22 | bus_LV_593-12_0_3_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_593-12_0_3_node_15 | 0.4 | n |  | TRUE
24 | bus_LV_593-12_0_3_node_16 | 0.4 | n |  | TRUE
25 | bus_LV_593-12_0_3_node_19 | 0.4 | n |  | TRUE
26 | bus_LV_593-12_0_3_node_18 | 0.4 | n |  | TRUE
27 | bus_LV_593-12_0_3_node_23 | 0.4 | n |  | TRUE
28 | bus_LV_593-12_0_3_node_28 | 0.4 | n |  | TRUE
29 | bus_LV_593-12_0_3_node_38 | 0.4 | n |  | TRUE
30 | bus_LV_593-12_0_3_node_27 | 0.4 | n |  | TRUE
31 | bus_LV_593-12_0_3_node_39 | 0.4 | n |  | TRUE
32 | bus_LV_593-12_0_3_node_30 | 0.4 | n |  | TRUE
33 | bus_LV_593-12_0_3_node_31 | 0.4 | n |  | TRUE
34 | bus_LV_593-12_0_3_node_32 | 0.4 | n |  | TRUE
35 | bus_LV_593-12_0_3_node_33 | 0.4 | n |  | TRUE
36 | bus_LV_593-12_0_3_node_34 | 0.4 | n |  | TRUE
37 | bus_LV_593-12_0_3_node_35 | 0.4 | n |  | TRUE
38 | bus_LV_593-12_0_3_node_36 | 0.4 | n |  | TRUE
39 | bus_LV_593-12_0_3_node_43 | 0.4 | n |  | TRUE
40 | bus_LV_593-12_0_3_node_37 | 0.4 | n |  | TRUE
41 | bus_LV_593-12_0_3_node_44 | 0.4 | n |  | TRUE
42 | bus_LV_593-12_0_3_node_45 | 0.4 | n |  | TRUE
43 | bus_LV_593-12_0_3_node_51 | 0.4 | n |  | TRUE
44 | bus_LV_593-12_0_3_node_41 | 0.4 | n |  | TRUE
45 | bus_LV_593-12_0_3_node_40 | 0.4 | n |  | TRUE
46 | bus_LV_593-12_0_3_node_58 | 0.4 | n |  | TRUE
47 | bus_LV_593-12_0_3_node_59 | 0.4 | n |  | TRUE
48 | bus_LV_593-12_0_3_node_50 | 0.4 | n |  | TRUE
49 | bus_LV_593-12_0_3_node_46 | 0.4 | n |  | TRUE
50 | bus_LV_593-12_0_3_node_47 | 0.4 | n |  | TRUE
51 | bus_LV_593-12_0_3_node_48 | 0.4 | n |  | TRUE
52 | bus_LV_593-12_0_3_node_49 | 0.4 | n |  | TRUE
53 | bus_LV_593-12_0_3_node_55 | 0.4 | n |  | TRUE
54 | bus_LV_593-12_0_3_node_56 | 0.4 | n |  | TRUE
55 | bus_LV_593-12_0_3_node_52 | 0.4 | n |  | TRUE
56 | bus_LV_593-12_0_3_node_53 | 0.4 | n |  | TRUE
57 | bus_LV_593-12_0_3_node_54 | 0.4 | n |  | TRUE
58 | bus_MV_81_0_node_71 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_593-12_0_3_load_0 | 0 | 0.012208 | 0.0030597 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_593-12_0_3_load_1 | 1 | 0.0013164 | 0.00032993 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_593-12_0_3_load_2 | 2 | 0.0014367 | 0.00036007 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_593-12_0_3_load_61 | 6 | 0.014415 | 0.0036127 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_593-12_0_3_load_6 | 7 | 0.058822 | 0.014742 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_593-12_0_3_load_4 | 9 | 0.027672 | 0.0069353 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_593-12_0_3_load_13 | 10 | 0.018477 | 0.0046309 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_593-12_0_3_load_9 | 11 | 0.0014682 | 0.00036797 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_593-12_0_3_load_8 | 12 | 0.0040473 | 0.0010144 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_593-12_0_3_load_26 | 16 | 0.0035616 | 0.00089263 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_593-12_0_3_load_24 | 17 | 0.033841 | 0.0084813 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_593-12_0_3_load_17 | 18 | 0.0042074 | 0.0010545 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_593-12_0_3_load_14 | 19 | 0.0033688 | 0.00084431 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_593-12_0_3_load_29 | 20 | 0.0041777 | 0.001047 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_593-12_0_3_load_22 | 22 | 0.0037053 | 0.00092864 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_593-12_0_3_load_15 | 23 | 0.0023492 | 0.00058876 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_593-12_0_3_load_16 | 24 | 0.0024524 | 0.00061462 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_593-12_0_3_load_18 | 26 | 0.003116 | 0.00078094 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_593-12_0_3_load_23 | 27 | 0.0033903 | 0.0008497 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_593-12_0_3_load_28 | 28 | 0.0016472 | 0.00041282 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_593-12_0_3_load_27 | 30 | 0.046814 | 0.011733 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_593-12_0_3_load_39 | 31 | 0.0038259 | 0.00095886 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_593-12_0_3_load_30 | 32 | 0.0030997 | 0.00077685 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_593-12_0_3_load_31 | 33 | 0.0039935 | 0.0010009 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_593-12_0_3_load_33 | 35 | 0.003236 | 0.00081101 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_593-12_0_3_load_34 | 36 | 0.0060924 | 0.0015269 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_593-12_0_3_load_35 | 37 | 0.0051499 | 0.0012907 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_593-12_0_3_load_36 | 38 | 0.0026778 | 0.00067111 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_593-12_0_3_load_37 | 40 | 0.0029242 | 0.00073287 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_593-12_0_3_load_44 | 41 | 0.0038244 | 0.00095848 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_593-12_0_3_load_45 | 42 | 0.0065514 | 0.0016419 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_593-12_0_3_load_51 | 43 | 0.0031234 | 0.00078281 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_593-12_0_3_load_41 | 44 | 0.0038314 | 0.00096025 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_593-12_0_3_load_59 | 47 | 0.0050812 | 0.0012735 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_593-12_0_3_load_50 | 48 | 0.0016061 | 0.00040252 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_593-12_0_3_load_46 | 49 | 0.0034453 | 0.00086346 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_593-12_0_3_load_47 | 50 | 0.0035431 | 0.00088799 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_593-12_0_3_load_48 | 51 | 0.0014304 | 0.00035849 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_593-12_0_3_load_49 | 52 | 0.0049994 | 0.001253 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_593-12_0_3_load_55 | 53 | 0.001762 | 0.00044161 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_593-12_0_3_load_56 | 54 | 0.0027568 | 0.00069093 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_593-12_0_3_load_52 | 55 | 0.0035448 | 0.00088842 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_593-12_0_3_load_53 | 56 | 0.001445 | 0.00036216 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_593-12_0_3_load_54 | 57 | 0.0063052 | 0.0015802 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 17 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_593-12_0_3_line_0 |  | 0 | 1 | 0.039036 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_593-12_0_3_line_1 |  | 0 | 2 | 0.010731 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_593-12_0_3_line_2 |  | 2 | 3 | 0.020223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_593-12_0_3_line_3 |  | 3 | 4 | 0.066569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_593-12_0_3_line_4 |  | 3 | 5 | 0.061196 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_593-12_0_3_line_5 |  | 4 | 6 | 0.00687 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_593-12_0_3_line_6 |  | 5 | 7 | 0.017774 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_593-12_0_3_line_7 |  | 5 | 8 | 0.043513 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_593-12_0_3_line_8 |  | 5 | 9 | 0.011459 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_593-12_0_3_line_9 |  | 8 | 10 | 0.00819 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_593-12_0_3_line_10 |  | 8 | 11 | 0.023722 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_593-12_0_3_line_11 |  | 11 | 12 | 0.012006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_593-12_0_3_line_12 |  | 12 | 13 | 0.01204 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
13 | LV_593-12_0_3_line_13 |  | 13 | 14 | 0.009525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
14 | LV_593-12_0_3_line_14 |  | 13 | 15 | 0.023087 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
15 | LV_593-12_0_3_line_15 |  | 14 | 16 | 0.014714 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_593-12_0_3_line_16 |  | 14 | 17 | 0.038705 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
17 | LV_593-12_0_3_line_17 |  | 15 | 18 | 0.021179 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
18 | LV_593-12_0_3_line_18 |  | 15 | 19 | 0.01291 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_593-12_0_3_line_19 |  | 16 | 20 | 0.012349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_593-12_0_3_line_20 |  | 17 | 21 | 0.014323 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_593-12_0_3_line_21 |  | 18 | 22 | 0.040339 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
22 | LV_593-12_0_3_line_22 |  | 19 | 23 | 0.012664 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_593-12_0_3_line_23 |  | 21 | 30 | 0.017425 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_593-12_0_3_line_24 |  | 22 | 27 | 3.8048e-05 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_593-12_0_3_line_25 |  | 23 | 24 | 0.01842 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_593-12_0_3_line_26 |  | 24 | 25 | 0.001881 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_593-12_0_3_line_27 |  | 25 | 26 | 0.019368 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_593-12_0_3_line_28 |  | 27 | 28 | 0.015839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_593-12_0_3_line_29 |  | 28 | 29 | 0.030954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_593-12_0_3_line_30 |  | 29 | 31 | 0.0089666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_593-12_0_3_line_31 |  | 31 | 45 | 0.05865 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_593-12_0_3_line_32 |  | 32 | 33 | 0.018371 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_593-12_0_3_line_33 |  | 32 | 34 | 0.0018283 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_593-12_0_3_line_34 |  | 33 | 35 | 0.003465 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_593-12_0_3_line_35 |  | 34 | 36 | 0.026582 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_593-12_0_3_line_36 |  | 34 | 37 | 0.011305 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_593-12_0_3_line_37 |  | 35 | 38 | 0.020969 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_593-12_0_3_line_38 |  | 36 | 39 | 0.0041442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_593-12_0_3_line_39 |  | 38 | 40 | 0.021647 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_593-12_0_3_line_40 |  | 39 | 41 | 0.014027 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_593-12_0_3_line_41 |  | 39 | 42 | 0.024263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_593-12_0_3_line_42 |  | 40 | 43 | 0.012162 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_593-12_0_3_line_43 |  | 41 | 46 | 0.0071231 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_593-12_0_3_line_44 |  | 43 | 44 | 0.0070626 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_593-12_0_3_line_45 |  | 44 | 45 | 0.033089 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_593-12_0_3_line_46 |  | 46 | 47 | 0.023461 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_593-12_0_3_line_47 |  | 46 | 48 | 0.0044922 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_593-12_0_3_line_48 |  | 48 | 51 | 0.012525 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_593-12_0_3_line_49 |  | 49 | 50 | 0.014546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_593-12_0_3_line_50 |  | 49 | 51 | 0.00057676 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_593-12_0_3_line_51 |  | 50 | 52 | 0.0079237 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_593-12_0_3_line_52 |  | 52 | 53 | 0.0017679 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_593-12_0_3_line_53 |  | 53 | 54 | 0.001282 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_593-12_0_3_line_54 |  | 54 | 57 | 0.0083332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_593-12_0_3_line_55 |  | 55 | 56 | 0.016301 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_593-12_0_3_line_56 |  | 56 | 57 | 0.022556 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_593-12_0_3_trafo_24 | 0.63 MVA 20/0.4 kV | 58 | 17 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11
0 | 2630544.6003 | 1170633.7002 | 2630580.8621 | 1170648.1535
1 | 2630590.8302 | 1170652.1266 | 2630580.8621 | 1170648.1535
2 | 2630609.1169 | 1170660.6808 | 2630600.2976 | 1170655.9001 | 2630590.8302 | 1170652.1266
3 | 2630609.1169 | 1170660.6808 | 2630612.5341 | 1170662.6769 | 2630613.2041 | 1170661.8021 | 2630616.5008 | 1170658.9063 | 2630626.3123 | 1170652.1194 | 2630631.2942 | 1170648.8098 | 2630635.5014 | 1170654.901 | 2630651.5657 | 1170659.6297 | 2630650.2255 | 1170664.4142 | 2630647.5213 | 1170674.1388
4 | 2630609.1169 | 1170660.6808 | 2630612.5341 | 1170662.6769 | 2630613.2041 | 1170661.8021 | 2630616.5008 | 1170658.9063 | 2630626.3123 | 1170652.1194 | 2630631.2942 | 1170648.8098 | 2630640.3541 | 1170642.4082 | 2630641.1602 | 1170641.8453 | 2630643.402 | 1170640.3004 | 2630645.4213 | 1170638.8655 | 2630656.2627 | 1170631.1724 | 2630653.1075 | 1170630.3225
5 | 2630654.1521 | 1170676.0069 | 2630647.5213 | 1170674.1388
6 | 2630653.1075 | 1170630.3225 | 2630663.3641 | 1170615.7895
7 | 2630653.1075 | 1170630.3225 | 2630656.2627 | 1170631.1724 | 2630673.0567 | 1170620.3302 | 2630675.9894 | 1170618.3219 | 2630689.601 | 1170608.9754 | 2630689.7546 | 1170608.865
8 | 2630653.1075 | 1170630.3225 | 2630642.0435 | 1170627.3403
9 | 2630689.7546 | 1170608.865 | 2630694.1718 | 1170615.7689
10 | 2630689.7546 | 1170608.865 | 2630692.7029 | 1170606.8012 | 2630708.6667 | 1170594.549
11 | 2630718.271 | 1170587.3524 | 2630716.804 | 1170588.3036 | 2630708.6667 | 1170594.549
12 | 2630728.7427 | 1170581.4833 | 2630724.2034 | 1170583.5056 | 2630718.271 | 1170587.3524
13 | 2630728.7427 | 1170581.4833 | 2630727.1029 | 1170577.5063 | 2630725.401 | 1170575.1964 | 2630723.6957 | 1170573.5646
14 | 2630751.3835 | 1170580.7987 | 2630748.7023 | 1170579.9957 | 2630744.3993 | 1170579.1955 | 2630740.8041 | 1170579.0993 | 2630733.6016 | 1170579.7962 | 2630728.7427 | 1170581.4833
15 | 2630723.6957 | 1170573.5646 | 2630728.3756 | 1170559.6146
16 | 2630723.6957 | 1170573.5646 | 2630719.9005 | 1170570.6993 | 2630713.6022 | 1170568.0991 | 2630687.9367 | 1170559.288
17 | 2630751.3835 | 1170580.7987 | 2630755.354 | 1170574.827 | 2630757.6977 | 1170571.3039 | 2630761.0017 | 1170568.4971 | 2630765.9401 | 1170566.2122
18 | 2630751.3835 | 1170580.7987 | 2630754.4008 | 1170581.7035 | 2630761.9919 | 1170584.2992 | 2630763.6355 | 1170584.8619
19 | 2630732.3034 | 1170547.9065 | 2630728.3756 | 1170559.6146
20 | 2630674.3864 | 1170554.6477 | 2630675.3411 | 1170554.9638 | 2630687.9367 | 1170559.288
21 | 2630803.3563 | 1170551.2628 | 2630795.604 | 1170553.5999 | 2630775.9016 | 1170561.6031 | 2630765.9401 | 1170566.2122
22 | 2630775.6164 | 1170588.9638 | 2630763.6355 | 1170584.8619
23 | 2630674.3864 | 1170554.6477 | 2630667.7038 | 1170552.4013 | 2630657.781 | 1170549.371
24 | 2630803.3563 | 1170551.2628 | 2630803.3927 | 1170551.2519
25 | 2630793.0434 | 1170594.9303 | 2630775.6164 | 1170588.9638
26 | 2630794.823 | 1170595.5396 | 2630793.0434 | 1170594.9303
27 | 2630794.823 | 1170595.5396 | 2630788.6831 | 1170613.9083
28 | 2630818.8333 | 1170547.7618 | 2630815.0008 | 1170548.4966 | 2630805.902 | 1170550.4954 | 2630803.3927 | 1170551.2519
29 | 2630849.0824 | 1170541.2008 | 2630823.302 | 1170546.9049 | 2630818.8333 | 1170547.7618
30 | 2630849.0824 | 1170541.2008 | 2630857.8374 | 1170539.2645
31 | 2630915.1037 | 1170526.599 | 2630857.8374 | 1170539.2645
32 | 2630805.6865 | 1170492.1402 | 2630820.7042 | 1170496.9993 | 2630823.202 | 1170497.6718
33 | 2630803.947 | 1170491.5774 | 2630805.6865 | 1170492.1402
34 | 2630826.5479 | 1170498.5725 | 2630823.202 | 1170497.6718
35 | 2630803.947 | 1170491.5774 | 2630788.9001 | 1170486.7979 | 2630783.6039 | 1170485.7035 | 2630778.2467 | 1170485.1425
36 | 2630803.947 | 1170491.5774 | 2630805.6322 | 1170488.1843 | 2630808.9689 | 1170481.4488
37 | 2630826.5479 | 1170498.5725 | 2630831.1021 | 1170499.7985 | 2630836.8031 | 1170501.0061 | 2630847.124 | 1170502.4798
38 | 2630774.1055 | 1170485.0324 | 2630777.8004 | 1170485.0958 | 2630778.2467 | 1170485.1425
39 | 2630868.5497 | 1170505.5602 | 2630868.2998 | 1170505.5033 | 2630847.124 | 1170502.4798
40 | 2630774.1055 | 1170485.0324 | 2630765.499 | 1170484.9994 | 2630760.1045 | 1170485.5243
41 | 2630763.6043 | 1170506.901 | 2630769.3 | 1170494.2014 | 2630774.1055 | 1170485.0324
42 | 2630880.2923 | 1170508.6446 | 2630877.5001 | 1170507.5961 | 2630868.5497 | 1170505.5602
43 | 2630753.0149 | 1170486.214 | 2630760.1045 | 1170485.5243
44 | 2630880.2923 | 1170508.6446 | 2630886.9041 | 1170511.1276
45 | 2630915.1037 | 1170526.599 | 2630914.5004 | 1170524.9061 | 2630913.2019 | 1170522.9985 | 2630911.4042 | 1170521.4996 | 2630908.2007 | 1170519.6044 | 2630887.8847 | 1170511.4958 | 2630886.9041 | 1170511.1276
46 | 2630753.0149 | 1170486.214 | 2630753.0026 | 1170493.1064 | 2630752.1003 | 1170497.504 | 2630746.9724 | 1170508.4414
47 | 2630753.0149 | 1170486.214 | 2630748.563 | 1170486.8151
48 | 2630748.563 | 1170486.8151 | 2630742.7026 | 1170487.6065 | 2630736.104 | 1170488.022
49 | 2630735.5284 | 1170488.0583 | 2630728.4988 | 1170488.501 | 2630721.0173 | 1170487.9351
50 | 2630736.104 | 1170488.022 | 2630735.5284 | 1170488.0583
51 | 2630721.0173 | 1170487.9351 | 2630713.9992 | 1170487.4042 | 2630713.1283 | 1170487.2436
52 | 2630711.3897 | 1170486.9231 | 2630713.1283 | 1170487.2436
53 | 2630711.3897 | 1170486.9231 | 2630710.129 | 1170486.6906
54 | 2630710.129 | 1170486.6906 | 2630704.2006 | 1170485.5977 | 2630701.9653 | 1170485.0354
55 | 2630664.2083 | 1170475.8725 | 2630666.9975 | 1170476.4031 | 2630680.0682 | 1170479.6256
56 | 2630680.0682 | 1170479.6256 | 2630686.474 | 1170481.2049 | 2630699.7078 | 1170484.4741 | 2630699.96 | 1170484.531 | 2630701.9653 | 1170485.0354

## bus_geodata
| x | y | coords
0 | 2630580.8621 | 1170648.1535
1 | 2630544.6003 | 1170633.7002
2 | 2630590.8302 | 1170652.1266
3 | 2630609.1169 | 1170660.6808
4 | 2630647.5213 | 1170674.1388
5 | 2630653.1075 | 1170630.3225
6 | 2630654.1521 | 1170676.0069
7 | 2630663.3641 | 1170615.7895
8 | 2630689.7546 | 1170608.865
9 | 2630642.0435 | 1170627.3403
10 | 2630694.1718 | 1170615.7689
11 | 2630708.6667 | 1170594.549
12 | 2630718.271 | 1170587.3524
13 | 2630728.7427 | 1170581.4833
14 | 2630723.6957 | 1170573.5646
15 | 2630751.3835 | 1170580.7987
16 | 2630728.3756 | 1170559.6146
17 | 2630687.9367 | 1170559.288
18 | 2630765.9401 | 1170566.2122
19 | 2630763.6355 | 1170584.8619
20 | 2630732.3034 | 1170547.9065
21 | 2630674.3864 | 1170554.6477
22 | 2630803.3563 | 1170551.2628
23 | 2630775.6164 | 1170588.9638
24 | 2630793.0434 | 1170594.9303
25 | 2630794.823 | 1170595.5396
26 | 2630788.6831 | 1170613.9083
27 | 2630803.3927 | 1170551.2519
28 | 2630818.8333 | 1170547.7618
29 | 2630849.0824 | 1170541.2008
30 | 2630657.781 | 1170549.371
31 | 2630857.8374 | 1170539.2645
32 | 2630805.6865 | 1170492.1402
33 | 2630823.202 | 1170497.6718
34 | 2630803.947 | 1170491.5774
35 | 2630826.5479 | 1170498.5725
36 | 2630778.2467 | 1170485.1425
37 | 2630808.9689 | 1170481.4488
38 | 2630847.124 | 1170502.4798
39 | 2630774.1055 | 1170485.0324
40 | 2630868.5497 | 1170505.5602
41 | 2630760.1045 | 1170485.5243
42 | 2630763.6043 | 1170506.901
43 | 2630880.2923 | 1170508.6446
44 | 2630886.9041 | 1170511.1276
45 | 2630915.1037 | 1170526.599
46 | 2630753.0149 | 1170486.214
47 | 2630746.9724 | 1170508.4414
48 | 2630748.563 | 1170486.8151
49 | 2630735.5284 | 1170488.0583
50 | 2630721.0173 | 1170487.9351
51 | 2630736.104 | 1170488.022
52 | 2630713.1283 | 1170487.2436
53 | 2630711.3897 | 1170486.9231
54 | 2630710.129 | 1170486.6906
55 | 2630664.2083 | 1170475.8725
56 | 2630680.0682 | 1170479.6256
57 | 2630701.9653 | 1170485.0354
58 | 2630674.3864 | 1170554.6477

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1