## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_593-6_0_5_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_593-6_0_5_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_593-6_0_5_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_593-6_0_5_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_593-6_0_5_node_4 | 0.4 | n |  | TRUE
5 | bus_LV_593-6_0_5_node_5 | 0.4 | n |  | TRUE
6 | bus_LV_593-6_0_5_node_6 | 0.4 | n |  | TRUE
7 | bus_LV_593-6_0_5_node_7 | 0.4 | n |  | TRUE
8 | bus_LV_593-6_0_5_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_593-6_0_5_node_9 | 0.4 | n |  | TRUE
10 | bus_LV_593-6_0_5_node_39 | 0.4 | n |  | TRUE
11 | bus_LV_593-6_0_5_node_13 | 0.4 | n |  | TRUE
12 | bus_LV_593-6_0_5_node_18 | 0.4 | n |  | TRUE
13 | bus_LV_593-6_0_5_node_32 | 0.4 | n |  | TRUE
14 | bus_LV_593-6_0_5_node_44 | 0.4 | n |  | TRUE
15 | bus_LV_593-6_0_5_node_16 | 0.4 | n |  | TRUE
16 | bus_LV_593-6_0_5_node_11 | 0.4 | n |  | TRUE
17 | bus_LV_593-6_0_5_node_19 | 0.4 | n |  | TRUE
18 | bus_LV_593-6_0_5_node_33 | 0.4 | n |  | TRUE
19 | bus_LV_593-6_0_5_node_10 | 0.4 | n |  | TRUE
20 | bus_LV_593-6_0_5_node_12 | 0.4 | n |  | TRUE
21 | bus_LV_593-6_0_5_node_14 | 0.4 | n |  | TRUE
22 | bus_LV_593-6_0_5_node_17 | 0.4 | n |  | TRUE
23 | bus_LV_593-6_0_5_node_21 | 0.4 | n |  | TRUE
24 | bus_LV_593-6_0_5_node_28 | 0.4 | n |  | TRUE
25 | bus_LV_593-6_0_5_node_30 | 0.4 | n |  | TRUE
26 | bus_LV_593-6_0_5_node_26 | 0.4 | n |  | TRUE
27 | bus_LV_593-6_0_5_node_47 | 0.4 | n |  | TRUE
28 | bus_LV_593-6_0_5_node_48 | 0.4 | n |  | TRUE
29 | bus_LV_593-6_0_5_node_35 | 0.4 | n |  | TRUE
30 | bus_LV_593-6_0_5_node_20 | 0.4 | n |  | TRUE
31 | bus_LV_593-6_0_5_node_22 | 0.4 | n |  | TRUE
32 | bus_LV_593-6_0_5_node_23 | 0.4 | n |  | TRUE
33 | bus_LV_593-6_0_5_node_36 | 0.4 | n |  | TRUE
34 | bus_LV_593-6_0_5_node_24 | 0.4 | n |  | TRUE
35 | bus_LV_593-6_0_5_node_25 | 0.4 | n |  | TRUE
36 | bus_LV_593-6_0_5_node_40 | 0.4 | n |  | TRUE
37 | bus_LV_593-6_0_5_node_41 | 0.4 | n |  | TRUE
38 | bus_LV_593-6_0_5_node_27 | 0.4 | n |  | TRUE
39 | bus_LV_593-6_0_5_node_29 | 0.4 | n |  | TRUE
40 | bus_LV_593-6_0_5_node_31 | 0.4 | n |  | TRUE
41 | bus_LV_593-6_0_5_node_46 | 0.4 | n |  | TRUE
42 | bus_LV_593-6_0_5_node_42 | 0.4 | n |  | TRUE
43 | bus_LV_593-6_0_5_node_45 | 0.4 | n |  | TRUE
44 | bus_LV_593-6_0_5_node_43 | 0.4 | n |  | TRUE
45 | bus_LV_593-6_0_5_node_37 | 0.4 | n |  | TRUE
46 | bus_LV_593-6_0_5_node_38 | 0.4 | n |  | TRUE
47 | bus_LV_593-6_0_5_node_53 | 0.4 | n |  | TRUE
48 | bus_LV_593-6_0_5_node_54 | 0.4 | n |  | TRUE
49 | bus_LV_593-6_0_5_node_52 | 0.4 | n |  | TRUE
50 | bus_LV_593-6_0_5_node_49 | 0.4 | n |  | TRUE
51 | bus_LV_593-6_0_5_node_50 | 0.4 | n |  | TRUE
52 | bus_LV_593-6_0_5_node_51 | 0.4 | n |  | TRUE
53 | bus_MV_81_0_node_158 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_593-6_0_5_load_0 | 0 | 0.021751 | 0.0054514 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_593-6_0_5_load_1 | 1 | 0.016473 | 0.0041285 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_593-6_0_5_load_3 | 3 | 0.022653 | 0.0056774 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_593-6_0_5_load_5 | 5 | 0.018845 | 0.004723 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_593-6_0_5_load_6 | 6 | 0.0078144 | 0.0019585 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_593-6_0_5_load_7 | 7 | 0.0077529 | 0.0019431 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_593-6_0_5_load_8 | 8 | 0.011884 | 0.0029783 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_593-6_0_5_load_9 | 9 | 0.0035131 | 0.00088046 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_593-6_0_5_load_39 | 10 | 0.019842 | 0.0049729 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_593-6_0_5_load_18 | 12 | 0.020317 | 0.0050919 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_593-6_0_5_load_32 | 13 | 0.0025237 | 0.0006325 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_593-6_0_5_load_44 | 14 | 0.0031924 | 0.0008001 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_593-6_0_5_load_16 | 15 | 0.027494 | 0.0068906 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_593-6_0_5_load_11 | 16 | 0.015583 | 0.0039055 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_593-6_0_5_load_19 | 17 | 0.01034 | 0.0025916 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_593-6_0_5_load_33 | 18 | 0.003967 | 0.00099423 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_593-6_0_5_load_10 | 19 | 0.01305 | 0.0032705 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_593-6_0_5_load_17 | 22 | 0.0067026 | 0.0016798 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_593-6_0_5_load_21 | 23 | 0.0033659 | 0.00084356 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_593-6_0_5_load_26 | 26 | 0.0021399 | 0.00053631 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_593-6_0_5_load_47 | 27 | 0.016022 | 0.0040154 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_593-6_0_5_load_48 | 28 | 0.0059941 | 0.0015023 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_593-6_0_5_load_35 | 29 | 0.0029946 | 0.00075052 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_593-6_0_5_load_20 | 30 | 0.016329 | 0.0040924 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_593-6_0_5_load_22 | 31 | 0.02928 | 0.0073382 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_593-6_0_5_load_23 | 32 | 0.010368 | 0.0025984 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_593-6_0_5_load_36 | 33 | 0.0022133 | 0.0005547 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_593-6_0_5_load_24 | 34 | 0.0052413 | 0.0013136 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_593-6_0_5_load_25 | 35 | 0.005568 | 0.0013955 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_593-6_0_5_load_40 | 36 | 0.0067217 | 0.0016846 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_593-6_0_5_load_41 | 37 | 0.0094581 | 0.0023704 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_593-6_0_5_load_27 | 38 | 0.0034294 | 0.0008595 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_593-6_0_5_load_29 | 39 | 0.0015056 | 0.00037734 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_593-6_0_5_load_31 | 40 | 0.0048975 | 0.0012274 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_593-6_0_5_load_46 | 41 | 0.0048901 | 0.0012256 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_593-6_0_5_load_42 | 42 | 0.0049995 | 0.001253 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_593-6_0_5_load_45 | 43 | 0.0039343 | 0.00098602 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_593-6_0_5_load_43 | 44 | 0.013476 | 0.0033775 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_593-6_0_5_load_37 | 45 | 0.011516 | 0.0028863 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_593-6_0_5_load_38 | 46 | 0.011716 | 0.0029363 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_593-6_0_5_load_54 | 48 | 0.0028705 | 0.00071942 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_593-6_0_5_load_52 | 49 | 0.0024498 | 0.00061398 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_593-6_0_5_load_49 | 50 | 0.0091624 | 0.0022963 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_593-6_0_5_load_50 | 51 | 0.0027663 | 0.00069331 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_593-6_0_5_load_51 | 52 | 0.0056126 | 0.0014066 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 4 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_593-6_0_5_line_0 |  | 0 | 1 | 0.00984 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_593-6_0_5_line_1 |  | 0 | 2 | 0.010559 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_593-6_0_5_line_2 |  | 1 | 3 | 0.0019281 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_593-6_0_5_line_3 |  | 2 | 4 | 0.016258 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
4 | LV_593-6_0_5_line_4 |  | 2 | 5 | 0.0094563 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_593-6_0_5_line_5 |  | 3 | 6 | 0.0063017 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_593-6_0_5_line_6 |  | 4 | 7 | 0.015838 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_593-6_0_5_line_7 |  | 4 | 8 | 0.016069 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
8 | LV_593-6_0_5_line_8 |  | 5 | 9 | 0.013308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_593-6_0_5_line_9 |  | 6 | 10 | 0.00061373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_593-6_0_5_line_10 |  | 7 | 11 | 0.005082 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_593-6_0_5_line_11 |  | 8 | 12 | 0.00018799 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_593-6_0_5_line_12 |  | 9 | 13 | 0.0027503 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_593-6_0_5_line_13 |  | 10 | 14 | 0.01457 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_593-6_0_5_line_14 |  | 11 | 15 | 0.017629 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_593-6_0_5_line_15 |  | 11 | 16 | 0.003091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_593-6_0_5_line_16 |  | 12 | 17 | 0.0060818 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_593-6_0_5_line_17 |  | 13 | 18 | 0.004106 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_593-6_0_5_line_18 |  | 14 | 43 | 0.00029912 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_593-6_0_5_line_19 |  | 15 | 23 | 0.018201 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_593-6_0_5_line_20 |  | 16 | 19 | 0.011279 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_593-6_0_5_line_21 |  | 17 | 30 | 0.0094558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_593-6_0_5_line_22 |  | 19 | 20 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_593-6_0_5_line_23 |  | 20 | 21 | 0.008373 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_593-6_0_5_line_24 |  | 21 | 22 | 0.025729 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_593-6_0_5_line_25 |  | 23 | 29 | 0.00072839 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_593-6_0_5_line_26 |  | 24 | 25 | 0.22168 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_593-6_0_5_line_27 |  | 24 | 26 | 0.043537 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_593-6_0_5_line_28 |  | 25 | 41 | 0.016142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_593-6_0_5_line_29 |  | 26 | 38 | 0.01252 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_593-6_0_5_line_30 |  | 27 | 28 | 0.015239 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_593-6_0_5_line_31 |  | 28 | 37 | 0.00080586 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_593-6_0_5_line_32 |  | 29 | 33 | 0.013827 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_593-6_0_5_line_33 |  | 30 | 31 | 0.00075424 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_593-6_0_5_line_34 |  | 31 | 32 | 0.0080515 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_593-6_0_5_line_35 |  | 32 | 34 | 0.0033497 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_593-6_0_5_line_36 |  | 33 | 47 | 0.00048182 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_593-6_0_5_line_37 |  | 34 | 35 | 0.0033246 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_593-6_0_5_line_38 |  | 35 | 36 | 0.00086272 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_593-6_0_5_line_39 |  | 36 | 37 | 0.00058803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_593-6_0_5_line_40 |  | 38 | 39 | 0.0017295 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_593-6_0_5_line_41 |  | 39 | 40 | 0.0038249 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_593-6_0_5_line_42 |  | 40 | 42 | 0.0049177 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_593-6_0_5_line_43 |  | 41 | 43 | 0.01076 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_593-6_0_5_line_44 |  | 42 | 44 | 0.0099031 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_593-6_0_5_line_45 |  | 45 | 46 | 0.010184 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_593-6_0_5_line_46 |  | 46 | 50 | 0.011235 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_593-6_0_5_line_47 |  | 47 | 48 | 0.028042 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_593-6_0_5_line_48 |  | 47 | 49 | 0.011079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_593-6_0_5_line_49 |  | 49 | 52 | 0.0020434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_593-6_0_5_line_50 |  | 50 | 51 | 0.0036153 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_593-6_0_5_line_51 |  | 51 | 52 | 0.0075742 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_593-6_0_5_trafo_4 | 0.63 MVA 20/0.4 kV | 53 | 4 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20 | x21 | y21
0 | 2631318.7042 | 1170527.2984 | 2631318.7042 | 1170527.2984 | 2631316.1319 | 1170529.1193 | 2631310.6721 | 1170532.9826
1 | 2631326.2934 | 1170519.9564 | 2631318.7042 | 1170527.2984
2 | 2631309.0982 | 1170534.0963 | 2631309.0982 | 1170534.0963 | 2631310.6721 | 1170532.9826
3 | 2631326.2934 | 1170519.9564 | 2631328.8978 | 1170520.8037 | 2631332.2002 | 1170521.2989 | 2631335.2306 | 1170521.1368 | 2631339.0974 | 1170520.5011 | 2631342.2162 | 1170519.5169
4 | 2631326.2934 | 1170519.9564 | 2631322.4977 | 1170518.7026 | 2631317.874 | 1170515.8008
5 | 2631309.0982 | 1170534.0963 | 2631303.539 | 1170537.0639
6 | 2631342.2162 | 1170519.5169 | 2631345.2996 | 1170517.9988 | 2631348.7078 | 1170515.8154 | 2631355.7472 | 1170511.318
7 | 2631342.2162 | 1170519.5169 | 2631349.2036 | 1170529.3027 | 2631352.3809 | 1170531.8046
8 | 2631317.874 | 1170515.8008 | 2631316.6032 | 1170515.0033 | 2631308.8474 | 1170508.7931 | 2631307.3874 | 1170507.6217
9 | 2631302.9975 | 1170537.3529 | 2631303.539 | 1170537.0639
10 | 2631360.0299 | 1170508.5819 | 2631355.7472 | 1170511.318
11 | 2631352.5286 | 1170531.9209 | 2631352.3809 | 1170531.8046
12 | 2631305.2484 | 1170505.8929 | 2631306.2952 | 1170506.7454 | 2631307.3874 | 1170507.6217
13 | 2631290.1446 | 1170544.214 | 2631302.9975 | 1170537.3529
14 | 2631360.0299 | 1170508.5819 | 2631357.1474 | 1170503.8533 | 2631355.4974 | 1170501.8992 | 2631348.5002 | 1170495.4238
15 | 2631360.0299 | 1170508.5819 | 2631360.5672 | 1170508.2289 | 2631362.6284 | 1170506.908
16 | 2631357.307 | 1170535.6833 | 2631352.5286 | 1170531.9209
17 | 2631305.2484 | 1170505.8929 | 2631302.0648 | 1170503.2999
18 | 2631289.8807 | 1170544.3549 | 2631290.1446 | 1170544.214
19 | 2631335.1258 | 1170483.0802 | 2631335.5038 | 1170483.3966 | 2631348.5002 | 1170495.4238
20 | 2631372.3422 | 1170501.1782 | 2631367.8276 | 1170503.7978 | 2631364.198 | 1170505.9022 | 2631362.6284 | 1170506.908
21 | 2631364.1244 | 1170542.1892 | 2631360.5027 | 1170538.1996 | 2631357.307 | 1170535.6833
22 | 2631382.1003 | 1170495.5792 | 2631380.3971 | 1170496.5041 | 2631372.3422 | 1170501.1782
23 | 2631382.1003 | 1170495.5792 | 2631382.9599 | 1170495.0612 | 2631389.3899 | 1170491.4262
24 | 2631389.3899 | 1170491.4262 | 2631378.1014 | 1170476.1039 | 2631373.6248 | 1170471.1225
25 | 2631335.1258 | 1170483.0802 | 2631334.5672 | 1170482.6127
26 | 2631266.152 | 1170557.0292 | 2631262.999 | 1170558.7025 | 2631262.1627 | 1170559.1762 | 2631249.4026 | 1170566.4025 | 2631200.7029 | 1170596.8987 | 2631184.4879 | 1170607.9981 | 2631180.5262 | 1170610.7123 | 2631185.0534 | 1170616.9501 | 2631189.3022 | 1170622.2971 | 2631204.5008 | 1170638.9956 | 2631207.4241 | 1170643.2463 | 2631208.6997 | 1170645.0983 | 2631211.3214 | 1170648.4914 | 2631225.7011 | 1170666.6976 | 2631229.4768 | 1170670.308 | 2631231.8003 | 1170672.1988 | 2631241.3029 | 1170677.8955 | 2631246.7985 | 1170680.3031 | 2631256.6002 | 1170682.8998 | 2631263.3074 | 1170683.3015 | 2631264.8981 | 1170683.3987 | 2631269.7026 | 1170683.357
27 | 2631269.7026 | 1170683.357 | 2631272.2985 | 1170677.0006 | 2631275.8984 | 1170670.3047 | 2631285.699 | 1170654.0029 | 2631290.6662 | 1170645.2693
28 | 2631266.152 | 1170557.0292 | 2631280.3891 | 1170549.4228
29 | 2631295.8019 | 1170634.0007 | 2631295.6008 | 1170635.9006 | 2631294.8019 | 1170637.9976 | 2631290.6662 | 1170645.2693
30 | 2631385.6853 | 1170567.1344 | 2631375.8315 | 1170555.5099
31 | 2631375.8315 | 1170555.5099 | 2631375.3104 | 1170554.8952
32 | 2631322.5704 | 1170476.1618 | 2631325.4014 | 1170476.7962 | 2631328.302 | 1170478.0564 | 2631331.7485 | 1170480.2532 | 2631334.5672 | 1170482.6127
33 | 2631364.6314 | 1170542.7477 | 2631364.1244 | 1170542.1892
34 | 2631370.0431 | 1170548.7092 | 2631364.6314 | 1170542.7477
35 | 2631372.2226 | 1170551.2525 | 2631370.3989 | 1170549.1012 | 2631370.0431 | 1170548.7092
36 | 2631322.5704 | 1170476.1618 | 2631322.1002 | 1170476.0564
37 | 2631372.2226 | 1170551.2525 | 2631374.3723 | 1170553.7886
38 | 2631374.9302 | 1170554.4467 | 2631374.3723 | 1170553.7886
39 | 2631375.3104 | 1170554.8952 | 2631374.9302 | 1170554.4467
40 | 2631295.8019 | 1170634.0007 | 2631295.8019 | 1170634.0007 | 2631295.4972 | 1170632.2982
41 | 2631293.8359 | 1170628.8529 | 2631295.4972 | 1170632.2982 | 2631295.4972 | 1170632.2982
42 | 2631293.8359 | 1170628.8529 | 2631291.7 | 1170624.4233
43 | 2631289.8807 | 1170544.3549 | 2631282.7612 | 1170548.1554 | 2631280.3891 | 1170549.4228
44 | 2631287.3988 | 1170615.503 | 2631291.7 | 1170624.4233
45 | 2631291.1734 | 1170459.4891 | 2631283.9508 | 1170453.3462 | 2631283.3735 | 1170452.9455
46 | 2631291.1734 | 1170459.4891 | 2631296.6022 | 1170464.1064 | 2631299.3468 | 1170465.955 | 2631300.0456 | 1170466.3426
47 | 2631322.1002 | 1170476.0564 | 2631324.4019 | 1170470.3988 | 2631327.3024 | 1170465.8004 | 2631334.2503 | 1170456.7542 | 2631337.6304 | 1170452.9478
48 | 2631322.1002 | 1170476.0564 | 2631314.3977 | 1170474.3043 | 2631311.6172 | 1170472.7618
49 | 2631311.6172 | 1170472.7618 | 2631309.8304 | 1170471.7706
50 | 2631300.0456 | 1170466.3426 | 2631303.207 | 1170468.0964
51 | 2631303.207 | 1170468.0964 | 2631309.8304 | 1170471.7706

## bus_geodata
| x | y | coords
0 | 2631318.7042 | 1170527.2984
1 | 2631310.6721 | 1170532.9826
2 | 2631326.2934 | 1170519.9564
3 | 2631309.0982 | 1170534.0963
4 | 2631342.2162 | 1170519.5169
5 | 2631317.874 | 1170515.8008
6 | 2631303.539 | 1170537.0639
7 | 2631355.7472 | 1170511.318
8 | 2631352.3809 | 1170531.8046
9 | 2631307.3874 | 1170507.6217
10 | 2631302.9975 | 1170537.3529
11 | 2631360.0299 | 1170508.5819
12 | 2631352.5286 | 1170531.9209
13 | 2631305.2484 | 1170505.8929
14 | 2631290.1446 | 1170544.214
15 | 2631348.5002 | 1170495.4238
16 | 2631362.6284 | 1170506.908
17 | 2631357.307 | 1170535.6833
18 | 2631302.0648 | 1170503.2999
19 | 2631372.3422 | 1170501.1782
20 | 2631382.1003 | 1170495.5792
21 | 2631389.3899 | 1170491.4262
22 | 2631373.6248 | 1170471.1225
23 | 2631335.1258 | 1170483.0802
24 | 2631269.7026 | 1170683.357
25 | 2631266.152 | 1170557.0292
26 | 2631290.6662 | 1170645.2693
27 | 2631385.6853 | 1170567.1344
28 | 2631375.8315 | 1170555.5099
29 | 2631334.5672 | 1170482.6127
30 | 2631364.1244 | 1170542.1892
31 | 2631364.6314 | 1170542.7477
32 | 2631370.0431 | 1170548.7092
33 | 2631322.5704 | 1170476.1618
34 | 2631372.2226 | 1170551.2525
35 | 2631374.3723 | 1170553.7886
36 | 2631374.9302 | 1170554.4467
37 | 2631375.3104 | 1170554.8952
38 | 2631295.8019 | 1170634.0007
39 | 2631295.4972 | 1170632.2982
40 | 2631293.8359 | 1170628.8529
41 | 2631280.3891 | 1170549.4228
42 | 2631291.7 | 1170624.4233
43 | 2631289.8807 | 1170544.3549
44 | 2631287.3988 | 1170615.503
45 | 2631283.3735 | 1170452.9455
46 | 2631291.1734 | 1170459.4891
47 | 2631322.1002 | 1170476.0564
48 | 2631337.6304 | 1170452.9478
49 | 2631311.6172 | 1170472.7618
50 | 2631300.0456 | 1170466.3426
51 | 2631303.207 | 1170468.0964
52 | 2631309.8304 | 1170471.7706
53 | 2631326.2934 | 1170519.9564

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | FALSE | FALSE |  | 50 | 1