## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6007-1_0_4_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6007-1_0_4_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6007-1_0_4_node_2 | 0.4 | n |  | TRUE
3 | bus_LV_6007-1_0_4_node_3 | 0.4 | n |  | TRUE
4 | bus_LV_6007-1_0_4_node_12 | 0.4 | n |  | TRUE
5 | bus_LV_6007-1_0_4_node_9 | 0.4 | n |  | TRUE
6 | bus_LV_6007-1_0_4_node_11 | 0.4 | n |  | TRUE
7 | bus_LV_6007-1_0_4_node_33 | 0.4 | n |  | TRUE
8 | bus_LV_6007-1_0_4_node_8 | 0.4 | n |  | TRUE
9 | bus_LV_6007-1_0_4_node_122 | 0.4 | n |  | TRUE
10 | bus_LV_6007-1_0_4_node_7 | 0.4 | n |  | TRUE
11 | bus_LV_6007-1_0_4_node_4 | 0.4 | n |  | TRUE
12 | bus_LV_6007-1_0_4_node_5 | 0.4 | n |  | TRUE
13 | bus_LV_6007-1_0_4_node_6 | 0.4 | n |  | TRUE
14 | bus_LV_6007-1_0_4_node_10 | 0.4 | n |  | TRUE
15 | bus_LV_6007-1_0_4_node_13 | 0.4 | n |  | TRUE
16 | bus_LV_6007-1_0_4_node_16 | 0.4 | n |  | TRUE
17 | bus_LV_6007-1_0_4_node_17 | 0.4 | n |  | TRUE
18 | bus_LV_6007-1_0_4_node_14 | 0.4 | n |  | TRUE
19 | bus_LV_6007-1_0_4_node_32 | 0.4 | n |  | TRUE
20 | bus_LV_6007-1_0_4_node_21 | 0.4 | n |  | TRUE
21 | bus_LV_6007-1_0_4_node_15 | 0.4 | n |  | TRUE
22 | bus_LV_6007-1_0_4_node_22 | 0.4 | n |  | TRUE
23 | bus_LV_6007-1_0_4_node_23 | 0.4 | n |  | TRUE
24 | bus_LV_6007-1_0_4_node_42 | 0.4 | n |  | TRUE
25 | bus_LV_6007-1_0_4_node_18 | 0.4 | n |  | TRUE
26 | bus_LV_6007-1_0_4_node_19 | 0.4 | n |  | TRUE
27 | bus_LV_6007-1_0_4_node_20 | 0.4 | n |  | TRUE
28 | bus_LV_6007-1_0_4_node_40 | 0.4 | n |  | TRUE
29 | bus_LV_6007-1_0_4_node_41 | 0.4 | n |  | TRUE
30 | bus_LV_6007-1_0_4_node_111 | 0.4 | n |  | TRUE
31 | bus_LV_6007-1_0_4_node_109 | 0.4 | n |  | TRUE
32 | bus_LV_6007-1_0_4_node_116 | 0.4 | n |  | TRUE
33 | bus_LV_6007-1_0_4_node_114 | 0.4 | n |  | TRUE
34 | bus_LV_6007-1_0_4_node_66 | 0.4 | n |  | TRUE
35 | bus_LV_6007-1_0_4_node_67 | 0.4 | n |  | TRUE
36 | bus_LV_6007-1_0_4_node_24 | 0.4 | n |  | TRUE
37 | bus_LV_6007-1_0_4_node_25 | 0.4 | n |  | TRUE
38 | bus_LV_6007-1_0_4_node_26 | 0.4 | n |  | TRUE
39 | bus_LV_6007-1_0_4_node_27 | 0.4 | n |  | TRUE
40 | bus_LV_6007-1_0_4_node_28 | 0.4 | n |  | TRUE
41 | bus_LV_6007-1_0_4_node_29 | 0.4 | n |  | TRUE
42 | bus_LV_6007-1_0_4_node_127 | 0.4 | n |  | TRUE
43 | bus_LV_6007-1_0_4_node_124 | 0.4 | n |  | TRUE
44 | bus_LV_6007-1_0_4_node_89 | 0.4 | n |  | TRUE
45 | bus_LV_6007-1_0_4_node_85 | 0.4 | n |  | TRUE
46 | bus_LV_6007-1_0_4_node_128 | 0.4 | n |  | TRUE
47 | bus_LV_6007-1_0_4_node_119 | 0.4 | n |  | TRUE
48 | bus_LV_6007-1_0_4_node_87 | 0.4 | n |  | TRUE
49 | bus_LV_6007-1_0_4_node_84 | 0.4 | n |  | TRUE
50 | bus_LV_6007-1_0_4_node_30 | 0.4 | n |  | TRUE
51 | bus_LV_6007-1_0_4_node_54 | 0.4 | n |  | TRUE
52 | bus_LV_6007-1_0_4_node_39 | 0.4 | n |  | TRUE
53 | bus_LV_6007-1_0_4_node_48 | 0.4 | n |  | TRUE
54 | bus_LV_6007-1_0_4_node_31 | 0.4 | n |  | TRUE
55 | bus_LV_6007-1_0_4_node_47 | 0.4 | n |  | TRUE
56 | bus_LV_6007-1_0_4_node_58 | 0.4 | n |  | TRUE
57 | bus_LV_6007-1_0_4_node_45 | 0.4 | n |  | TRUE
58 | bus_LV_6007-1_0_4_node_34 | 0.4 | n |  | TRUE
59 | bus_LV_6007-1_0_4_node_35 | 0.4 | n |  | TRUE
60 | bus_LV_6007-1_0_4_node_36 | 0.4 | n |  | TRUE
61 | bus_LV_6007-1_0_4_node_37 | 0.4 | n |  | TRUE
62 | bus_LV_6007-1_0_4_node_38 | 0.4 | n |  | TRUE
63 | bus_LV_6007-1_0_4_node_51 | 0.4 | n |  | TRUE
64 | bus_LV_6007-1_0_4_node_49 | 0.4 | n |  | TRUE
65 | bus_LV_6007-1_0_4_node_62 | 0.4 | n |  | TRUE
66 | bus_LV_6007-1_0_4_node_59 | 0.4 | n |  | TRUE
67 | bus_LV_6007-1_0_4_node_50 | 0.4 | n |  | TRUE
68 | bus_LV_6007-1_0_4_node_60 | 0.4 | n |  | TRUE
69 | bus_LV_6007-1_0_4_node_43 | 0.4 | n |  | TRUE
70 | bus_LV_6007-1_0_4_node_78 | 0.4 | n |  | TRUE
71 | bus_LV_6007-1_0_4_node_117 | 0.4 | n |  | TRUE
72 | bus_LV_6007-1_0_4_node_71 | 0.4 | n |  | TRUE
73 | bus_LV_6007-1_0_4_node_79 | 0.4 | n |  | TRUE
74 | bus_LV_6007-1_0_4_node_82 | 0.4 | n |  | TRUE
75 | bus_LV_6007-1_0_4_node_44 | 0.4 | n |  | TRUE
76 | bus_LV_6007-1_0_4_node_46 | 0.4 | n |  | TRUE
77 | bus_LV_6007-1_0_4_node_57 | 0.4 | n |  | TRUE
78 | bus_LV_6007-1_0_4_node_53 | 0.4 | n |  | TRUE
79 | bus_LV_6007-1_0_4_node_52 | 0.4 | n |  | TRUE
80 | bus_LV_6007-1_0_4_node_120 | 0.4 | n |  | TRUE
81 | bus_LV_6007-1_0_4_node_118 | 0.4 | n |  | TRUE
82 | bus_LV_6007-1_0_4_node_73 | 0.4 | n |  | TRUE
83 | bus_LV_6007-1_0_4_node_65 | 0.4 | n |  | TRUE
84 | bus_LV_6007-1_0_4_node_55 | 0.4 | n |  | TRUE
85 | bus_LV_6007-1_0_4_node_56 | 0.4 | n |  | TRUE
86 | bus_LV_6007-1_0_4_node_74 | 0.4 | n |  | TRUE
87 | bus_LV_6007-1_0_4_node_61 | 0.4 | n |  | TRUE
88 | bus_LV_6007-1_0_4_node_75 | 0.4 | n |  | TRUE
89 | bus_LV_6007-1_0_4_node_76 | 0.4 | n |  | TRUE
90 | bus_LV_6007-1_0_4_node_96 | 0.4 | n |  | TRUE
91 | bus_LV_6007-1_0_4_node_97 | 0.4 | n |  | TRUE
92 | bus_LV_6007-1_0_4_node_63 | 0.4 | n |  | TRUE
93 | bus_LV_6007-1_0_4_node_64 | 0.4 | n |  | TRUE
94 | bus_LV_6007-1_0_4_node_80 | 0.4 | n |  | TRUE
95 | bus_LV_6007-1_0_4_node_81 | 0.4 | n |  | TRUE
96 | bus_LV_6007-1_0_4_node_83 | 0.4 | n |  | TRUE
97 | bus_LV_6007-1_0_4_node_68 | 0.4 | n |  | TRUE
98 | bus_LV_6007-1_0_4_node_69 | 0.4 | n |  | TRUE
99 | bus_LV_6007-1_0_4_node_70 | 0.4 | n |  | TRUE
100 | bus_LV_6007-1_0_4_node_72 | 0.4 | n |  | TRUE
101 | bus_LV_6007-1_0_4_node_102 | 0.4 | n |  | TRUE
102 | bus_LV_6007-1_0_4_node_104 | 0.4 | n |  | TRUE
103 | bus_LV_6007-1_0_4_node_101 | 0.4 | n |  | TRUE
104 | bus_LV_6007-1_0_4_node_77 | 0.4 | n |  | TRUE
105 | bus_LV_6007-1_0_4_node_106 | 0.4 | n |  | TRUE
106 | bus_LV_6007-1_0_4_node_121 | 0.4 | n |  | TRUE
107 | bus_LV_6007-1_0_4_node_98 | 0.4 | n |  | TRUE
108 | bus_LV_6007-1_0_4_node_112 | 0.4 | n |  | TRUE
109 | bus_LV_6007-1_0_4_node_86 | 0.4 | n |  | TRUE
110 | bus_LV_6007-1_0_4_node_88 | 0.4 | n |  | TRUE
111 | bus_LV_6007-1_0_4_node_90 | 0.4 | n |  | TRUE
112 | bus_LV_6007-1_0_4_node_99 | 0.4 | n |  | TRUE
113 | bus_LV_6007-1_0_4_node_100 | 0.4 | n |  | TRUE
114 | bus_LV_6007-1_0_4_node_91 | 0.4 | n |  | TRUE
115 | bus_LV_6007-1_0_4_node_92 | 0.4 | n |  | TRUE
116 | bus_LV_6007-1_0_4_node_93 | 0.4 | n |  | TRUE
117 | bus_LV_6007-1_0_4_node_94 | 0.4 | n |  | TRUE
118 | bus_LV_6007-1_0_4_node_95 | 0.4 | n |  | TRUE
119 | bus_LV_6007-1_0_4_node_123 | 0.4 | n |  | TRUE
120 | bus_LV_6007-1_0_4_node_125 | 0.4 | n |  | TRUE
121 | bus_LV_6007-1_0_4_node_126 | 0.4 | n |  | TRUE
122 | bus_LV_6007-1_0_4_node_130 | 0.4 | n |  | TRUE
123 | bus_LV_6007-1_0_4_node_103 | 0.4 | n |  | TRUE
124 | bus_LV_6007-1_0_4_node_105 | 0.4 | n |  | TRUE
125 | bus_LV_6007-1_0_4_node_110 | 0.4 | n |  | TRUE
126 | bus_LV_6007-1_0_4_node_107 | 0.4 | n |  | TRUE
127 | bus_LV_6007-1_0_4_node_108 | 0.4 | n |  | TRUE
128 | bus_LV_6007-1_0_4_node_113 | 0.4 | n |  | TRUE
129 | bus_LV_6007-1_0_4_node_131 | 0.4 | n |  | TRUE
130 | bus_LV_6007-1_0_4_node_129 | 0.4 | n |  | TRUE
131 | bus_LV_6007-1_0_4_node_132 | 0.4 | n |  | TRUE
132 | bus_LV_6007-1_0_4_node_133 | 0.4 | n |  | TRUE
133 | bus_MV_85_0_node_99 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6007-1_0_4_load_0 | 0 | 0.023082 | 0.005785 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6007-1_0_4_load_2 | 2 | 0.0086632 | 0.0021712 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6007-1_0_4_load_12 | 4 | 0.0038739 | 0.0009709 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6007-1_0_4_load_9 | 5 | 0.0039451 | 0.00098873 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6007-1_0_4_load_33 | 7 | 0.0059221 | 0.0014842 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6007-1_0_4_load_8 | 8 | 0.0073998 | 0.0018546 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6007-1_0_4_load_4 | 11 | 0.0021638 | 0.00054229 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6007-1_0_4_load_5 | 12 | 0.0041718 | 0.0010456 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6007-1_0_4_load_6 | 13 | 0.0060873 | 0.0015256 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6007-1_0_4_load_13 | 15 | 0.0078524 | 0.001968 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6007-1_0_4_load_16 | 16 | 0.0022337 | 0.00055982 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6007-1_0_4_load_17 | 17 | 0.0045916 | 0.0011508 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6007-1_0_4_load_14 | 18 | 0.0053556 | 0.0013422 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6007-1_0_4_load_32 | 19 | 0.0069005 | 0.0017294 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6007-1_0_4_load_21 | 20 | 0.0022542 | 0.00056495 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6007-1_0_4_load_22 | 22 | 0.0054468 | 0.0013651 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6007-1_0_4_load_23 | 23 | 0.0033083 | 0.00082915 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6007-1_0_4_load_42 | 24 | 0.0026878 | 0.00067363 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6007-1_0_4_load_19 | 26 | 0.0017142 | 0.00042962 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6007-1_0_4_load_20 | 27 | 0.003418 | 0.00085664 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6007-1_0_4_load_40 | 28 | 0.0024917 | 0.00062448 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6007-1_0_4_load_111 | 30 | 0.0021308 | 0.00053403 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6007-1_0_4_load_114 | 33 | 0.0037561 | 0.00094137 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6007-1_0_4_load_66 | 34 | 0.0032605 | 0.00081715 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6007-1_0_4_load_67 | 35 | 0.0059577 | 0.0014931 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6007-1_0_4_load_24 | 36 | 0.002152 | 0.00053935 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6007-1_0_4_load_25 | 37 | 0.0021246 | 0.00053247 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6007-1_0_4_load_27 | 39 | 0.0014474 | 0.00036276 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6007-1_0_4_load_28 | 40 | 0.0017162 | 0.00043011 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6007-1_0_4_load_29 | 41 | 0.0022518 | 0.00056435 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6007-1_0_4_load_127 | 42 | 0.0026763 | 0.00067074 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6007-1_0_4_load_124 | 43 | 0.0014478 | 0.00036286 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6007-1_0_4_load_85 | 45 | 0.0022347 | 0.00056006 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6007-1_0_4_load_128 | 46 | 0.0033543 | 0.00084067 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6007-1_0_4_load_119 | 47 | 0.0024103 | 0.00060409 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6007-1_0_4_load_87 | 48 | 0.0010264 | 0.00025724 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6007-1_0_4_load_84 | 49 | 0.0027374 | 0.00068605 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6007-1_0_4_load_30 | 50 | 0.0032929 | 0.00082527 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6007-1_0_4_load_54 | 51 | 0.0036235 | 0.00090814 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6007-1_0_4_load_39 | 52 | 0.0047456 | 0.0011894 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6007-1_0_4_load_48 | 53 | 0.0027505 | 0.00068933 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6007-1_0_4_load_31 | 54 | 0.0015349 | 0.00038469 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6007-1_0_4_load_47 | 55 | 0.0011587 | 0.00029039 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6007-1_0_4_load_58 | 56 | 0.0013283 | 0.0003329 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6007-1_0_4_load_45 | 57 | 0.0014685 | 0.00036803 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6007-1_0_4_load_34 | 58 | 0.0036137 | 0.00090569 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6007-1_0_4_load_35 | 59 | 0.003101 | 0.00077717 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6007-1_0_4_load_51 | 63 | 0.0026267 | 0.00065831 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6007-1_0_4_load_49 | 64 | 0.0037973 | 0.00095168 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6007-1_0_4_load_62 | 65 | 0.0053843 | 0.0013494 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6007-1_0_4_load_59 | 66 | 0.0037705 | 0.00094499 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6007-1_0_4_load_60 | 68 | 0.0022693 | 0.00056873 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6007-1_0_4_load_78 | 70 | 0.003958 | 0.00099197 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6007-1_0_4_load_79 | 73 | 0.0054405 | 0.0013635 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6007-1_0_4_load_82 | 74 | 0.0028989 | 0.00072653 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6007-1_0_4_load_44 | 75 | 0.001218 | 0.00030527 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6007-1_0_4_load_46 | 76 | 0.0015018 | 0.00037637 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6007-1_0_4_load_53 | 78 | 0.0024765 | 0.00062067 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6007-1_0_4_load_120 | 80 | 0.002146 | 0.00053783 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6007-1_0_4_load_118 | 81 | 0.0017592 | 0.00044091 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6007-1_0_4_load_73 | 82 | 0.0030042 | 0.00075291 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6007-1_0_4_load_65 | 83 | 0.0025468 | 0.00063828 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6007-1_0_4_load_55 | 84 | 0.0031827 | 0.00079765 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6007-1_0_4_load_74 | 86 | 0.0014127 | 0.00035407 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6007-1_0_4_load_61 | 87 | 0.0045023 | 0.0011284 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6007-1_0_4_load_75 | 88 | 0.0056064 | 0.0014051 | 0 | 0 |  | 1 | TRUE | wye
66 | LV_6007-1_0_4_load_76 | 89 | 0.0028788 | 0.0007215 | 0 | 0 |  | 1 | TRUE | wye
67 | LV_6007-1_0_4_load_96 | 90 | 0.0039573 | 0.0009918 | 0 | 0 |  | 1 | TRUE | wye
68 | LV_6007-1_0_4_load_97 | 91 | 0.0049385 | 0.0012377 | 0 | 0 |  | 1 | TRUE | wye
69 | LV_6007-1_0_4_load_63 | 92 | 0.0013747 | 0.00034454 | 0 | 0 |  | 1 | TRUE | wye
70 | LV_6007-1_0_4_load_64 | 93 | 0.0017872 | 0.00044791 | 0 | 0 |  | 1 | TRUE | wye
71 | LV_6007-1_0_4_load_81 | 95 | 0.0027506 | 0.00068938 | 0 | 0 |  | 1 | TRUE | wye
72 | LV_6007-1_0_4_load_83 | 96 | 0.00097963 | 0.00024552 | 0 | 0 |  | 1 | TRUE | wye
73 | LV_6007-1_0_4_load_68 | 97 | 0.0022564 | 0.00056551 | 0 | 0 |  | 1 | TRUE | wye
74 | LV_6007-1_0_4_load_69 | 98 | 0.0088237 | 0.0022114 | 0 | 0 |  | 1 | TRUE | wye
75 | LV_6007-1_0_4_load_70 | 99 | 0.0082421 | 0.0020657 | 0 | 0 |  | 1 | TRUE | wye
76 | LV_6007-1_0_4_load_72 | 100 | 0.0058865 | 0.0014753 | 0 | 0 |  | 1 | TRUE | wye
77 | LV_6007-1_0_4_load_104 | 102 | 0.00593 | 0.0014862 | 0 | 0 |  | 1 | TRUE | wye
78 | LV_6007-1_0_4_load_101 | 103 | 0.0030708 | 0.0007696 | 0 | 0 |  | 1 | TRUE | wye
79 | LV_6007-1_0_4_load_106 | 105 | 0.0043253 | 0.001084 | 0 | 0 |  | 1 | TRUE | wye
80 | LV_6007-1_0_4_load_121 | 106 | 0.0031551 | 0.00079075 | 0 | 0 |  | 1 | TRUE | wye
81 | LV_6007-1_0_4_load_98 | 107 | 0.006867 | 0.001721 | 0 | 0 |  | 1 | TRUE | wye
82 | LV_6007-1_0_4_load_112 | 108 | 0.0040809 | 0.0010228 | 0 | 0 |  | 1 | TRUE | wye
83 | LV_6007-1_0_4_load_86 | 109 | 0.0034001 | 0.00085214 | 0 | 0 |  | 1 | TRUE | wye
84 | LV_6007-1_0_4_load_88 | 110 | 0.0014293 | 0.00035823 | 0 | 0 |  | 1 | TRUE | wye
85 | LV_6007-1_0_4_load_90 | 111 | 0.0014032 | 0.00035168 | 0 | 0 |  | 1 | TRUE | wye
86 | LV_6007-1_0_4_load_99 | 112 | 0.0014788 | 0.00037061 | 0 | 0 |  | 1 | TRUE | wye
87 | LV_6007-1_0_4_load_91 | 114 | 0.00462 | 0.0011579 | 0 | 0 |  | 1 | TRUE | wye
88 | LV_6007-1_0_4_load_92 | 115 | 0.0030684 | 0.00076902 | 0 | 0 |  | 1 | TRUE | wye
89 | LV_6007-1_0_4_load_93 | 116 | 0.0051698 | 0.0012957 | 0 | 0 |  | 1 | TRUE | wye
90 | LV_6007-1_0_4_load_123 | 119 | 0.0041434 | 0.0010384 | 0 | 0 |  | 1 | TRUE | wye
91 | LV_6007-1_0_4_load_125 | 120 | 0.0023185 | 0.00058108 | 0 | 0 |  | 1 | TRUE | wye
92 | LV_6007-1_0_4_load_126 | 121 | 0.00088935 | 0.00022289 | 0 | 0 |  | 1 | TRUE | wye
93 | LV_6007-1_0_4_load_130 | 122 | 0.0027986 | 0.0007014 | 0 | 0 |  | 1 | TRUE | wye
94 | LV_6007-1_0_4_load_110 | 125 | 0.0026127 | 0.00065481 | 0 | 0 |  | 1 | TRUE | wye
95 | LV_6007-1_0_4_load_107 | 126 | 0.0032431 | 0.0008128 | 0 | 0 |  | 1 | TRUE | wye
96 | LV_6007-1_0_4_load_108 | 127 | 0.0036088 | 0.00090446 | 0 | 0 |  | 1 | TRUE | wye
97 | LV_6007-1_0_4_load_113 | 128 | 0.0040075 | 0.0010044 | 0 | 0 |  | 1 | TRUE | wye
98 | LV_6007-1_0_4_load_129 | 130 | 0.0029489 | 0.00073905 | 0 | 0 |  | 1 | TRUE | wye
99 | LV_6007-1_0_4_load_132 | 131 | 0.0023798 | 0.00059645 | 0 | 0 |  | 1 | TRUE | wye
100 | LV_6007-1_0_4_load_133 | 132 | 0.00069917 | 0.00017523 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 104 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6007-1_0_4_line_0 |  | 0 | 1 | 0.034929 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6007-1_0_4_line_1 |  | 0 | 2 | 0.058441 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6007-1_0_4_line_2 |  | 1 | 3 | 0.035652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6007-1_0_4_line_3 |  | 3 | 4 | 0.039227 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6007-1_0_4_line_4 |  | 3 | 5 | 0.025712 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6007-1_0_4_line_5 |  | 4 | 9 | 0.048318 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6007-1_0_4_line_6 |  | 5 | 10 | 0.018145 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6007-1_0_4_line_7 |  | 6 | 7 | 0.010811 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6007-1_0_4_line_8 |  | 6 | 8 | 0.014278 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6007-1_0_4_line_9 |  | 7 | 19 | 0.014693 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6007-1_0_4_line_10 |  | 8 | 13 | 0.010569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6007-1_0_4_line_11 |  | 9 | 20 | 0.15333 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6007-1_0_4_line_12 |  | 10 | 14 | 0.018138 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6007-1_0_4_line_13 |  | 10 | 12 | 0.010303 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6007-1_0_4_line_14 |  | 11 | 12 | 0.0029063 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6007-1_0_4_line_15 |  | 11 | 13 | 0.028159 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6007-1_0_4_line_16 |  | 14 | 15 | 0.015008 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6007-1_0_4_line_17 |  | 15 | 18 | 0.0071652 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6007-1_0_4_line_18 |  | 16 | 17 | 0.014932 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6007-1_0_4_line_19 |  | 17 | 25 | 0.013167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6007-1_0_4_line_20 |  | 18 | 21 | 0.024666 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6007-1_0_4_line_21 |  | 20 | 32 | 0.2148 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6007-1_0_4_line_22 |  | 21 | 22 | 0.0031393 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6007-1_0_4_line_23 |  | 21 | 23 | 0.0077187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6007-1_0_4_line_24 |  | 22 | 24 | 0.019314 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6007-1_0_4_line_25 |  | 24 | 29 | 0.0093052 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6007-1_0_4_line_26 |  | 25 | 26 | 0.016625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6007-1_0_4_line_27 |  | 25 | 27 | 0.013954 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6007-1_0_4_line_28 |  | 26 | 28 | 0.0096171 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6007-1_0_4_line_29 |  | 28 | 29 | 0.0034489 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6007-1_0_4_line_30 |  | 29 | 69 | 0.022261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6007-1_0_4_line_31 |  | 30 | 31 | 0.0042546 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6007-1_0_4_line_32 |  | 31 | 126 | 0.0050544 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6007-1_0_4_line_33 |  | 32 | 33 | 0.0076142 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6007-1_0_4_line_34 |  | 34 | 35 | 0.0077813 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6007-1_0_4_line_35 |  | 35 | 94 | 0.011261 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6007-1_0_4_line_36 |  | 36 | 37 | 0.01232 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6007-1_0_4_line_37 |  | 36 | 38 | 0.0010061 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6007-1_0_4_line_38 |  | 37 | 39 | 0.019208 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6007-1_0_4_line_39 |  | 38 | 40 | 0.012914 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6007-1_0_4_line_40 |  | 38 | 41 | 0.015888 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6007-1_0_4_line_41 |  | 39 | 42 | 0.0094678 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6007-1_0_4_line_42 |  | 39 | 43 | 0.01614 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6007-1_0_4_line_43 |  | 40 | 44 | 0.033206 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6007-1_0_4_line_44 |  | 41 | 45 | 0.013332 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6007-1_0_4_line_45 |  | 42 | 46 | 0.021878 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6007-1_0_4_line_46 |  | 44 | 47 | 0.027129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6007-1_0_4_line_47 |  | 44 | 48 | 0.0042724 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6007-1_0_4_line_48 |  | 45 | 49 | 0.0090514 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6007-1_0_4_line_49 |  | 46 | 130 | 0.0035353 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6007-1_0_4_line_50 |  | 47 | 81 | 0.011921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6007-1_0_4_line_51 |  | 48 | 109 | 0.0074955 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6007-1_0_4_line_52 |  | 49 | 63 | 0.0012354 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6007-1_0_4_line_53 |  | 50 | 51 | 0.080602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6007-1_0_4_line_54 |  | 51 | 52 | 0.01776 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6007-1_0_4_line_55 |  | 51 | 53 | 0.022223 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6007-1_0_4_line_56 |  | 52 | 60 | 0.0058475 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6007-1_0_4_line_57 |  | 53 | 76 | 0.064925 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6007-1_0_4_line_58 |  | 54 | 55 | 0.08019 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6007-1_0_4_line_59 |  | 55 | 56 | 0.0018294 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6007-1_0_4_line_60 |  | 55 | 57 | 0.012641 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6007-1_0_4_line_61 |  | 56 | 77 | 0.014451 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6007-1_0_4_line_62 |  | 57 | 75 | 0.0019707 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6007-1_0_4_line_63 |  | 58 | 59 | 0.023609 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6007-1_0_4_line_64 |  | 58 | 60 | 0.042079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6007-1_0_4_line_65 |  | 59 | 61 | 0.048755 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6007-1_0_4_line_66 |  | 60 | 62 | 0.007198 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6007-1_0_4_line_67 |  | 61 | 63 | 0.021733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6007-1_0_4_line_68 |  | 61 | 64 | 0.022187 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6007-1_0_4_line_69 |  | 62 | 65 | 0.0024646 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6007-1_0_4_line_70 |  | 62 | 66 | 0.012896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6007-1_0_4_line_71 |  | 64 | 67 | 0.010569 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6007-1_0_4_line_72 |  | 66 | 68 | 0.015703 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6007-1_0_4_line_73 |  | 67 | 78 | 0.011611 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6007-1_0_4_line_74 |  | 68 | 87 | 0.026074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6007-1_0_4_line_75 |  | 69 | 70 | 0.021185 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6007-1_0_4_line_76 |  | 69 | 71 | 0.010419 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
77 | LV_6007-1_0_4_line_77 |  | 70 | 72 | 0.0082118 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6007-1_0_4_line_78 |  | 71 | 73 | 0.0043552 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6007-1_0_4_line_79 |  | 71 | 74 | 0.01431 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
80 | LV_6007-1_0_4_line_80 |  | 72 | 98 | 0.0067035 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6007-1_0_4_line_81 |  | 74 | 94 | 0.023411 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
82 | LV_6007-1_0_4_line_82 |  | 75 | 76 | 0.021704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6007-1_0_4_line_83 |  | 77 | 86 | 0.011381 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
84 | LV_6007-1_0_4_line_84 |  | 77 | 85 | 0.064743 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
85 | LV_6007-1_0_4_line_85 |  | 78 | 82 | 0.020535 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
86 | LV_6007-1_0_4_line_86 |  | 79 | 80 | 0.013285 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
87 | LV_6007-1_0_4_line_87 |  | 79 | 81 | 0.014129 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
88 | LV_6007-1_0_4_line_88 |  | 82 | 83 | 0.024267 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
89 | LV_6007-1_0_4_line_89 |  | 83 | 93 | 0.014996 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
90 | LV_6007-1_0_4_line_90 |  | 84 | 85 | 0.021434 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
91 | LV_6007-1_0_4_line_91 |  | 87 | 88 | 0.016864 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
92 | LV_6007-1_0_4_line_92 |  | 88 | 89 | 0.0015558 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
93 | LV_6007-1_0_4_line_93 |  | 89 | 104 | 0.033406 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
94 | LV_6007-1_0_4_line_94 |  | 90 | 91 | 0.014789 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
95 | LV_6007-1_0_4_line_95 |  | 91 | 107 | 0.0026398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
96 | LV_6007-1_0_4_line_96 |  | 92 | 93 | 0.068016 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
97 | LV_6007-1_0_4_line_97 |  | 94 | 95 | 0.016454 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
98 | LV_6007-1_0_4_line_98 |  | 94 | 96 | 0.020599 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
99 | LV_6007-1_0_4_line_99 |  | 95 | 108 | 0.0055589 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
100 | LV_6007-1_0_4_line_100 |  | 96 | 106 | 0.0017369 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
101 | LV_6007-1_0_4_line_101 |  | 97 | 98 | 0.010265 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
102 | LV_6007-1_0_4_line_102 |  | 97 | 99 | 0.0049901 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
103 | LV_6007-1_0_4_line_103 |  | 99 | 100 | 0.023487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
104 | LV_6007-1_0_4_line_104 |  | 100 | 101 | 0.0066216 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
105 | LV_6007-1_0_4_line_105 |  | 101 | 102 | 0.010152 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
106 | LV_6007-1_0_4_line_106 |  | 101 | 103 | 0.0053733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
107 | LV_6007-1_0_4_line_107 |  | 102 | 118 | 0.016308 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
108 | LV_6007-1_0_4_line_108 |  | 103 | 123 | 0.025858 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
109 | LV_6007-1_0_4_line_109 |  | 104 | 105 | 0.014116 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
110 | LV_6007-1_0_4_line_110 |  | 104 | 106 | 0.0033341 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 2 | cs | TRUE
111 | LV_6007-1_0_4_line_111 |  | 105 | 107 | 0.015942 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
112 | LV_6007-1_0_4_line_112 |  | 109 | 110 | 0.019964 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
113 | LV_6007-1_0_4_line_113 |  | 110 | 111 | 0.010539 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
114 | LV_6007-1_0_4_line_114 |  | 111 | 112 | 0.0016398 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
115 | LV_6007-1_0_4_line_115 |  | 112 | 113 | 0.025585 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
116 | LV_6007-1_0_4_line_116 |  | 113 | 121 | 0.037109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
117 | LV_6007-1_0_4_line_117 |  | 114 | 115 | 0.02079 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
118 | LV_6007-1_0_4_line_118 |  | 114 | 116 | 0.025443 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
119 | LV_6007-1_0_4_line_119 |  | 115 | 117 | 0.01572 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
120 | LV_6007-1_0_4_line_120 |  | 116 | 118 | 0.008927 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
121 | LV_6007-1_0_4_line_121 |  | 117 | 119 | 0.01708 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
122 | LV_6007-1_0_4_line_122 |  | 119 | 120 | 0.0068109 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
123 | LV_6007-1_0_4_line_123 |  | 120 | 128 | 0.00033803 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
124 | LV_6007-1_0_4_line_124 |  | 121 | 122 | 0.003806 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
125 | LV_6007-1_0_4_line_125 |  | 122 | 129 | 0.029926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
126 | LV_6007-1_0_4_line_126 |  | 123 | 124 | 0.013866 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
127 | LV_6007-1_0_4_line_127 |  | 124 | 125 | 0.023718 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
128 | LV_6007-1_0_4_line_128 |  | 125 | 127 | 0.0098091 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
129 | LV_6007-1_0_4_line_129 |  | 126 | 127 | 0.0065608 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
130 | LV_6007-1_0_4_line_130 |  | 129 | 131 | 0.0085447 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
131 | LV_6007-1_0_4_line_131 |  | 131 | 132 | 0.015329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6007-1_0_4_trafo_77 | 0.63 MVA 20/0.4 kV | 133 | 104 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5
0 | 2638785.2132 | 1129401.3668 | 2638782.0238 | 1129407.4383 | 2638785.4866 | 1129415.1866 | 2638796.9805 | 1129431.043
1 | 2638793.458 | 1129477.8361 | 2638810.2619 | 1129466.4159 | 2638801.4599 | 1129437.2224 | 2638796.9805 | 1129431.043
2 | 2638785.2132 | 1129401.3668 | 2638772.5614 | 1129391.0916 | 2638755.6842 | 1129381.4787
3 | 2638755.6842 | 1129381.4787 | 2638758.4558 | 1129376.9052 | 2638751.1788 | 1129364.5079 | 2638750.7238 | 1129350.1533 | 2638747.4558 | 1129346.1828
4 | 2638755.6842 | 1129381.4787 | 2638748.8008 | 1129391.8287 | 2638751.9896 | 1129401.4763 | 2638751.6012 | 1129404.5731
5 | 2638710.141 | 1129316.9546 | 2638722.6503 | 1129321.8482 | 2638738.3795 | 1129335.1555 | 2638747.4558 | 1129346.1828
6 | 2638743.5402 | 1129420.6097 | 2638751.2428 | 1129407.4301 | 2638751.6012 | 1129404.5731
7 | 2638719.6576 | 1129360.9711 | 2638710.2094 | 1129355.7167
8 | 2638719.6576 | 1129360.9711 | 2638718.0434 | 1129371.2659 | 2638718.6044 | 1129375.0826
9 | 2638710.2094 | 1129355.7167 | 2638707.0388 | 1129353.9535 | 2638696.362 | 1129351.6062 | 2638696.2301 | 1129351.5879
10 | 2638724.1901 | 1129384.0549 | 2638718.6044 | 1129375.0826
11 | 2638710.141 | 1129316.9546 | 2638638.3577 | 1129181.467
12 | 2638743.5402 | 1129420.6097 | 2638750.5274 | 1129437.3518
13 | 2638743.5402 | 1129420.6097 | 2638738.8233 | 1129411.4499
14 | 2638737.4927 | 1129408.8661 | 2638738.8233 | 1129411.4499
15 | 2638737.4927 | 1129408.8661 | 2638734.7754 | 1129403.5894 | 2638725.7334 | 1129386.534 | 2638724.1901 | 1129384.0549
16 | 2638750.5274 | 1129437.3518 | 2638737.4047 | 1129444.6341
17 | 2638737.4047 | 1129444.6341 | 2638731.1396 | 1129448.1109
18 | 2638767.6239 | 1129473.5719 | 2638763.8921 | 1129464.9735 | 2638761.28 | 1129460.0667
19 | 2638771.6599 | 1129486.0896 | 2638768.6288 | 1129475.8872 | 2638767.6239 | 1129473.5719
20 | 2638735.1974 | 1129472.427 | 2638733.5137 | 1129464.7012 | 2638731.1396 | 1129448.1109 | 2638731.1396 | 1129448.1109
21 | 2638638.3577 | 1129181.467 | 2638828.218 | 1129081.0135
22 | 2638735.1974 | 1129472.427 | 2638735.8671 | 1129475.494
23 | 2638735.1974 | 1129472.427 | 2638728.2921 | 1129475.876
24 | 2638735.8671 | 1129475.494 | 2638736.8213 | 1129479.8633 | 2638742.8229 | 1129493.4377
25 | 2638746.5857 | 1129501.9481 | 2638742.8229 | 1129493.4377
26 | 2638771.6599 | 1129486.0896 | 2638759.7846 | 1129492.917 | 2638757.3691 | 1129494.5698
27 | 2638771.6599 | 1129486.0896 | 2638774.0308 | 1129489.94 | 2638780.7037 | 1129496.6064
28 | 2638749.4321 | 1129500.0005 | 2638757.3691 | 1129494.5698
29 | 2638746.5857 | 1129501.9481 | 2638749.4321 | 1129500.0005
30 | 2638741.6442 | 1129518.2136 | 2638747.2603 | 1129512.0798 | 2638742.1302 | 1129506.0662 | 2638746.5857 | 1129501.9481
31 | 2638804.5789 | 1129515.382 | 2638800.911 | 1129513.2261
32 | 2638804.5789 | 1129515.382 | 2638807.7491 | 1129519.3186
33 | 2638828.218 | 1129081.0135 | 2638832.6745 | 1129080.3973 | 2638835.7803 | 1129080.6414
34 | 2638712.4838 | 1129497.7444 | 2638718.653 | 1129493.002
35 | 2638703.5561 | 1129504.6075 | 2638712.4838 | 1129497.7444
36 | 2638619.6589 | 1129555.5362 | 2638631.1816 | 1129559.8954
37 | 2638618.7179 | 1129555.1802 | 2638619.6589 | 1129555.5362
38 | 2638649.0999 | 1129563.2448 | 2638636.7312 | 1129558.1299 | 2638631.1816 | 1129559.8954
39 | 2638618.7179 | 1129555.1802 | 2638612.2378 | 1129553.0822 | 2638607.4448 | 1129555.7974 | 2638607.3571 | 1129556.3849
40 | 2638618.7179 | 1129555.1802 | 2638611.9232 | 1129540.8184
41 | 2638649.0999 | 1129563.2448 | 2638652.1283 | 1129554.6154 | 2638652.1673 | 1129554.2953
42 | 2638649.0999 | 1129563.2448 | 2638657.7581 | 1129566.8242 | 2638664.3945 | 1129568.1695
43 | 2638593.3681 | 1129585.356 | 2638596.0633 | 1129580.6486 | 2638599.7838 | 1129573.3908 | 2638601.2363 | 1129571.4991 | 2638605.6906 | 1129567.5478 | 2638607.3571 | 1129556.3849
44 | 2638611.9232 | 1129540.8184 | 2638604.7586 | 1129529.5751
45 | 2638646.2179 | 1129534.2142 | 2638651.5847 | 1129542.05 | 2638652.7787 | 1129549.2724 | 2638652.1673 | 1129554.2953
46 | 2638593.3681 | 1129585.356 | 2638577.8004 | 1129563.6902 | 2638577.5852 | 1129563.2944
47 | 2638593.3681 | 1129585.356 | 2638596.6043 | 1129588.1453
48 | 2638598.3052 | 1129523.2812 | 2638604.1062 | 1129528.5512 | 2638604.7586 | 1129529.5751
49 | 2638644.2202 | 1129531.2975 | 2638646.2179 | 1129534.2142
50 | 2638571.8909 | 1129552.8219 | 2638577.5852 | 1129563.2944
51 | 2638602.2818 | 1129593.039 | 2638596.6043 | 1129588.1453
52 | 2638598.3052 | 1129523.2812 | 2638597.3908 | 1129522.4505
53 | 2638581.2792 | 1129410.5469 | 2638606.7308 | 1129334.069
54 | 2638581.2792 | 1129410.5469 | 2638595.1308 | 1129414.0916 | 2638598.1713 | 1129415.7482
55 | 2638581.2792 | 1129410.5469 | 2638570.5831 | 1129407.8097 | 2638561.177 | 1129401.7627
56 | 2638603.306 | 1129418.546 | 2638598.1713 | 1129415.7482
57 | 2638561.177 | 1129401.7627 | 2638552.2098 | 1129395.9978 | 2638536.6296 | 1129385.8712 | 2638518.2781 | 1129371.8251 | 2638507.2557 | 1129365.7769
58 | 2638476.8806 | 1129346.649 | 2638518.175 | 1129277.9085
59 | 2638476.8806 | 1129346.649 | 2638475.2419 | 1129345.8357
60 | 2638476.8806 | 1129346.649 | 2638476.8806 | 1129346.649 | 2638482.6421 | 1129351.5437 | 2638486.5493 | 1129354.7913
61 | 2638461.8206 | 1129340.6725 | 2638468.4185 | 1129342.4487 | 2638475.2419 | 1129345.8357
62 | 2638488.0648 | 1129356.051 | 2638486.5493 | 1129354.7913
63 | 2638588.8889 | 1129463.2246 | 2638588.5791 | 1129460.6512 | 2638582.4421 | 1129440.5504
64 | 2638603.306 | 1129418.546 | 2638589.8795 | 1129418.5937 | 2638584.33 | 1129419.1253 | 2638579.4128 | 1129428.0095 | 2638580.6113 | 1129434.5538 | 2638582.4421 | 1129440.5504
65 | 2638581.4544 | 1129507.674 | 2638588.8322 | 1129503.0854 | 2638590.8614 | 1129479.6087 | 2638588.8889 | 1129463.2246
66 | 2638603.306 | 1129418.546 | 2638609.1953 | 1129422.7079
67 | 2638581.4544 | 1129507.674 | 2638593.8286 | 1129519.2143 | 2638597.3908 | 1129522.4505
68 | 2638581.4544 | 1129507.674 | 2638575.3876 | 1129503.5888 | 2638566.3265 | 1129496.7387 | 2638564.242 | 1129493.9103
69 | 2638609.1953 | 1129422.7079 | 2638611.2089 | 1129424.129
70 | 2638609.1953 | 1129422.7079 | 2638622.0643 | 1129423.5415
71 | 2638557.9718 | 1129485.402 | 2638564.242 | 1129493.9103
72 | 2638622.0643 | 1129423.5415 | 2638623.6632 | 1129423.6451 | 2638636.9601 | 1129428.3381
73 | 2638557.9718 | 1129485.402 | 2638549.5779 | 1129477.379
74 | 2638636.9601 | 1129428.3381 | 2638641.7551 | 1129430.0304 | 2638658.8032 | 1129442.2736
75 | 2638741.6442 | 1129518.2136 | 2638752.7327 | 1129528.3787 | 2638756.465 | 1129533.2564
76 | 2638741.6442 | 1129518.2136 | 2638739.4956 | 1129520.5455 | 2638735.3146 | 1129525.0988 | 2638734.5854 | 1129525.8946
77 | 2638757.8135 | 1129539.6725 | 2638759.6993 | 1129537.4834 | 2638756.465 | 1129533.2564
78 | 2638734.5854 | 1129525.8946 | 2638737.9606 | 1129528.647
79 | 2638734.5854 | 1129525.8946 | 2638731.9632 | 1129523.9991 | 2638728.6684 | 1129521.2877 | 2638723.4176 | 1129516.9547
80 | 2638757.8135 | 1129539.6725 | 2638763.7649 | 1129542.7576
81 | 2638703.5561 | 1129504.6075 | 2638713.7851 | 1129510.6871 | 2638721.5271 | 1129515.3946 | 2638723.4176 | 1129516.9547
82 | 2638488.0648 | 1129356.051 | 2638492.09 | 1129359.3966 | 2638504.9139 | 1129364.4919 | 2638507.2557 | 1129365.7769
83 | 2638461.8206 | 1129340.6725 | 2638457.41 | 1129334.1078 | 2638454.9022 | 1129331.7058
84 | 2638504.1395 | 1129388.1212 | 2638495.7868 | 1129378.8633 | 2638476.9978 | 1129362.1354 | 2638465.7145 | 1129352.1809 | 2638461.8206 | 1129340.6725
85 | 2638549.5779 | 1129477.379 | 2638538.992 | 1129467.2608 | 2638533.8335 | 1129464.4146
86 | 2638569.5526 | 1129539.2475 | 2638563.5633 | 1129541.1214 | 2638556.5628 | 1129541.4724
87 | 2638569.5526 | 1129539.2475 | 2638569.7149 | 1129548.82 | 2638571.8909 | 1129552.8219
88 | 2638512.5864 | 1129452.6916 | 2638533.8335 | 1129464.4146
89 | 2638499.4565 | 1129445.4472 | 2638512.5864 | 1129452.6916
90 | 2638504.1395 | 1129388.1212 | 2638517.4129 | 1129404.9501
91 | 2638669.2631 | 1129455.1772 | 2638662.9027 | 1129445.2176 | 2638658.8032 | 1129442.2736
92 | 2638669.2631 | 1129455.1772 | 2638670.1005 | 1129456.4884
93 | 2638686.3775 | 1129485.5325 | 2638680.8351 | 1129472.9129 | 2638675.7839 | 1129465.3879 | 2638670.1005 | 1129456.4884
94 | 2638648.7775 | 1129456.9818 | 2638659.9021 | 1129466.7272
95 | 2638659.9021 | 1129466.7272 | 2638661.8877 | 1129468.4667
96 | 2638436.4033 | 1129420.5447 | 2638446.8429 | 1129425.9984 | 2638490.296 | 1129440.3929 | 2638499.4565 | 1129445.4472
97 | 2638703.5561 | 1129504.6075 | 2638698.5568 | 1129520.2835 | 2638698.5568 | 1129520.2835
98 | 2638703.5561 | 1129504.6075 | 2638689.771 | 1129489.3007
99 | 2638698.5568 | 1129520.2835 | 2638698.6137 | 1129525.8421
100 | 2638689.771 | 1129489.3007 | 2638688.6087 | 1129488.01
101 | 2638772.8488 | 1129547.5375 | 2638769.9513 | 1129545.9645 | 2638763.7649 | 1129542.7576
102 | 2638772.8488 | 1129547.5375 | 2638777.2343 | 1129549.9184
103 | 2638798.0339 | 1129560.8172 | 2638794.7152 | 1129559.2632 | 2638786.57 | 1129554.9867 | 2638777.2343 | 1129549.9184
104 | 2638804.0307 | 1129563.6252 | 2638798.0339 | 1129560.8172
105 | 2638804.0307 | 1129563.6252 | 2638797.8864 | 1129571.7073
106 | 2638804.0307 | 1129563.6252 | 2638809.0091 | 1129565.647
107 | 2638784.4134 | 1129578.985 | 2638793.8542 | 1129577.0112 | 2638797.8864 | 1129571.7073
108 | 2638830.4259 | 1129556.7465 | 2638829.3341 | 1129557.64 | 2638825.5655 | 1129557.9382 | 2638820.4015 | 1129565.6423 | 2638809.0091 | 1129565.647
109 | 2638686.3775 | 1129485.5325 | 2638673.8792 | 1129478.9715
110 | 2638686.3775 | 1129485.5325 | 2638688.6087 | 1129488.01
111 | 2638661.8877 | 1129468.4667 | 2638673.8792 | 1129478.9715
112 | 2638602.2818 | 1129593.039 | 2638603.2043 | 1129593.8341 | 2638619.1409 | 1129603.7051
113 | 2638627.9444 | 1129609.4868 | 2638624.9478 | 1129607.3019 | 2638619.1409 | 1129603.7051
114 | 2638627.9444 | 1129609.4868 | 2638629.2694 | 1129610.4529
115 | 2638649.9422 | 1129625.5262 | 2638629.2694 | 1129610.4529
116 | 2638649.9422 | 1129625.5262 | 2638677.2771 | 1129650.6234
117 | 2638750.3925 | 1129577.9808 | 2638735.3 | 1129579.1039 | 2638729.7801 | 1129577.87
118 | 2638750.3925 | 1129577.9808 | 2638772.4372 | 1129576.3403 | 2638775.6965 | 1129577.06
119 | 2638714.4718 | 1129574.3015 | 2638719.3782 | 1129575.5447 | 2638729.7801 | 1129577.87
120 | 2638784.4134 | 1129578.985 | 2638775.6965 | 1129577.06
121 | 2638714.4718 | 1129574.3015 | 2638712.9877 | 1129565.4765 | 2638710.2687 | 1129557.8135
122 | 2638707.9912 | 1129551.3947 | 2638710.2687 | 1129557.8135
123 | 2638707.9912 | 1129551.3947 | 2638707.8782 | 1129551.0761
124 | 2638680.0807 | 1129653.1975 | 2638677.2771 | 1129650.6234
125 | 2638703.9389 | 1129671.1277 | 2638696.5806 | 1129666.6673 | 2638686.033 | 1129658.6624 | 2638680.0807 | 1129653.1975
126 | 2638830.4259 | 1129556.7465 | 2638837.8803 | 1129545.044
127 | 2638837.8803 | 1129545.044 | 2638818.0532 | 1129532.0278
128 | 2638811.8641 | 1129524.4284 | 2638817.9064 | 1129531.9314 | 2638818.0532 | 1129532.0278
129 | 2638807.7491 | 1129519.3186 | 2638811.8641 | 1129524.4284
130 | 2638703.9389 | 1129671.1277 | 2638708.46 | 1129669.9671 | 2638712.1312 | 1129668.7208
131 | 2638727.1934 | 1129666.1262 | 2638714.952 | 1129667.7631 | 2638712.1312 | 1129668.7208

## bus_geodata
| x | y | coords
0 | 2638796.9805 | 1129431.043
1 | 2638785.2132 | 1129401.3668
2 | 2638793.458 | 1129477.8361
3 | 2638755.6842 | 1129381.4787
4 | 2638747.4558 | 1129346.1828
5 | 2638751.6012 | 1129404.5731
6 | 2638719.6576 | 1129360.9711
7 | 2638710.2094 | 1129355.7167
8 | 2638718.6044 | 1129375.0826
9 | 2638710.141 | 1129316.9546
10 | 2638743.5402 | 1129420.6097
11 | 2638737.4927 | 1129408.8661
12 | 2638738.8233 | 1129411.4499
13 | 2638724.1901 | 1129384.0549
14 | 2638750.5274 | 1129437.3518
15 | 2638737.4047 | 1129444.6341
16 | 2638761.28 | 1129460.0667
17 | 2638767.6239 | 1129473.5719
18 | 2638731.1396 | 1129448.1109
19 | 2638696.2301 | 1129351.5879
20 | 2638638.3577 | 1129181.467
21 | 2638735.1974 | 1129472.427
22 | 2638735.8671 | 1129475.494
23 | 2638728.2921 | 1129475.876
24 | 2638742.8229 | 1129493.4377
25 | 2638771.6599 | 1129486.0896
26 | 2638757.3691 | 1129494.5698
27 | 2638780.7037 | 1129496.6064
28 | 2638749.4321 | 1129500.0005
29 | 2638746.5857 | 1129501.9481
30 | 2638800.911 | 1129513.2261
31 | 2638804.5789 | 1129515.382
32 | 2638828.218 | 1129081.0135
33 | 2638835.7803 | 1129080.6414
34 | 2638718.653 | 1129493.002
35 | 2638712.4838 | 1129497.7444
36 | 2638619.6589 | 1129555.5362
37 | 2638631.1816 | 1129559.8954
38 | 2638618.7178 | 1129555.1802
39 | 2638649.0999 | 1129563.2448
40 | 2638607.3571 | 1129556.3849
41 | 2638611.9232 | 1129540.8184
42 | 2638652.1673 | 1129554.2953
43 | 2638664.3945 | 1129568.1695
44 | 2638593.3681 | 1129585.356
45 | 2638604.7586 | 1129529.5751
46 | 2638646.2179 | 1129534.2142
47 | 2638577.5852 | 1129563.2944
48 | 2638596.6043 | 1129588.1453
49 | 2638598.3052 | 1129523.2812
50 | 2638606.7308 | 1129334.069
51 | 2638581.2792 | 1129410.5469
52 | 2638598.1713 | 1129415.7482
53 | 2638561.177 | 1129401.7627
54 | 2638518.175 | 1129277.9085
55 | 2638476.8806 | 1129346.649
56 | 2638475.2419 | 1129345.8357
57 | 2638486.5493 | 1129354.7913
58 | 2638582.4421 | 1129440.5504
59 | 2638588.8889 | 1129463.2246
60 | 2638603.306 | 1129418.546
61 | 2638581.4544 | 1129507.674
62 | 2638609.1953 | 1129422.7079
63 | 2638597.3908 | 1129522.4505
64 | 2638564.242 | 1129493.9103
65 | 2638611.2089 | 1129424.129
66 | 2638622.0643 | 1129423.5415
67 | 2638557.9718 | 1129485.402
68 | 2638636.9601 | 1129428.3381
69 | 2638741.6442 | 1129518.2136
70 | 2638756.465 | 1129533.2564
71 | 2638734.5854 | 1129525.8946
72 | 2638757.8135 | 1129539.6725
73 | 2638737.9606 | 1129528.647
74 | 2638723.4176 | 1129516.9547
75 | 2638488.0648 | 1129356.051
76 | 2638507.2557 | 1129365.7769
77 | 2638461.8206 | 1129340.6725
78 | 2638549.578 | 1129477.379
79 | 2638569.5526 | 1129539.2475
80 | 2638556.5628 | 1129541.4724
81 | 2638571.8909 | 1129552.8219
82 | 2638533.8335 | 1129464.4146
83 | 2638512.5864 | 1129452.6916
84 | 2638517.4129 | 1129404.9501
85 | 2638504.1395 | 1129388.1212
86 | 2638454.9022 | 1129331.7058
87 | 2638658.8032 | 1129442.2736
88 | 2638669.2631 | 1129455.1772
89 | 2638670.1005 | 1129456.4884
90 | 2638648.7775 | 1129456.9818
91 | 2638659.9021 | 1129466.7272
92 | 2638436.4033 | 1129420.5447
93 | 2638499.4565 | 1129445.4472
94 | 2638703.5561 | 1129504.6075
95 | 2638698.5568 | 1129520.2835
96 | 2638689.771 | 1129489.3007
97 | 2638772.8488 | 1129547.5375
98 | 2638763.7649 | 1129542.7576
99 | 2638777.2343 | 1129549.9184
100 | 2638798.0339 | 1129560.8172
101 | 2638804.0307 | 1129563.6252
102 | 2638797.8864 | 1129571.7073
103 | 2638809.0091 | 1129565.647
104 | 2638686.3775 | 1129485.5325
105 | 2638673.8792 | 1129478.9715
106 | 2638688.6087 | 1129488.01
107 | 2638661.8877 | 1129468.4667
108 | 2638698.6137 | 1129525.8421
109 | 2638602.2818 | 1129593.039
110 | 2638619.1409 | 1129603.7051
111 | 2638627.9444 | 1129609.4868
112 | 2638629.2694 | 1129610.4529
113 | 2638649.9422 | 1129625.5262
114 | 2638750.3925 | 1129577.9808
115 | 2638729.7801 | 1129577.87
116 | 2638775.6965 | 1129577.06
117 | 2638714.4718 | 1129574.3015
118 | 2638784.4134 | 1129578.985
119 | 2638710.2687 | 1129557.8135
120 | 2638707.9912 | 1129551.3947
121 | 2638677.2771 | 1129650.6234
122 | 2638680.0807 | 1129653.1975
123 | 2638830.4259 | 1129556.7465
124 | 2638837.8803 | 1129545.044
125 | 2638818.0532 | 1129532.0278
126 | 2638807.7491 | 1129519.3186
127 | 2638811.8641 | 1129524.4284
128 | 2638707.8782 | 1129551.0761
129 | 2638703.9389 | 1129671.1277
130 | 2638644.2202 | 1129531.2975
131 | 2638712.1312 | 1129668.7208
132 | 2638727.1934 | 1129666.1262
133 | 2638703.5561 | 1129504.6075

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.97886 | -0.40764 | 0.023082 | 0.005785
1 | 0.97989 | -0.38749 | 0 | 0
2 | 0.97839 | -0.41685 | 0.0086632 | 0.0021712
3 | 0.98094 | -0.36696 | 0 | 0
4 | 0.98058 | -0.374 | 0.0038739 | 0.0009709
5 | 0.98193 | -0.34758 | 0.0039451 | 0.00098873
6 | 0.98126 | -0.36078 | 0 | 0
7 | 0.98113 | -0.36329 | 0.0059221 | 0.0014842
8 | 0.98142 | -0.35747 | 0.0073998 | 0.0018546
9 | 0.98031 | -0.37927 | 0 | 0
10 | 0.98269 | -0.33264 | 0 | 0
11 | 0.98231 | -0.34021 | 0.0021638 | 0.00054229
12 | 0.98238 | -0.33871 | 0.0041718 | 0.0010456
13 | 0.98162 | -0.3536 | 0.0060873 | 0.0015256
14 | 0.98401 | -0.30706 | 0 | 0
15 | 0.98509 | -0.28595 | 0.0078524 | 0.001968
16 | 0.99028 | -0.18581 | 0.0022337 | 0.00055982
17 | 0.99031 | -0.18521 | 0.0045916 | 0.0011508
18 | 0.98566 | -0.27487 | 0.0053556 | 0.0013422
19 | 0.98103 | -0.36513 | 0.0069005 | 0.0017294
20 | 0.97946 | -0.39603 | 0.0022542 | 0.00056495
21 | 0.98775 | -0.23449 | 0 | 0
22 | 0.98802 | -0.22917 | 0.0054468 | 0.0013651
23 | 0.98772 | -0.23494 | 0.0033083 | 0.00082915
24 | 0.98981 | -0.19468 | 0.0026878 | 0.00067363
25 | 0.99039 | -0.18362 | 0 | 0
26 | 0.99055 | -0.18059 | 0.0017142 | 0.00042962
27 | 0.99035 | -0.18446 | 0.003418 | 0.00085664
28 | 0.99065 | -0.17855 | 0.0024917 | 0.00062448
29 | 0.9907 | -0.17766 | 0 | 0
30 | 0.98769 | -0.23636 | 0.0021308 | 0.00053403
31 | 0.9877 | -0.23619 | 0 | 0
32 | 0.97871 | -0.41071 | 0 | 0
33 | 0.97868 | -0.41123 | 0.0037561 | 0.00094137
34 | 0.99734 | -0.050584 | 0.0032605 | 0.00081715
35 | 0.99736 | -0.050139 | 0.0059577 | 0.0014931
36 | 0.97844 | -0.41524 | 0.002152 | 0.00053935
37 | 0.97828 | -0.41838 | 0.0021246 | 0.00053247
38 | 0.97845 | -0.41495 | 0 | 0
39 | 0.97807 | -0.42254 | 0.0014474 | 0.00036276
40 | 0.97817 | -0.42048 | 0.0017162 | 0.00043011
41 | 0.97904 | -0.40347 | 0.0022518 | 0.00056435
42 | 0.97799 | -0.42409 | 0.0026763 | 0.00067074
43 | 0.97805 | -0.42296 | 0.0014478 | 0.00036286
44 | 0.9775 | -0.4337 | 0 | 0
45 | 0.97956 | -0.3933 | 0.0022347 | 0.00056006
46 | 0.97786 | -0.4266 | 0.0033543 | 0.00084067
47 | 0.97734 | -0.43682 | 0.0024103 | 0.00060409
48 | 0.97744 | -0.4349 | 0.0010264 | 0.00025724
49 | 0.97993 | -0.38604 | 0.0027374 | 0.00068605
50 | 0.9874 | -0.24097 | 0.0032929 | 0.00082527
51 | 0.98764 | -0.23623 | 0.0036235 | 0.00090814
52 | 0.98801 | -0.2291 | 0.0047456 | 0.0011894
53 | 0.98732 | -0.24241 | 0.0027505 | 0.00068933
54 | 0.9861 | -0.26621 | 0.0015349 | 0.00038469
55 | 0.98622 | -0.26401 | 0.0011587 | 0.00029039
56 | 0.98621 | -0.2642 | 0.0013283 | 0.0003329
57 | 0.98632 | -0.26205 | 0.0014685 | 0.00036803
58 | 0.98538 | -0.27993 | 0.0036137 | 0.00090569
59 | 0.9839 | -0.30864 | 0.003101 | 0.00077717
60 | 0.98815 | -0.22625 | 0 | 0
61 | 0.98098 | -0.36547 | 0 | 0
62 | 0.98881 | -0.21361 | 0 | 0
63 | 0.97998 | -0.38499 | 0.0026267 | 0.00065831
64 | 0.98067 | -0.37149 | 0.0037973 | 0.00095168
65 | 0.9888 | -0.21384 | 0.0053843 | 0.0013494
66 | 0.99005 | -0.18976 | 0.0037705 | 0.00094499
67 | 0.98056 | -0.37364 | 0 | 0
68 | 0.99161 | -0.15974 | 0.0022693 | 0.00056873
69 | 0.99311 | -0.13138 | 0 | 0
70 | 0.99169 | -0.15879 | 0.003958 | 0.00099197
71 | 0.99402 | -0.11387 | 0 | 0
72 | 0.99117 | -0.16886 | 0 | 0
73 | 0.994 | -0.11428 | 0.0054405 | 0.0013635
74 | 0.99531 | -0.089174 | 0.0028989 | 0.00072653
75 | 0.98633 | -0.2617 | 0.001218 | 0.00030527
76 | 0.98656 | -0.2573 | 0.0015018 | 0.00037637
77 | 0.98614 | -0.26539 | 0 | 0
78 | 0.98044 | -0.37599 | 0.0024765 | 0.00062067
79 | 0.97727 | -0.43823 | 0 | 0
80 | 0.97724 | -0.43875 | 0.002146 | 0.00053783
81 | 0.9773 | -0.43767 | 0.0017592 | 0.00044091
82 | 0.98028 | -0.37924 | 0.0030042 | 0.00075291
83 | 0.98015 | -0.38175 | 0.0025468 | 0.00063828
84 | 0.98589 | -0.27031 | 0.0031827 | 0.00079765
85 | 0.98595 | -0.26909 | 0 | 0
86 | 0.98613 | -0.26568 | 0.0014127 | 0.00035407
87 | 0.99426 | -0.10908 | 0.0045023 | 0.0011284
88 | 0.99604 | -0.075115 | 0.0056064 | 0.0014051
89 | 0.99621 | -0.071835 | 0.0028788 | 0.0007215
90 | 0.99944 | -0.010758 | 0.0039573 | 0.0009918
91 | 0.99949 | -0.009737 | 0.0049385 | 0.0012377
92 | 0.98002 | -0.38431 | 0.0013747 | 0.00034454
93 | 0.98011 | -0.38261 | 0.0017872 | 0.00044791
94 | 0.99746 | -0.048321 | 0 | 0
95 | 0.99735 | -0.05029 | 0.0027506 | 0.00068938
96 | 0.99949 | -0.0096344 | 0.00097963 | 0.00024552
97 | 0.99017 | -0.18809 | 0.0022564 | 0.00056551
98 | 0.99074 | -0.17708 | 0.0088237 | 0.0022114
99 | 0.98991 | -0.19324 | 0.0082421 | 0.0020657
100 | 0.98883 | -0.21407 | 0.0058865 | 0.0014753
101 | 0.98857 | -0.21926 | 0 | 0
102 | 0.98829 | -0.22456 | 0.00593 | 0.0014862
103 | 0.98849 | -0.22066 | 0.0030708 | 0.0007696
104 | 1 | 0 | -0.36817 | -0.093627
105 | 0.99974 | -0.0049439 | 0.0043253 | 0.001084
106 | 0.99966 | -0.0063648 | 0.0031551 | 0.00079075
107 | 0.99951 | -0.0093272 | 0.006867 | 0.001721
108 | 0.99733 | -0.050688 | 0.0040809 | 0.0010228
109 | 0.97734 | -0.43689 | 0.0034001 | 0.00085214
110 | 0.97713 | -0.44092 | 0.0014293 | 0.00035823
111 | 0.97704 | -0.44278 | 0.0014032 | 0.00035168
112 | 0.97703 | -0.44303 | 0.0014788 | 0.00037061
113 | 0.97686 | -0.44619 | 0 | 0
114 | 0.98733 | -0.24333 | 0.00462 | 0.0011579
115 | 0.98707 | -0.24836 | 0.0030684 | 0.00076902
116 | 0.98775 | -0.23507 | 0.0051698 | 0.0012957
117 | 0.98692 | -0.25131 | 0 | 0
118 | 0.98794 | -0.23135 | 0 | 0
119 | 0.98675 | -0.25451 | 0.0041434 | 0.0010384
120 | 0.98672 | -0.25528 | 0.0023185 | 0.00058108
121 | 0.97663 | -0.45078 | 0.00088935 | 0.00022289
122 | 0.97661 | -0.45119 | 0.0027986 | 0.0007014
123 | 0.98822 | -0.22601 | 0 | 0
124 | 0.98807 | -0.22889 | 0 | 0
125 | 0.98782 | -0.2338 | 0.0026127 | 0.00065481
126 | 0.98771 | -0.236 | 0.0032431 | 0.0008128
127 | 0.98774 | -0.23537 | 0.0036088 | 0.00090446
128 | 0.98671 | -0.2553 | 0.0040075 | 0.0010044
129 | 0.97653 | -0.45287 | 0 | 0
130 | 0.97785 | -0.42679 | 0.0029489 | 0.00073905
131 | 0.9765 | -0.45335 | 0.0023798 | 0.00059645
132 | 0.97649 | -0.45355 | 0.00069917 | 0.00017523
133 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | -0.031749 | -0.0079579 | 0.03178 | 0.007977 | 3.0512e-05 | 1.9088e-05 | 0.048264 | 0.048264 | 0.048264 | 0.97886 | -0.40764 | 0.97989 | -0.38749 | 13.2593
1 | 0.008667 | 0.0021729 | -0.0086632 | -0.0021712 | 3.8044e-06 | 1.7005e-06 | 0.013175 | 0.013176 | 0.013176 | 0.97886 | -0.40764 | 0.97839 | -0.41685 | 3.6197
2 | -0.03178 | -0.007977 | 0.031811 | 0.0079964 | 3.1143e-05 | 1.9482e-05 | 0.048264 | 0.048264 | 0.048264 | 0.97989 | -0.38749 | 0.98094 | -0.36696 | 13.2593
3 | 0.0098966 | 0.0024793 | -0.0098933 | -0.0024777 | 3.3152e-06 | 1.6267e-06 | 0.015012 | 0.015012 | 0.015012 | 0.98094 | -0.36696 | 0.98058 | -0.374 | 4.1242
4 | -0.041708 | -0.010476 | 0.041746 | 0.0105 | 3.8605e-05 | 2.4382e-05 | 0.063276 | 0.063276 | 0.063276 | 0.98094 | -0.36696 | 0.98193 | -0.34758 | 17.3835
5 | 0.0060193 | 0.0015068 | -0.0060178 | -0.0015064 | 1.5116e-06 | 3.5807e-07 | 0.0091336 | 0.0091338 | 0.0091338 | 0.98058 | -0.374 | 0.98031 | -0.37927 | 2.5093
6 | -0.045691 | -0.011489 | 0.045724 | 0.01151 | 3.2634e-05 | 2.0656e-05 | 0.069254 | 0.069254 | 0.069254 | 0.98193 | -0.34758 | 0.98269 | -0.33264 | 19.0258
7 | 0.012825 | 0.0032147 | -0.012823 | -0.0032139 | 1.5334e-06 | 8.4484e-07 | 0.019448 | 0.019448 | 0.019448 | 0.98126 | -0.36078 | 0.98113 | -0.36329 | 5.3429
8 | -0.012825 | -0.0032147 | 0.012827 | 0.0032158 | 2.0252e-06 | 1.1157e-06 | 0.019448 | 0.019448 | 0.019448 | 0.98126 | -0.36078 | 0.98142 | -0.35747 | 5.3429
9 | 0.0069011 | 0.0017296 | -0.0069005 | -0.0017294 | 6.036e-07 | 2.0077e-07 | 0.010467 | 0.010467 | 0.010467 | 0.98113 | -0.36329 | 0.98103 | -0.36513 | 2.8754
10 | -0.020227 | -0.0050704 | 0.02023 | 0.0050726 | 3.7276e-06 | 2.2521e-06 | 0.030668 | 0.030668 | 0.030668 | 0.98142 | -0.35747 | 0.98162 | -0.3536 | 8.4252
11 | 0.0060178 | 0.0015064 | -0.006013 | -0.0015053 | 4.7972e-06 | 1.1388e-06 | 0.0091338 | 0.0091345 | 0.0091345 | 0.98031 | -0.37927 | 0.97946 | -0.39603 | 2.5095
12 | -0.078405 | -0.019713 | 0.078501 | 0.019774 | 9.5909e-05 | 6.1151e-05 | 0.11875 | 0.11875 | 0.11875 | 0.98269 | -0.33264 | 0.98401 | -0.30706 | 32.6225
13 | 0.032682 | 0.0082037 | -0.032672 | -0.0081978 | 9.4637e-06 | 5.9263e-06 | 0.049492 | 0.049492 | 0.049492 | 0.98269 | -0.33264 | 0.98238 | -0.33871 | 13.5967
14 | -0.028498 | -0.007151 | 0.0285 | 0.0071522 | 2.0314e-06 | 1.2633e-06 | 0.043173 | 0.043173 | 0.043173 | 0.98231 | -0.34021 | 0.98238 | -0.33871 | 11.8607
15 | 0.026335 | 0.0066087 | -0.026318 | -0.0065983 | 1.6807e-05 | 1.04e-05 | 0.039895 | 0.039895 | 0.039895 | 0.98231 | -0.34021 | 0.98162 | -0.3536 | 10.9602
16 | -0.078501 | -0.019774 | 0.078581 | 0.019825 | 7.9357e-05 | 5.0598e-05 | 0.11875 | 0.11875 | 0.11875 | 0.98401 | -0.30706 | 0.98509 | -0.28595 | 32.6225
17 | -0.086433 | -0.021793 | 0.086479 | 0.021822 | 4.5835e-05 | 2.9243e-05 | 0.13061 | 0.13061 | 0.13061 | 0.98509 | -0.28595 | 0.98566 | -0.27487 | 35.881
18 | -0.0022337 | -0.00055982 | 0.0022338 | 0.00055967 | 6.308e-08 | -1.5174e-07 | 0.0033564 | 0.0033563 | 0.0033564 | 0.99028 | -0.18581 | 0.99031 | -0.18521 | 0.92209
19 | -0.0068253 | -0.0017104 | 0.0068259 | 0.0017106 | 5.1932e-07 | 1.6294e-07 | 0.010256 | 0.010256 | 0.010256 | 0.99031 | -0.18521 | 0.99039 | -0.18362 | 2.8175
20 | -0.091835 | -0.023164 | 0.092012 | 0.023278 | 0.00017793 | 0.00011356 | 0.13869 | 0.13869 | 0.13869 | 0.98566 | -0.27487 | 0.98775 | -0.23449 | 38.1022
21 | 0.0037588 | 0.00094031 | -0.0037562 | -0.00094133 | 2.6266e-06 | -1.0203e-06 | 0.0057099 | 0.0057108 | 0.0057108 | 0.97946 | -0.39603 | 0.97871 | -0.41071 | 1.5689
22 | -0.095321 | -0.024107 | 0.095345 | 0.024123 | 2.4301e-05 | 1.5513e-05 | 0.14368 | 0.14368 | 0.14368 | 0.98775 | -0.23449 | 0.98802 | -0.22917 | 39.4714
23 | 0.0033084 | 0.00082909 | -0.0033083 | -0.00082915 | 7.1901e-08 | -5.2779e-08 | 0.004984 | 0.004984 | 0.004984 | 0.98775 | -0.23449 | 0.98772 | -0.23494 | 1.3692
24 | -0.10079 | -0.025488 | 0.10096 | 0.025594 | 0.00016707 | 0.00010668 | 0.15188 | 0.15188 | 0.15188 | 0.98802 | -0.22917 | 0.98981 | -0.19468 | 41.725
25 | -0.10365 | -0.026268 | 0.10373 | 0.026322 | 8.4832e-05 | 5.4173e-05 | 0.15592 | 0.15592 | 0.15592 | 0.98981 | -0.19468 | 0.9907 | -0.17766 | 42.8351
26 | -0.010244 | -0.0025671 | 0.010246 | 0.0025679 | 1.4768e-06 | 7.312e-07 | 0.015391 | 0.015391 | 0.015391 | 0.99039 | -0.18362 | 0.99055 | -0.18059 | 4.2283
27 | 0.0034182 | 0.00085655 | -0.003418 | -0.00085664 | 1.3802e-07 | -9.1229e-08 | 0.0051356 | 0.0051357 | 0.0051357 | 0.99039 | -0.18362 | 0.99035 | -0.18446 | 1.4109
28 | -0.01196 | -0.0029975 | 0.011961 | 0.0029981 | 1.1641e-06 | 6.2121e-07 | 0.017966 | 0.017966 | 0.017966 | 0.99055 | -0.18059 | 0.99065 | -0.17855 | 4.9358
29 | -0.014453 | -0.0036226 | 0.014453 | 0.0036229 | 6.0952e-07 | 3.4568e-07 | 0.021709 | 0.021709 | 0.021709 | 0.99065 | -0.17855 | 0.9907 | -0.17766 | 5.964
30 | -0.11818 | -0.029945 | 0.11845 | 0.030113 | 0.00026339 | 0.00016828 | 0.17763 | 0.17763 | 0.17763 | 0.9907 | -0.17766 | 0.99311 | -0.13138 | 48.799
31 | -0.0021308 | -0.00053403 | 0.0021308 | 0.00053399 | 1.6442e-08 | -4.3929e-08 | 0.0032102 | 0.0032102 | 0.0032102 | 0.98769 | -0.23636 | 0.9877 | -0.23619 | 0.88193
32 | -0.0021308 | -0.00053399 | 0.0021309 | 0.00053394 | 1.9532e-08 | -5.2188e-08 | 0.0032102 | 0.0032102 | 0.0032102 | 0.9877 | -0.23619 | 0.98771 | -0.236 | 0.88192
33 | 0.0037562 | 0.00094133 | -0.0037561 | -0.00094137 | 9.3124e-08 | -3.6083e-08 | 0.0057108 | 0.0057109 | 0.0057109 | 0.97871 | -0.41071 | 0.97868 | -0.41123 | 1.5689
34 | -0.0032605 | -0.00081715 | 0.0032605 | 0.00081709 | 6.9051e-08 | -5.7353e-08 | 0.0048646 | 0.0048645 | 0.0048646 | 0.99734 | -0.050584 | 0.99736 | -0.050139 | 1.3364
35 | -0.0092182 | -0.0023102 | 0.009219 | 0.0023106 | 7.9874e-07 | 3.6423e-07 | 0.013753 | 0.013753 | 0.013753 | 0.99736 | -0.050139 | 0.99746 | -0.048321 | 3.7783
36 | 0.014005 | 0.0035113 | -0.014003 | -0.0035101 | 2.096e-06 | 1.1867e-06 | 0.0213 | 0.0213 | 0.0213 | 0.97844 | -0.41524 | 0.97828 | -0.41838 | 5.8516
37 | -0.016157 | -0.0040507 | 0.016158 | 0.0040508 | 2.2781e-07 | 1.3316e-07 | 0.024573 | 0.024573 | 0.024573 | 0.97844 | -0.41524 | 0.97845 | -0.41495 | 6.7507
38 | 0.011879 | 0.0029777 | -0.011876 | -0.0029764 | 2.3515e-06 | 1.2639e-06 | 0.018068 | 0.018068 | 0.018068 | 0.97828 | -0.41838 | 0.97807 | -0.42254 | 4.9638
39 | 0.023566 | 0.0059142 | -0.02356 | -0.0059104 | 6.221e-06 | 3.8193e-06 | 0.035842 | 0.035842 | 0.035842 | 0.97845 | -0.41495 | 0.97817 | -0.42048 | 9.8466
40 | -0.039723 | -0.009965 | 0.039745 | 0.0099787 | 2.1746e-05 | 1.3718e-05 | 0.060414 | 0.060414 | 0.060414 | 0.97845 | -0.41495 | 0.97904 | -0.40347 | 16.5973
41 | 0.0089809 | 0.002251 | -0.0089802 | -0.0022506 | 6.6283e-07 | 3.054e-07 | 0.013663 | 0.013663 | 0.013663 | 0.97807 | -0.42254 | 0.97799 | -0.42409 | 3.7537
42 | 0.0014479 | 0.00036268 | -0.0014478 | -0.00036286 | 2.9367e-08 | -1.8376e-07 | 0.0022027 | 0.0022028 | 0.0022028 | 0.97807 | -0.42254 | 0.97805 | -0.42296 | 0.60515
43 | 0.021844 | 0.0054803 | -0.02183 | -0.0054719 | 1.3751e-05 | 8.3842e-06 | 0.033231 | 0.033231 | 0.033231 | 0.97817 | -0.42048 | 0.9775 | -0.4337 | 9.1294
44 | -0.041997 | -0.010543 | 0.042017 | 0.010556 | 2.0374e-05 | 1.2871e-05 | 0.063836 | 0.063836 | 0.063836 | 0.97904 | -0.40347 | 0.97956 | -0.3933 | 17.5375
45 | 0.006304 | 0.0015799 | -0.0063032 | -0.0015797 | 7.5477e-07 | 2.0856e-07 | 0.0095915 | 0.0095916 | 0.0095916 | 0.97799 | -0.42409 | 0.97786 | -0.4266 | 2.6351
46 | 0.0063168 | 0.0015828 | -0.0063158 | -0.0015825 | 9.4067e-07 | 2.62e-07 | 0.0096157 | 0.0096158 | 0.0096158 | 0.9775 | -0.4337 | 0.97734 | -0.43682 | 2.6417
47 | 0.015513 | 0.0038891 | -0.015512 | -0.0038886 | 8.935e-07 | 5.1828e-07 | 0.023615 | 0.023616 | 0.023616 | 0.9775 | -0.4337 | 0.97744 | -0.4349 | 6.4878
48 | -0.044252 | -0.011116 | 0.044267 | 0.011126 | 1.5342e-05 | 9.705e-06 | 0.067231 | 0.067231 | 0.067231 | 0.97956 | -0.3933 | 0.97993 | -0.38604 | 18.4701
49 | 0.0029489 | 0.00073903 | -0.0029489 | -0.00073905 | 2.6695e-08 | -2.7264e-08 | 0.0044873 | 0.0044873 | 0.0044873 | 0.97786 | -0.4266 | 0.97785 | -0.42679 | 1.2328
50 | 0.0039055 | 0.00097842 | -0.0039053 | -0.00097847 | 1.5805e-07 | -4.8226e-08 | 0.005946 | 0.0059461 | 0.0059461 | 0.97734 | -0.43682 | 0.9773 | -0.43767 | 1.6335
51 | 0.014486 | 0.0036314 | -0.014484 | -0.0036306 | 1.367e-06 | 7.8093e-07 | 0.022053 | 0.022053 | 0.022053 | 0.97744 | -0.4349 | 0.97734 | -0.43689 | 6.0585
52 | -0.047005 | -0.011812 | 0.047007 | 0.011813 | 2.361e-06 | 1.4954e-06 | 0.071388 | 0.071388 | 0.071388 | 0.97993 | -0.38604 | 0.97998 | -0.38499 | 19.612
53 | -0.0032929 | -0.00082527 | 0.0032936 | 0.00082471 | 7.4425e-07 | -5.5489e-07 | 0.0049624 | 0.004962 | 0.0049624 | 0.9874 | -0.24097 | 0.98764 | -0.23623 | 1.3633
54 | -0.022491 | -0.0056392 | 0.022499 | 0.0056439 | 7.6481e-06 | 4.6674e-06 | 0.033887 | 0.033887 | 0.033887 | 0.98764 | -0.23623 | 0.98801 | -0.2291 | 9.3097
55 | 0.015574 | 0.0039063 | -0.01557 | -0.0039037 | 4.5889e-06 | 2.6526e-06 | 0.023466 | 0.023466 | 0.023466 | 0.98764 | -0.23623 | 0.98732 | -0.24241 | 6.4467
56 | -0.027245 | -0.0068332 | 0.027248 | 0.0068355 | 3.6923e-06 | 2.2882e-06 | 0.041034 | 0.041034 | 0.041034 | 0.98801 | -0.2291 | 0.98815 | -0.22625 | 11.2732
57 | 0.012819 | 0.0032144 | -0.01281 | -0.0032094 | 9.0886e-06 | 4.987e-06 | 0.019321 | 0.019321 | 0.019321 | 0.98732 | -0.24241 | 0.98656 | -0.2573 | 5.308
58 | -0.0015349 | -0.00038469 | 0.0015351 | 0.00038377 | 1.613e-07 | -9.1989e-07 | 0.0023162 | 0.0023158 | 0.0023162 | 0.9861 | -0.26621 | 0.98622 | -0.26401 | 0.63632
59 | 0.0059248 | 0.0014839 | -0.0059247 | -0.0014838 | 5.4817e-08 | 1.174e-08 | 0.008939 | 0.0089391 | 0.0089391 | 0.98622 | -0.26401 | 0.98621 | -0.2642 | 2.4558
60 | -0.0086186 | -0.002158 | 0.0086194 | 0.0021584 | 8.0148e-07 | 3.5163e-07 | 0.013003 | 0.013003 | 0.013003 | 0.98622 | -0.26401 | 0.98632 | -0.26205 | 3.5723
61 | 0.0045965 | 0.0011509 | -0.0045962 | -0.001151 | 2.6062e-07 | -1.7581e-08 | 0.0069349 | 0.006935 | 0.006935 | 0.98621 | -0.2642 | 0.98614 | -0.26539 | 1.9052
62 | -0.010088 | -0.0025264 | 0.010088 | 0.0025265 | 1.7116e-07 | 8.4391e-08 | 0.015218 | 0.015218 | 0.015218 | 0.98632 | -0.26205 | 0.98633 | -0.2617 | 4.1809
63 | 0.068046 | 0.017209 | -0.067953 | -0.01715 | 9.3582e-05 | 5.9593e-05 | 0.10281 | 0.10281 | 0.10281 | 0.98538 | -0.27993 | 0.9839 | -0.30864 | 28.2452
64 | -0.07166 | -0.018115 | 0.071845 | 0.018233 | 0.00018497 | 0.00011784 | 0.10827 | 0.10827 | 0.10827 | 0.98538 | -0.27993 | 0.98815 | -0.22625 | 29.7443
65 | 0.064852 | 0.016373 | -0.064676 | -0.01626 | 0.00017603 | 0.00011204 | 0.098123 | 0.098123 | 0.098123 | 0.9839 | -0.30864 | 0.98098 | -0.36547 | 26.9568
66 | -0.099093 | -0.025068 | 0.099154 | 0.025107 | 6.017e-05 | 3.8417e-05 | 0.1493 | 0.1493 | 0.1493 | 0.98815 | -0.22625 | 0.98881 | -0.21361 | 41.0174
67 | 0.04968 | 0.012501 | -0.049634 | -0.012472 | 4.6304e-05 | 2.936e-05 | 0.075376 | 0.075376 | 0.075376 | 0.98098 | -0.36547 | 0.97998 | -0.38499 | 20.7077
68 | 0.014996 | 0.0037596 | -0.014991 | -0.0037571 | 4.3049e-06 | 2.4751e-06 | 0.022747 | 0.022747 | 0.022747 | 0.98098 | -0.36547 | 0.98067 | -0.37149 | 6.2491
69 | 0.0053844 | 0.0013494 | -0.0053843 | -0.0013494 | 6.0678e-08 | 7.2204e-09 | 0.0081027 | 0.0081027 | 0.0081027 | 0.98881 | -0.21361 | 0.9888 | -0.21384 | 2.226
70 | -0.10454 | -0.026456 | 0.10466 | 0.026533 | 0.00011982 | 7.6519e-05 | 0.15741 | 0.15741 | 0.15741 | 0.98881 | -0.21361 | 0.99005 | -0.18976 | 43.2434
71 | 0.011194 | 0.0028054 | -0.011193 | -0.0028048 | 1.1434e-06 | 5.9846e-07 | 0.016985 | 0.016985 | 0.016985 | 0.98067 | -0.37149 | 0.98056 | -0.37364 | 4.6663
72 | -0.10843 | -0.027478 | 0.10858 | 0.027578 | 0.00015659 | 0.00010002 | 0.16307 | 0.16307 | 0.16307 | 0.99005 | -0.18976 | 0.99161 | -0.15974 | 44.8003
73 | 0.011193 | 0.0028048 | -0.011192 | -0.0028042 | 1.2562e-06 | 6.5752e-07 | 0.016985 | 0.016985 | 0.016985 | 0.98056 | -0.37364 | 0.98044 | -0.37599 | 4.6663
74 | -0.11085 | -0.028146 | 0.11113 | 0.02832 | 0.00027099 | 0.0001731 | 0.16648 | 0.16648 | 0.16648 | 0.99161 | -0.15974 | 0.99426 | -0.10908 | 45.7358
75 | 0.073396 | 0.01851 | -0.0733 | -0.018449 | 9.6148e-05 | 6.1261e-05 | 0.11001 | 0.11001 | 0.11001 | 0.99311 | -0.13138 | 0.99169 | -0.15879 | 30.2234
76 | -0.19184 | -0.048623 | 0.19201 | 0.048726 | 0.00016163 | 0.00010317 | 0.28764 | 0.28764 | 0.28764 | 0.99311 | -0.13138 | 0.99402 | -0.11387 | 39.5111
77 | 0.069342 | 0.017457 | -0.069308 | -0.017435 | 3.3355e-05 | 2.1241e-05 | 0.10407 | 0.10407 | 0.10407 | 0.99169 | -0.15879 | 0.99117 | -0.16886 | 28.5918
78 | 0.0054406 | 0.0013635 | -0.0054405 | -0.0013635 | 1.0833e-07 | 1.2878e-08 | 0.0081444 | 0.0081444 | 0.0081444 | 0.99402 | -0.11387 | 0.994 | -0.11428 | 2.2375
79 | -0.19745 | -0.05009 | 0.19768 | 0.05024 | 0.00023475 | 0.00014987 | 0.29579 | 0.29579 | 0.29579 | 0.99402 | -0.11387 | 0.99531 | -0.089174 | 40.6298
80 | 0.069308 | 0.017435 | -0.069281 | -0.017418 | 2.7228e-05 | 1.734e-05 | 0.10407 | 0.10407 | 0.10407 | 0.99117 | -0.16886 | 0.99074 | -0.17708 | 28.5918
81 | -0.20058 | -0.050966 | 0.20098 | 0.051219 | 0.00039538 | 0.00025243 | 0.30012 | 0.30012 | 0.30012 | 0.99531 | -0.089174 | 0.99746 | -0.048321 | 41.2251
82 | -0.011306 | -0.0028318 | 0.011308 | 0.002833 | 2.3677e-06 | 1.2383e-06 | 0.017056 | 0.017056 | 0.017056 | 0.98633 | -0.2617 | 0.98656 | -0.2573 | 4.6857
83 | 0.0014128 | 0.00035393 | -0.0014127 | -0.00035407 | 1.9395e-08 | -1.3279e-07 | 0.0021317 | 0.0021318 | 0.0021318 | 0.98614 | -0.26539 | 0.98613 | -0.26568 | 0.58565
84 | 0.0031834 | 0.00079703 | -0.0031829 | -0.0007975 | 5.6017e-07 | -4.6734e-07 | 0.0048033 | 0.0048036 | 0.0048036 | 0.98614 | -0.26539 | 0.98595 | -0.26909 | 1.3197
85 | 0.0087151 | 0.0021835 | -0.0087138 | -0.0021829 | 1.3472e-06 | 6.0329e-07 | 0.013227 | 0.013227 | 0.013227 | 0.98044 | -0.37599 | 0.98028 | -0.37924 | 3.6337
86 | 0.002146 | 0.0005377 | -0.002146 | -0.00053783 | 5.3191e-08 | -1.3241e-07 | 0.0032676 | 0.0032676 | 0.0032676 | 0.97727 | -0.43823 | 0.97724 | -0.43875 | 0.8977
87 | -0.002146 | -0.0005377 | 0.0021461 | 0.00053756 | 5.6569e-08 | -1.4083e-07 | 0.0032676 | 0.0032675 | 0.0032676 | 0.97727 | -0.43823 | 0.9773 | -0.43767 | 0.89768
88 | 0.0057096 | 0.00143 | -0.0057089 | -0.0014298 | 6.835e-07 | 1.3155e-07 | 0.0086666 | 0.0086667 | 0.0086667 | 0.98028 | -0.37924 | 0.98015 | -0.38175 | 2.381
89 | 0.0031621 | 0.00079156 | -0.003162 | -0.00079166 | 1.2958e-07 | -1.0606e-07 | 0.0048003 | 0.0048003 | 0.0048003 | 0.98015 | -0.38175 | 0.98011 | -0.38261 | 1.3188
90 | -0.0031827 | -0.00079765 | 0.0031829 | 0.0007975 | 1.8546e-07 | -1.5464e-07 | 0.0048036 | 0.0048036 | 0.0048036 | 0.98589 | -0.27031 | 0.98595 | -0.26909 | 1.3197
91 | -0.11563 | -0.029448 | 0.11582 | 0.029569 | 0.00018975 | 0.00012122 | 0.17322 | 0.17322 | 0.17322 | 0.99426 | -0.10908 | 0.99604 | -0.075115 | 47.5869
92 | -0.12142 | -0.030974 | 0.12144 | 0.030987 | 1.9239e-05 | 1.2293e-05 | 0.18159 | 0.18159 | 0.18159 | 0.99604 | -0.075115 | 0.99621 | -0.071835 | 49.8878
93 | -0.12432 | -0.031708 | 0.12475 | 0.031985 | 0.00043288 | 0.00027661 | 0.18589 | 0.18589 | 0.18589 | 0.99621 | -0.071835 | 1 | 0 | 51.0692
94 | -0.0039573 | -0.0009918 | 0.0039575 | 0.00099173 | 1.9252e-07 | -7.0605e-08 | 0.0058919 | 0.0058918 | 0.0058919 | 0.99944 | -0.010758 | 0.99949 | -0.009737 | 1.6186
95 | -0.0088961 | -0.0022294 | 0.0088962 | 0.0022295 | 1.7364e-07 | 7.6532e-08 | 0.013244 | 0.013244 | 0.013244 | 0.99949 | -0.009737 | 0.99951 | -0.0093272 | 3.6385
96 | -0.0013747 | -0.00034454 | 0.0013748 | 0.00034375 | 1.1111e-07 | -7.8598e-07 | 0.0020873 | 0.002087 | 0.0020873 | 0.98002 | -0.38431 | 0.98011 | -0.38261 | 0.57344
97 | 0.0068323 | 0.0017123 | -0.0068316 | -0.0017121 | 6.4101e-07 | 1.955e-07 | 0.010192 | 0.010193 | 0.010193 | 0.99746 | -0.048321 | 0.99735 | -0.05029 | 2.8002
98 | -0.21703 | -0.055242 | 0.21743 | 0.055501 | 0.00040562 | 0.00025905 | 0.32406 | 0.32406 | 0.32406 | 0.99746 | -0.048321 | 0.99949 | -0.0096344 | 44.5143
99 | 0.004081 | 0.0010228 | -0.0040809 | -0.0010228 | 7.728e-08 | -2.3082e-08 | 0.0060887 | 0.0060887 | 0.0060887 | 0.99735 | -0.05029 | 0.99733 | -0.050688 | 1.6727
100 | -0.21841 | -0.055746 | 0.21845 | 0.055768 | 3.451e-05 | 2.2041e-05 | 0.32552 | 0.32552 | 0.32552 | 0.99949 | -0.0096344 | 0.99966 | -0.0063648 | 44.7146
101 | -0.060426 | -0.015186 | 0.060457 | 0.015207 | 3.1752e-05 | 2.0189e-05 | 0.090822 | 0.090822 | 0.090822 | 0.99017 | -0.18809 | 0.99074 | -0.17708 | 24.951
102 | 0.058169 | 0.014621 | -0.058155 | -0.014612 | 1.4304e-05 | 9.0906e-06 | 0.087431 | 0.087431 | 0.087431 | 0.99017 | -0.18809 | 0.98991 | -0.19324 | 24.0195
103 | 0.049913 | 0.012546 | -0.049863 | -0.012515 | 4.9597e-05 | 3.1441e-05 | 0.075041 | 0.075042 | 0.075042 | 0.98991 | -0.19324 | 0.98883 | -0.21407 | 20.6158
104 | 0.043977 | 0.011039 | -0.043966 | -0.011032 | 1.0877e-05 | 6.8761e-06 | 0.066183 | 0.066183 | 0.066183 | 0.98883 | -0.21407 | 0.98857 | -0.21926 | 18.1823
105 | 0.029291 | 0.0073521 | -0.029283 | -0.0073475 | 7.4019e-06 | 4.6071e-06 | 0.044093 | 0.044093 | 0.044093 | 0.98857 | -0.21926 | 0.98829 | -0.22456 | 12.1135
106 | 0.014675 | 0.0036803 | -0.014674 | -0.0036798 | 9.833e-07 | 5.6043e-07 | 0.022091 | 0.022091 | 0.022091 | 0.98857 | -0.21926 | 0.98849 | -0.22066 | 6.0688
107 | 0.023353 | 0.0058613 | -0.023346 | -0.0058567 | 7.5619e-06 | 4.6307e-06 | 0.035165 | 0.035165 | 0.035165 | 0.98829 | -0.22456 | 0.98794 | -0.23135 | 9.6606
108 | 0.011604 | 0.0029102 | -0.011601 | -0.0029086 | 2.9589e-06 | 1.5623e-06 | 0.017468 | 0.017468 | 0.017468 | 0.98849 | -0.22066 | 0.98822 | -0.22601 | 4.7989
109 | 0.020097 | 0.0050393 | -0.020092 | -0.0050365 | 4.7339e-06 | 2.8446e-06 | 0.029905 | 0.029905 | 0.029905 | 1 | 0 | 0.99974 | -0.0049439 | 8.2157
110 | 0.22167 | 0.056603 | -0.2216 | -0.056559 | 6.8168e-05 | 4.354e-05 | 0.33022 | 0.33022 | 0.33022 | 1 | 0 | 0.99966 | -0.0063648 | 45.3597
111 | 0.015767 | 0.0039525 | -0.015763 | -0.0039506 | 3.2923e-06 | 1.8981e-06 | 0.023467 | 0.023467 | 0.023467 | 0.99974 | -0.0049439 | 0.99951 | -0.0093272 | 6.4471
112 | 0.011084 | 0.0027784 | -0.011082 | -0.0027773 | 2.1322e-06 | 1.1145e-06 | 0.016876 | 0.016876 | 0.016876 | 0.97734 | -0.43689 | 0.97713 | -0.44092 | 4.6364
113 | 0.0096529 | 0.0024191 | -0.009652 | -0.0024187 | 8.5399e-07 | 4.1455e-07 | 0.0147 | 0.0147 | 0.0147 | 0.97713 | -0.44092 | 0.97704 | -0.44278 | 4.0384
114 | 0.0082488 | 0.002067 | -0.0082487 | -0.002067 | 9.705e-08 | 4.1575e-08 | 0.012563 | 0.012563 | 0.012563 | 0.97704 | -0.44278 | 0.97703 | -0.44303 | 3.4513
115 | 0.0067699 | 0.0016963 | -0.0067689 | -0.001696 | 1.0199e-06 | 3.3241e-07 | 0.010311 | 0.010311 | 0.010311 | 0.97703 | -0.44303 | 0.97686 | -0.44619 | 2.8326
116 | 0.0067689 | 0.001696 | -0.0067674 | -0.0016955 | 1.4794e-06 | 4.8235e-07 | 0.010311 | 0.010311 | 0.010311 | 0.97686 | -0.44619 | 0.97663 | -0.45078 | 2.8326
117 | 0.013544 | 0.0033963 | -0.013541 | -0.0033945 | 3.2489e-06 | 1.8135e-06 | 0.020414 | 0.020414 | 0.020414 | 0.98733 | -0.24333 | 0.98707 | -0.24836 | 5.6082
118 | -0.018164 | -0.0045542 | 0.018172 | 0.0045585 | 7.1509e-06 | 4.2511e-06 | 0.027377 | 0.027376 | 0.027377 | 0.98733 | -0.24333 | 0.98775 | -0.23507 | 7.521
119 | 0.010473 | 0.0026255 | -0.010471 | -0.0026248 | 1.4694e-06 | 7.3952e-07 | 0.015788 | 0.015788 | 0.015788 | 0.98707 | -0.24836 | 0.98692 | -0.25131 | 4.3374
120 | -0.023341 | -0.0058542 | 0.023346 | 0.0058567 | 4.1395e-06 | 2.535e-06 | 0.035165 | 0.035165 | 0.035165 | 0.98775 | -0.23507 | 0.98794 | -0.23135 | 9.6606
121 | 0.010471 | 0.0026248 | -0.01047 | -0.0026239 | 1.5965e-06 | 8.0357e-07 | 0.015788 | 0.015788 | 0.015788 | 0.98692 | -0.25131 | 0.98675 | -0.25451 | 4.3374
122 | 0.0063262 | 0.0015855 | -0.006326 | -0.0015854 | 2.3245e-07 | 6.1766e-08 | 0.0095399 | 0.0095399 | 0.0095399 | 0.98675 | -0.25451 | 0.98672 | -0.25528 | 2.6209
123 | 0.0040075 | 0.0010044 | -0.0040075 | -0.0010044 | 4.6303e-09 | -1.3544e-09 | 0.0060435 | 0.0060435 | 0.0060435 | 0.98672 | -0.25528 | 0.98671 | -0.2553 | 1.6603
124 | 0.0058781 | 0.0014726 | -0.005878 | -0.0014726 | 1.1447e-07 | 2.5639e-08 | 0.0089558 | 0.0089558 | 0.0089558 | 0.97663 | -0.45078 | 0.97661 | -0.45119 | 2.4604
125 | 0.0030793 | 0.00077121 | -0.0030791 | -0.00077142 | 2.4703e-07 | -2.1633e-07 | 0.0046916 | 0.0046918 | 0.0046918 | 0.97661 | -0.45119 | 0.97653 | -0.45287 | 1.289
126 | 0.011601 | 0.0029086 | -0.011599 | -0.0029078 | 1.5866e-06 | 8.3783e-07 | 0.017468 | 0.017468 | 0.017468 | 0.98822 | -0.22601 | 0.98807 | -0.22889 | 4.799
127 | 0.011599 | 0.0029078 | -0.011596 | -0.0029063 | 2.714e-06 | 1.4332e-06 | 0.017468 | 0.017468 | 0.017468 | 0.98807 | -0.22889 | 0.98782 | -0.2338 | 4.799
128 | 0.0089836 | 0.0022515 | -0.008983 | -0.0022512 | 6.7364e-07 | 3.0557e-07 | 0.013533 | 0.013533 | 0.013533 | 0.98782 | -0.2338 | 0.98774 | -0.23537 | 3.7178
129 | -0.005374 | -0.0013467 | 0.0053741 | 0.0013468 | 1.6126e-07 | 1.9236e-08 | 0.0080961 | 0.008096 | 0.0080961 | 0.98771 | -0.236 | 0.98774 | -0.23537 | 2.2242
130 | 0.0030791 | 0.00077142 | -0.003079 | -0.00077149 | 7.0535e-08 | -6.1754e-08 | 0.0046918 | 0.0046918 | 0.0046918 | 0.97653 | -0.45287 | 0.9765 | -0.45335 | 1.289
131 | 0.00069918 | 0.00017504 | -0.00069917 | -0.00017523 | 6.5248e-09 | -1.8759e-07 | 0.0010654 | 0.0010654 | 0.0010654 | 0.9765 | -0.45335 | 0.97649 | -0.45355 | 0.2927

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.36817 | 0.093627

## res_load
| p_mw | q_mvar
0 | 0.023082 | 0.005785
1 | 0.0086632 | 0.0021712
2 | 0.0038739 | 0.0009709
3 | 0.0039451 | 0.00098873
4 | 0.0059221 | 0.0014842
5 | 0.0073998 | 0.0018546
6 | 0.0021638 | 0.00054229
7 | 0.0041718 | 0.0010456
8 | 0.0060873 | 0.0015256
9 | 0.0078524 | 0.001968
10 | 0.0022337 | 0.00055982
11 | 0.0045916 | 0.0011508
12 | 0.0053556 | 0.0013422
13 | 0.0069005 | 0.0017294
14 | 0.0022542 | 0.00056495
15 | 0.0054468 | 0.0013651
16 | 0.0033083 | 0.00082915
17 | 0.0026878 | 0.00067363
18 | 0.0017142 | 0.00042962
19 | 0.003418 | 0.00085664
20 | 0.0024917 | 0.00062448
21 | 0.0021308 | 0.00053403
22 | 0.0037561 | 0.00094137
23 | 0.0032605 | 0.00081715
24 | 0.0059577 | 0.0014931
25 | 0.002152 | 0.00053935
26 | 0.0021246 | 0.00053247
27 | 0.0014474 | 0.00036276
28 | 0.0017162 | 0.00043011
29 | 0.0022518 | 0.00056435
30 | 0.0026763 | 0.00067074
31 | 0.0014478 | 0.00036286
32 | 0.0022347 | 0.00056006
33 | 0.0033543 | 0.00084067
34 | 0.0024103 | 0.00060409
35 | 0.0010264 | 0.00025724
36 | 0.0027374 | 0.00068605
37 | 0.0032929 | 0.00082527
38 | 0.0036235 | 0.00090814
39 | 0.0047456 | 0.0011894
40 | 0.0027505 | 0.00068933
41 | 0.0015349 | 0.00038469
42 | 0.0011587 | 0.00029039
43 | 0.0013283 | 0.0003329
44 | 0.0014685 | 0.00036803
45 | 0.0036137 | 0.00090569
46 | 0.003101 | 0.00077717
47 | 0.0026267 | 0.00065831
48 | 0.0037973 | 0.00095168
49 | 0.0053843 | 0.0013494
50 | 0.0037705 | 0.00094499
51 | 0.0022693 | 0.00056873
52 | 0.003958 | 0.00099197
53 | 0.0054405 | 0.0013635
54 | 0.0028989 | 0.00072653
55 | 0.001218 | 0.00030527
56 | 0.0015018 | 0.00037637
57 | 0.0024765 | 0.00062067
58 | 0.002146 | 0.00053783
59 | 0.0017592 | 0.00044091
60 | 0.0030042 | 0.00075291
61 | 0.0025468 | 0.00063828
62 | 0.0031827 | 0.00079765
63 | 0.0014127 | 0.00035407
64 | 0.0045023 | 0.0011284
65 | 0.0056064 | 0.0014051
66 | 0.0028788 | 0.0007215
67 | 0.0039573 | 0.0009918
68 | 0.0049385 | 0.0012377
69 | 0.0013747 | 0.00034454
70 | 0.0017872 | 0.00044791
71 | 0.0027506 | 0.00068938
72 | 0.00097963 | 0.00024552
73 | 0.0022564 | 0.00056551
74 | 0.0088237 | 0.0022114
75 | 0.0082421 | 0.0020657
76 | 0.0058865 | 0.0014753
77 | 0.00593 | 0.0014862
78 | 0.0030708 | 0.0007696
79 | 0.0043253 | 0.001084
80 | 0.0031551 | 0.00079075
81 | 0.006867 | 0.001721
82 | 0.0040809 | 0.0010228
83 | 0.0034001 | 0.00085214
84 | 0.0014293 | 0.00035823
85 | 0.0014032 | 0.00035168
86 | 0.0014788 | 0.00037061
87 | 0.00462 | 0.0011579
88 | 0.0030684 | 0.00076902
89 | 0.0051698 | 0.0012957
90 | 0.0041434 | 0.0010384
91 | 0.0023185 | 0.00058108
92 | 0.00088935 | 0.00022289
93 | 0.0027986 | 0.0007014
94 | 0.0026127 | 0.00065481
95 | 0.0032431 | 0.0008128
96 | 0.0036088 | 0.00090446
97 | 0.0040075 | 0.0010044
98 | 0.0029489 | 0.00073905
99 | 0.0023798 | 0.00059645
100 | 0.00069917 | 0.00017523

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1