## bus
| name | vn_kv | type | zone | in_service
0 | bus_LV_6007-31_0_1_node_0 | 0.4 | n |  | TRUE
1 | bus_LV_6007-31_0_1_node_1 | 0.4 | n |  | TRUE
2 | bus_LV_6007-31_0_1_node_12 | 0.4 | n |  | TRUE
3 | bus_LV_6007-31_0_1_node_2 | 0.4 | n |  | TRUE
4 | bus_LV_6007-31_0_1_node_17 | 0.4 | n |  | TRUE
5 | bus_LV_6007-31_0_1_node_10 | 0.4 | n |  | TRUE
6 | bus_LV_6007-31_0_1_node_42 | 0.4 | n |  | TRUE
7 | bus_LV_6007-31_0_1_node_41 | 0.4 | n |  | TRUE
8 | bus_LV_6007-31_0_1_node_3 | 0.4 | n |  | TRUE
9 | bus_LV_6007-31_0_1_node_4 | 0.4 | n |  | TRUE
10 | bus_LV_6007-31_0_1_node_5 | 0.4 | n |  | TRUE
11 | bus_LV_6007-31_0_1_node_6 | 0.4 | n |  | TRUE
12 | bus_LV_6007-31_0_1_node_7 | 0.4 | n |  | TRUE
13 | bus_LV_6007-31_0_1_node_29 | 0.4 | n |  | TRUE
14 | bus_LV_6007-31_0_1_node_30 | 0.4 | n |  | TRUE
15 | bus_LV_6007-31_0_1_node_8 | 0.4 | n |  | TRUE
16 | bus_LV_6007-31_0_1_node_35 | 0.4 | n |  | TRUE
17 | bus_LV_6007-31_0_1_node_36 | 0.4 | n |  | TRUE
18 | bus_LV_6007-31_0_1_node_26 | 0.4 | n |  | TRUE
19 | bus_LV_6007-31_0_1_node_22 | 0.4 | n |  | TRUE
20 | bus_LV_6007-31_0_1_node_20 | 0.4 | n |  | TRUE
21 | bus_LV_6007-31_0_1_node_31 | 0.4 | n |  | TRUE
22 | bus_LV_6007-31_0_1_node_18 | 0.4 | n |  | TRUE
23 | bus_LV_6007-31_0_1_node_9 | 0.4 | n |  | TRUE
24 | bus_LV_6007-31_0_1_node_15 | 0.4 | n |  | TRUE
25 | bus_LV_6007-31_0_1_node_82 | 0.4 | n |  | TRUE
26 | bus_LV_6007-31_0_1_node_13 | 0.4 | n |  | TRUE
27 | bus_LV_6007-31_0_1_node_14 | 0.4 | n |  | TRUE
28 | bus_LV_6007-31_0_1_node_16 | 0.4 | n |  | TRUE
29 | bus_LV_6007-31_0_1_node_33 | 0.4 | n |  | TRUE
30 | bus_LV_6007-31_0_1_node_34 | 0.4 | n |  | TRUE
31 | bus_LV_6007-31_0_1_node_19 | 0.4 | n |  | TRUE
32 | bus_LV_6007-31_0_1_node_21 | 0.4 | n |  | TRUE
33 | bus_LV_6007-31_0_1_node_32 | 0.4 | n |  | TRUE
34 | bus_LV_6007-31_0_1_node_23 | 0.4 | n |  | TRUE
35 | bus_LV_6007-31_0_1_node_24 | 0.4 | n |  | TRUE
36 | bus_LV_6007-31_0_1_node_25 | 0.4 | n |  | TRUE
37 | bus_LV_6007-31_0_1_node_27 | 0.4 | n |  | TRUE
38 | bus_LV_6007-31_0_1_node_28 | 0.4 | n |  | TRUE
39 | bus_LV_6007-31_0_1_node_38 | 0.4 | n |  | TRUE
40 | bus_LV_6007-31_0_1_node_50 | 0.4 | n |  | TRUE
41 | bus_LV_6007-31_0_1_node_84 | 0.4 | n |  | TRUE
42 | bus_LV_6007-31_0_1_node_39 | 0.4 | n |  | TRUE
43 | bus_LV_6007-31_0_1_node_37 | 0.4 | n |  | TRUE
44 | bus_LV_6007-31_0_1_node_49 | 0.4 | n |  | TRUE
45 | bus_LV_6007-31_0_1_node_83 | 0.4 | n |  | TRUE
46 | bus_LV_6007-31_0_1_node_40 | 0.4 | n |  | TRUE
47 | bus_LV_6007-31_0_1_node_43 | 0.4 | n |  | TRUE
48 | bus_LV_6007-31_0_1_node_44 | 0.4 | n |  | TRUE
49 | bus_LV_6007-31_0_1_node_45 | 0.4 | n |  | TRUE
50 | bus_LV_6007-31_0_1_node_46 | 0.4 | n |  | TRUE
51 | bus_LV_6007-31_0_1_node_47 | 0.4 | n |  | TRUE
52 | bus_LV_6007-31_0_1_node_55 | 0.4 | n |  | TRUE
53 | bus_LV_6007-31_0_1_node_67 | 0.4 | n |  | TRUE
54 | bus_LV_6007-31_0_1_node_53 | 0.4 | n |  | TRUE
55 | bus_LV_6007-31_0_1_node_68 | 0.4 | n |  | TRUE
56 | bus_LV_6007-31_0_1_node_48 | 0.4 | n |  | TRUE
57 | bus_LV_6007-31_0_1_node_78 | 0.4 | n |  | TRUE
58 | bus_LV_6007-31_0_1_node_77 | 0.4 | n |  | TRUE
59 | bus_LV_6007-31_0_1_node_76 | 0.4 | n |  | TRUE
60 | bus_LV_6007-31_0_1_node_85 | 0.4 | n |  | TRUE
61 | bus_LV_6007-31_0_1_node_51 | 0.4 | n |  | TRUE
62 | bus_LV_6007-31_0_1_node_52 | 0.4 | n |  | TRUE
63 | bus_LV_6007-31_0_1_node_54 | 0.4 | n |  | TRUE
64 | bus_LV_6007-31_0_1_node_57 | 0.4 | n |  | TRUE
65 | bus_LV_6007-31_0_1_node_56 | 0.4 | n |  | TRUE
66 | bus_LV_6007-31_0_1_node_58 | 0.4 | n |  | TRUE
67 | bus_LV_6007-31_0_1_node_59 | 0.4 | n |  | TRUE
68 | bus_LV_6007-31_0_1_node_65 | 0.4 | n |  | TRUE
69 | bus_LV_6007-31_0_1_node_66 | 0.4 | n |  | TRUE
70 | bus_LV_6007-31_0_1_node_60 | 0.4 | n |  | TRUE
71 | bus_LV_6007-31_0_1_node_61 | 0.4 | n |  | TRUE
72 | bus_LV_6007-31_0_1_node_62 | 0.4 | n |  | TRUE
73 | bus_LV_6007-31_0_1_node_63 | 0.4 | n |  | TRUE
74 | bus_LV_6007-31_0_1_node_64 | 0.4 | n |  | TRUE
75 | bus_LV_6007-31_0_1_node_73 | 0.4 | n |  | TRUE
76 | bus_LV_6007-31_0_1_node_69 | 0.4 | n |  | TRUE
77 | bus_LV_6007-31_0_1_node_80 | 0.4 | n |  | TRUE
78 | bus_LV_6007-31_0_1_node_70 | 0.4 | n |  | TRUE
79 | bus_LV_6007-31_0_1_node_79 | 0.4 | n |  | TRUE
80 | bus_LV_6007-31_0_1_node_72 | 0.4 | n |  | TRUE
81 | bus_LV_6007-31_0_1_node_74 | 0.4 | n |  | TRUE
82 | bus_LV_6007-31_0_1_node_75 | 0.4 | n |  | TRUE
83 | bus_LV_6007-31_0_1_node_71 | 0.4 | n |  | TRUE
84 | bus_LV_6007-31_0_1_node_81 | 0.4 | n |  | TRUE
85 | bus_MV_87_0_node_178 | 20 | n |  | TRUE

## load
| name | bus | p_mw | q_mvar | const_z_percent | const_i_percent | sn_mva | scaling | in_service | type
0 | LV_6007-31_0_1_load_0 | 0 | 0.00045274 | 0.00011347 | 0 | 0 |  | 1 | TRUE | wye
1 | LV_6007-31_0_1_load_12 | 2 | 0.00082666 | 0.00020718 | 0 | 0 |  | 1 | TRUE | wye
2 | LV_6007-31_0_1_load_2 | 3 | 0.000514 | 0.00012882 | 0 | 0 |  | 1 | TRUE | wye
3 | LV_6007-31_0_1_load_10 | 5 | 0.00069222 | 0.00017349 | 0 | 0 |  | 1 | TRUE | wye
4 | LV_6007-31_0_1_load_42 | 6 | 0.00047719 | 0.00011959 | 0 | 0 |  | 1 | TRUE | wye
5 | LV_6007-31_0_1_load_41 | 7 | 0.00052033 | 0.00013041 | 0 | 0 |  | 1 | TRUE | wye
6 | LV_6007-31_0_1_load_3 | 8 | 0.0014849 | 0.00037215 | 0 | 0 |  | 1 | TRUE | wye
7 | LV_6007-31_0_1_load_4 | 9 | 0.0014237 | 0.0003568 | 0 | 0 |  | 1 | TRUE | wye
8 | LV_6007-31_0_1_load_5 | 10 | 0.001624 | 0.00040702 | 0 | 0 |  | 1 | TRUE | wye
9 | LV_6007-31_0_1_load_7 | 12 | 0.0017371 | 0.00043537 | 0 | 0 |  | 1 | TRUE | wye
10 | LV_6007-31_0_1_load_30 | 14 | 0.0021328 | 0.00053454 | 0 | 0 |  | 1 | TRUE | wye
11 | LV_6007-31_0_1_load_35 | 16 | 0.0022984 | 0.00057604 | 0 | 0 |  | 1 | TRUE | wye
12 | LV_6007-31_0_1_load_36 | 17 | 0.0021742 | 0.0005449 | 0 | 0 |  | 1 | TRUE | wye
13 | LV_6007-31_0_1_load_26 | 18 | 0.0012852 | 0.0003221 | 0 | 0 |  | 1 | TRUE | wye
14 | LV_6007-31_0_1_load_22 | 19 | 0.0018741 | 0.00046968 | 0 | 0 |  | 1 | TRUE | wye
15 | LV_6007-31_0_1_load_31 | 21 | 0.0020744 | 0.00051988 | 0 | 0 |  | 1 | TRUE | wye
16 | LV_6007-31_0_1_load_18 | 22 | 0.0014628 | 0.00036661 | 0 | 0 |  | 1 | TRUE | wye
17 | LV_6007-31_0_1_load_9 | 23 | 0.00051415 | 0.00012886 | 0 | 0 |  | 1 | TRUE | wye
18 | LV_6007-31_0_1_load_15 | 24 | 0.00050278 | 0.00012601 | 0 | 0 |  | 1 | TRUE | wye
19 | LV_6007-31_0_1_load_82 | 25 | 0.0011308 | 0.0002834 | 0 | 0 |  | 1 | TRUE | wye
20 | LV_6007-31_0_1_load_13 | 26 | 0.00078499 | 0.00019674 | 0 | 0 |  | 1 | TRUE | wye
21 | LV_6007-31_0_1_load_14 | 27 | 0.00053589 | 0.00013431 | 0 | 0 |  | 1 | TRUE | wye
22 | LV_6007-31_0_1_load_16 | 28 | 0.00067214 | 0.00016845 | 0 | 0 |  | 1 | TRUE | wye
23 | LV_6007-31_0_1_load_34 | 30 | 0.00068893 | 0.00017266 | 0 | 0 |  | 1 | TRUE | wye
24 | LV_6007-31_0_1_load_19 | 31 | 0.0012592 | 0.00031559 | 0 | 0 |  | 1 | TRUE | wye
25 | LV_6007-31_0_1_load_21 | 32 | 0.0016294 | 0.00040836 | 0 | 0 |  | 1 | TRUE | wye
26 | LV_6007-31_0_1_load_32 | 33 | 0.0015268 | 0.00038264 | 0 | 0 |  | 1 | TRUE | wye
27 | LV_6007-31_0_1_load_23 | 34 | 0.0023034 | 0.00057729 | 0 | 0 |  | 1 | TRUE | wye
28 | LV_6007-31_0_1_load_24 | 35 | 0.0017023 | 0.00042665 | 0 | 0 |  | 1 | TRUE | wye
29 | LV_6007-31_0_1_load_27 | 37 | 0.0016218 | 0.00040645 | 0 | 0 |  | 1 | TRUE | wye
30 | LV_6007-31_0_1_load_84 | 41 | 0.0027058 | 0.00067815 | 0 | 0 |  | 1 | TRUE | wye
31 | LV_6007-31_0_1_load_39 | 42 | 0.0023991 | 0.00060126 | 0 | 0 |  | 1 | TRUE | wye
32 | LV_6007-31_0_1_load_37 | 43 | 0.0056941 | 0.0014271 | 0 | 0 |  | 1 | TRUE | wye
33 | LV_6007-31_0_1_load_83 | 45 | 0.0024019 | 0.00060198 | 0 | 0 |  | 1 | TRUE | wye
34 | LV_6007-31_0_1_load_40 | 46 | 0.0049001 | 0.0012281 | 0 | 0 |  | 1 | TRUE | wye
35 | LV_6007-31_0_1_load_43 | 47 | 0.0012786 | 0.00032046 | 0 | 0 |  | 1 | TRUE | wye
36 | LV_6007-31_0_1_load_44 | 48 | 0.0010716 | 0.00026858 | 0 | 0 |  | 1 | TRUE | wye
37 | LV_6007-31_0_1_load_45 | 49 | 0.00067004 | 0.00016793 | 0 | 0 |  | 1 | TRUE | wye
38 | LV_6007-31_0_1_load_46 | 50 | 0.0015206 | 0.0003811 | 0 | 0 |  | 1 | TRUE | wye
39 | LV_6007-31_0_1_load_47 | 51 | 0.00073441 | 0.00018406 | 0 | 0 |  | 1 | TRUE | wye
40 | LV_6007-31_0_1_load_55 | 52 | 0.0010606 | 0.00026582 | 0 | 0 |  | 1 | TRUE | wye
41 | LV_6007-31_0_1_load_53 | 54 | 0.0014422 | 0.00036145 | 0 | 0 |  | 1 | TRUE | wye
42 | LV_6007-31_0_1_load_48 | 56 | 0.0012203 | 0.00030583 | 0 | 0 |  | 1 | TRUE | wye
43 | LV_6007-31_0_1_load_77 | 58 | 0.0010973 | 0.00027501 | 0 | 0 |  | 1 | TRUE | wye
44 | LV_6007-31_0_1_load_76 | 59 | 0.0016166 | 0.00040516 | 0 | 0 |  | 1 | TRUE | wye
45 | LV_6007-31_0_1_load_85 | 60 | 0.0045774 | 0.0011472 | 0 | 0 |  | 1 | TRUE | wye
46 | LV_6007-31_0_1_load_51 | 61 | 0.00090382 | 0.00022652 | 0 | 0 |  | 1 | TRUE | wye
47 | LV_6007-31_0_1_load_52 | 62 | 0.00098562 | 0.00024702 | 0 | 0 |  | 1 | TRUE | wye
48 | LV_6007-31_0_1_load_54 | 63 | 0.0015385 | 0.00038559 | 0 | 0 |  | 1 | TRUE | wye
49 | LV_6007-31_0_1_load_57 | 64 | 0.00064127 | 0.00016072 | 0 | 0 |  | 1 | TRUE | wye
50 | LV_6007-31_0_1_load_56 | 65 | 0.00063575 | 0.00015933 | 0 | 0 |  | 1 | TRUE | wye
51 | LV_6007-31_0_1_load_58 | 66 | 0.00080304 | 0.00020126 | 0 | 0 |  | 1 | TRUE | wye
52 | LV_6007-31_0_1_load_59 | 67 | 0.00065722 | 0.00016472 | 0 | 0 |  | 1 | TRUE | wye
53 | LV_6007-31_0_1_load_65 | 68 | 0.00079461 | 0.00019915 | 0 | 0 |  | 1 | TRUE | wye
54 | LV_6007-31_0_1_load_66 | 69 | 0.00070797 | 0.00017743 | 0 | 0 |  | 1 | TRUE | wye
55 | LV_6007-31_0_1_load_60 | 70 | 0.00081376 | 0.00020395 | 0 | 0 |  | 1 | TRUE | wye
56 | LV_6007-31_0_1_load_61 | 71 | 0.00090276 | 0.00022625 | 0 | 0 |  | 1 | TRUE | wye
57 | LV_6007-31_0_1_load_62 | 72 | 0.00064092 | 0.00016063 | 0 | 0 |  | 1 | TRUE | wye
58 | LV_6007-31_0_1_load_63 | 73 | 0.0012139 | 0.00030422 | 0 | 0 |  | 1 | TRUE | wye
59 | LV_6007-31_0_1_load_73 | 75 | 0.00097211 | 0.00024363 | 0 | 0 |  | 1 | TRUE | wye
60 | LV_6007-31_0_1_load_69 | 76 | 0.0011821 | 0.00029627 | 0 | 0 |  | 1 | TRUE | wye
61 | LV_6007-31_0_1_load_79 | 79 | 0.00070185 | 0.0001759 | 0 | 0 |  | 1 | TRUE | wye
62 | LV_6007-31_0_1_load_74 | 81 | 0.00069937 | 0.00017528 | 0 | 0 |  | 1 | TRUE | wye
63 | LV_6007-31_0_1_load_75 | 82 | 0.00058108 | 0.00014563 | 0 | 0 |  | 1 | TRUE | wye
64 | LV_6007-31_0_1_load_71 | 83 | 0.00082174 | 0.00020595 | 0 | 0 |  | 1 | TRUE | wye
65 | LV_6007-31_0_1_load_81 | 84 | 0.00099275 | 0.00024881 | 0 | 0 |  | 1 | TRUE | wye

## ext_grid
| name | bus | vm_pu | va_degree | slack_weight | in_service
0 |  | 45 | 1 | 0 | 1 | TRUE

## line
| name | std_type | from_bus | to_bus | length_km | r_ohm_per_km | x_ohm_per_km | c_nf_per_km | g_us_per_km | max_i_ka | df | parallel | type | in_service
0 | LV_6007-31_0_1_line_0 |  | 0 | 1 | 0.030029 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
1 | LV_6007-31_0_1_line_1 |  | 0 | 2 | 0.049928 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
2 | LV_6007-31_0_1_line_2 |  | 1 | 3 | 0.0047316 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
3 | LV_6007-31_0_1_line_3 |  | 2 | 4 | 0.062822 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
4 | LV_6007-31_0_1_line_4 |  | 2 | 5 | 0.061262 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
5 | LV_6007-31_0_1_line_5 |  | 3 | 6 | 0.0065288 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
6 | LV_6007-31_0_1_line_6 |  | 4 | 24 | 0.039413 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
7 | LV_6007-31_0_1_line_7 |  | 5 | 23 | 0.041926 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
8 | LV_6007-31_0_1_line_8 |  | 6 | 7 | 0.0043051 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
9 | LV_6007-31_0_1_line_9 |  | 7 | 25 | 0.13445 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
10 | LV_6007-31_0_1_line_10 |  | 8 | 9 | 0.0072112 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
11 | LV_6007-31_0_1_line_11 |  | 8 | 10 | 0.0068963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
12 | LV_6007-31_0_1_line_12 |  | 9 | 11 | 0.0052379 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
13 | LV_6007-31_0_1_line_13 |  | 10 | 12 | 0.008412 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
14 | LV_6007-31_0_1_line_14 |  | 11 | 13 | 0.030532 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
15 | LV_6007-31_0_1_line_15 |  | 11 | 14 | 0.017074 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
16 | LV_6007-31_0_1_line_16 |  | 12 | 15 | 0.023437 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
17 | LV_6007-31_0_1_line_17 |  | 13 | 16 | 0.020233 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
18 | LV_6007-31_0_1_line_18 |  | 13 | 17 | 0.037032 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
19 | LV_6007-31_0_1_line_19 |  | 14 | 18 | 0.025602 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
20 | LV_6007-31_0_1_line_20 |  | 15 | 19 | 0.018155 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
21 | LV_6007-31_0_1_line_21 |  | 15 | 20 | 0.017495 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
22 | LV_6007-31_0_1_line_22 |  | 16 | 30 | 0.023021 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
23 | LV_6007-31_0_1_line_23 |  | 17 | 43 | 0.024311 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
24 | LV_6007-31_0_1_line_24 |  | 18 | 35 | 0.012909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
25 | LV_6007-31_0_1_line_25 |  | 19 | 21 | 0.050704 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
26 | LV_6007-31_0_1_line_26 |  | 20 | 22 | 0.053057 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
27 | LV_6007-31_0_1_line_27 |  | 21 | 33 | 0.15006 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
28 | LV_6007-31_0_1_line_28 |  | 22 | 31 | 0.036127 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
29 | LV_6007-31_0_1_line_29 |  | 24 | 26 | 0.0038642 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
30 | LV_6007-31_0_1_line_30 |  | 26 | 27 | 0.0069084 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
31 | LV_6007-31_0_1_line_31 |  | 27 | 28 | 0.0007202 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
32 | LV_6007-31_0_1_line_32 |  | 28 | 29 | 0.0089207 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
33 | LV_6007-31_0_1_line_33 |  | 29 | 30 | 0.0040738 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
34 | LV_6007-31_0_1_line_34 |  | 31 | 32 | 0.0030909 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
35 | LV_6007-31_0_1_line_35 |  | 34 | 35 | 0.014293 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
36 | LV_6007-31_0_1_line_36 |  | 36 | 37 | 0.056769 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
37 | LV_6007-31_0_1_line_37 |  | 36 | 38 | 0.014997 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
38 | LV_6007-31_0_1_line_38 |  | 37 | 39 | 0.021263 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
39 | LV_6007-31_0_1_line_39 |  | 38 | 40 | 0.036963 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
40 | LV_6007-31_0_1_line_40 |  | 38 | 41 | 0.02669 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
41 | LV_6007-31_0_1_line_41 |  | 39 | 42 | 0.018519 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
42 | LV_6007-31_0_1_line_42 |  | 39 | 43 | 0.011575 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
43 | LV_6007-31_0_1_line_43 |  | 40 | 44 | 0.092668 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
44 | LV_6007-31_0_1_line_44 |  | 41 | 45 | 0.048723 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
45 | LV_6007-31_0_1_line_45 |  | 42 | 46 | 0.017028 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
46 | LV_6007-31_0_1_line_46 |  | 44 | 57 | 0.13612 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
47 | LV_6007-31_0_1_line_47 |  | 44 | 56 | 0.017298 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
48 | LV_6007-31_0_1_line_48 |  | 47 | 48 | 0.11329 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
49 | LV_6007-31_0_1_line_49 |  | 47 | 49 | 0.054808 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
50 | LV_6007-31_0_1_line_50 |  | 48 | 50 | 0.062351 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
51 | LV_6007-31_0_1_line_51 |  | 49 | 51 | 0.010037 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
52 | LV_6007-31_0_1_line_52 |  | 50 | 52 | 0.06446 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
53 | LV_6007-31_0_1_line_53 |  | 51 | 53 | 0.054726 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
54 | LV_6007-31_0_1_line_54 |  | 52 | 54 | 0.017944 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
55 | LV_6007-31_0_1_line_55 |  | 53 | 55 | 0.055921 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
56 | LV_6007-31_0_1_line_56 |  | 54 | 61 | 0.022896 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
57 | LV_6007-31_0_1_line_57 |  | 55 | 81 | 0.0090625 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
58 | LV_6007-31_0_1_line_58 |  | 57 | 60 | 0.063913 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
59 | LV_6007-31_0_1_line_59 |  | 57 | 58 | 0.022098 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
60 | LV_6007-31_0_1_line_60 |  | 58 | 59 | 0.030689 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
61 | LV_6007-31_0_1_line_61 |  | 59 | 73 | 0.15487 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
62 | LV_6007-31_0_1_line_62 |  | 61 | 62 | 0.012433 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
63 | LV_6007-31_0_1_line_63 |  | 62 | 63 | 0.026478 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
64 | LV_6007-31_0_1_line_64 |  | 63 | 64 | 0.014783 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
65 | LV_6007-31_0_1_line_65 |  | 64 | 65 | 0.028167 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
66 | LV_6007-31_0_1_line_66 |  | 65 | 66 | 0.0070787 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
67 | LV_6007-31_0_1_line_67 |  | 66 | 67 | 0.0036961 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
68 | LV_6007-31_0_1_line_68 |  | 67 | 68 | 0.0044276 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
69 | LV_6007-31_0_1_line_69 |  | 68 | 69 | 0.019672 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
70 | LV_6007-31_0_1_line_70 |  | 69 | 79 | 0.0062349 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
71 | LV_6007-31_0_1_line_71 |  | 70 | 71 | 0.003733 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
72 | LV_6007-31_0_1_line_72 |  | 70 | 72 | 0.011251 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
73 | LV_6007-31_0_1_line_73 |  | 71 | 73 | 0.028851 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
74 | LV_6007-31_0_1_line_74 |  | 72 | 74 | 0.04542 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
75 | LV_6007-31_0_1_line_75 |  | 74 | 75 | 0.026635 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
76 | LV_6007-31_0_1_line_76 |  | 74 | 76 | 0.060663 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
77 | LV_6007-31_0_1_line_77 |  | 75 | 77 | 0.012183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
78 | LV_6007-31_0_1_line_78 |  | 76 | 78 | 0.1183 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
79 | LV_6007-31_0_1_line_79 |  | 77 | 84 | 0.024121 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
80 | LV_6007-31_0_1_line_80 |  | 78 | 83 | 0.015442 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
81 | LV_6007-31_0_1_line_81 |  | 78 | 80 | 0.025899 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
82 | LV_6007-31_0_1_line_82 |  | 79 | 80 | 0.09391 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE
83 | LV_6007-31_0_1_line_83 |  | 81 | 82 | 0.043064 | 0.125 | 0.08 | 261 | 0 | 0.364 | 1 | 1 | cs | TRUE

## trafo
| name | std_type | hv_bus | lv_bus | sn_mva | vn_hv_kv | vn_lv_kv | vk_percent | vkr_percent | pfe_kw | i0_percent | shift_degree | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent | tap_step_degree | tap_pos | tap_phase_shifter | parallel | df | in_service
0 | LV_6007-31_0_1_trafo_83 | 0.63 MVA 20/0.4 kV | 85 | 45 | 0.63 | 20 | 0.4 | 6 | 1.206 | 1.65 | 0.2619 | 150 | hv | 0 | -2 | 2 | 2.5 | 0 | 0 | FALSE | 1 | 1 | TRUE

## line_geodata
| x0 | y0 | x1 | y1 | x2 | y2 | x3 | y3 | x4 | y4 | x5 | y5 | x6 | y6 | x7 | y7 | x8 | y8 | x9 | y9 | x10 | y10 | x11 | y11 | x12 | y12 | x13 | y13 | x14 | y14 | x15 | y15 | x16 | y16 | x17 | y17 | x18 | y18 | x19 | y19 | x20 | y20
0 | 2641963.7335 | 1132310.5312 | 2641977.2989 | 1132315.0721 | 2641992.8138 | 1132317.6256
1 | 2642005.1179 | 1132366.014 | 2641992.8138 | 1132317.6256
2 | 2641963.7335 | 1132310.5312 | 2641961.7214 | 1132314.8137
3 | 2641992.577 | 1132424.4339 | 2641992.2157 | 1132414.3818 | 2641990.6046 | 1132398.0289 | 2641990.527 | 1132389.2572 | 2641995.7358 | 1132383.1125 | 2642003.8932 | 1132368.1393 | 2642005.1179 | 1132366.014
4 | 2642005.1179 | 1132366.014 | 2642007.0962 | 1132362.5809 | 2642013.8809 | 1132365.6629 | 2642030.6964 | 1132358.9652 | 2642049.3679 | 1132348.8787 | 2642058.0027 | 1132342.8591
5 | 2641961.7214 | 1132314.8137 | 2641958.9451 | 1132320.7228
6 | 2641992.577 | 1132424.4339 | 2641993.6186 | 1132429.6549 | 2641994.0223 | 1132433.6152 | 2641994.5012 | 1132440.0441 | 2641990.7425 | 1132463.4051
7 | 2642090.2976 | 1132316.7497 | 2642071.2464 | 1132329.3653 | 2642063.3251 | 1132339.1486 | 2642058.0027 | 1132342.8591
8 | 2641957.1143 | 1132324.6193 | 2641958.9451 | 1132320.7228
9 | 2641957.1143 | 1132324.6193 | 2641825.4895 | 1132297.2257
10 | 2641956.5916 | 1132532.6751 | 2641962.222 | 1132537.1807
11 | 2641956.5916 | 1132532.6751 | 2641954.5426 | 1132531.0354 | 2641951.2446 | 1132528.3203
12 | 2641964.6071 | 1132541.8441 | 2641962.222 | 1132537.1807
13 | 2641951.2446 | 1132528.3203 | 2641949.0001 | 1132526.4724 | 2641944.3249 | 1132523.5664
14 | 2641990.6783 | 1132527.1064 | 2641987.5657 | 1132529.6305 | 2641979.8773 | 1132535.8692 | 2641975.7444 | 1132536.7632 | 2641973.3452 | 1132538.5697 | 2641969.0435 | 1132539.3736 | 2641964.6071 | 1132541.8441
15 | 2641964.6071 | 1132541.8441 | 2641962.9879 | 1132558.8415
16 | 2641923.4872 | 1132512.9109 | 2641932.9588 | 1132517.0898 | 2641941.8018 | 1132521.998 | 2641944.3249 | 1132523.5664
17 | 2641990.6783 | 1132527.1064 | 2641985.1205 | 1132507.6517
18 | 2641990.6783 | 1132527.1064 | 2641996.1995 | 1132538.0392 | 2641999.0685 | 1132548.4088 | 2642000.417 | 1132560.4354 | 2642000.737 | 1132562.3317
19 | 2641962.9879 | 1132558.8415 | 2641962.9879 | 1132558.8415 | 2641964.7029 | 1132565.7569 | 2641971.1909 | 1132570.5266 | 2641976.4561 | 1132579.5233 | 2641976.4561 | 1132579.5233
20 | 2641923.4872 | 1132512.9109 | 2641922.3201 | 1132515.7931 | 2641919.6081 | 1132520.5101 | 2641914.5931 | 1132528.7017
21 | 2641923.4872 | 1132512.9109 | 2641913.6062 | 1132507.8065 | 2641910.6258 | 1132505.7181 | 2641908.7846 | 1132503.6487
22 | 2641981.6488 | 1132485.0686 | 2641982.042 | 1132496.8755 | 2641985.1205 | 1132507.6517
23 | 2642000.737 | 1132562.3317 | 2642004.2769 | 1132583.3072 | 2642004.4063 | 1132586.3432
24 | 2641971.1868 | 1132591.2684 | 2641971.5742 | 1132589.6057 | 2641976.4561 | 1132579.5233
25 | 2641914.5931 | 1132528.7017 | 2641914.5931 | 1132528.7017 | 2641908.9636 | 1132536.7001 | 2641898.1384 | 1132548.9758 | 2641894.3857 | 1132553.8857 | 2641890.4229 | 1132560.2393 | 2641886.6461 | 1132568.6396 | 2641885.8423 | 1132570.1125
26 | 2641908.7846 | 1132503.6487 | 2641905.0463 | 1132505.3792 | 2641899.8425 | 1132511.9354 | 2641894.0166 | 1132518.2761 | 2641889.8482 | 1132523.1831 | 2641886.5269 | 1132525.8392 | 2641882.8042 | 1132526.4248 | 2641878.6777 | 1132526.3962 | 2641874.9578 | 1132526.5817 | 2641872.4732 | 1132527.3871 | 2641870.3914 | 1132530.0519 | 2641868.3656 | 1132533.0912
27 | 2641852.8428 | 1132649.4135 | 2641842.9584 | 1132645.9433 | 2641838.0119 | 1132644.2638 | 2641826.5648 | 1132627.4094 | 2641821.1218 | 1132622.9473 | 2641817.1289 | 1132618.0838 | 2641815.3248 | 1132610.6565 | 2641815.7917 | 1132603.2559 | 2641820.3852 | 1132595.8728 | 2641824.4286 | 1132593.4329 | 2641828.3572 | 1132592.0149 | 2641835.1811 | 1132590.5168 | 2641841.3841 | 1132589.7371 | 2641845.927 | 1132589.6685 | 2641853.6703 | 1132589.9333 | 2641863.3754 | 1132590.4118 | 2641870.1831 | 1132590.1366 | 2641873.9172 | 1132587.9058 | 2641877.4506 | 1132584.6285 | 2641881.8348 | 1132577.4552 | 2641885.8423 | 1132570.1125
28 | 2641836.6559 | 1132547.3024 | 2641850.2883 | 1132540.1957 | 2641853.6115 | 1132538.3733 | 2641856.7135 | 1132537.3609 | 2641859.8097 | 1132537.1823 | 2641863.2794 | 1132537.5509 | 2641865.385 | 1132537.0096 | 2641866.8438 | 1132535.3745 | 2641868.3656 | 1132533.0912
29 | 2641990.7425 | 1132463.4051 | 2641990.1286 | 1132467.2203
30 | 2641987.4357 | 1132473.5813 | 2641990.1239 | 1132467.2498 | 2641990.1286 | 1132467.2203
31 | 2641987.4357 | 1132473.5813 | 2641987.1543 | 1132474.2442
32 | 2641981.5132 | 1132480.997 | 2641986.3121 | 1132476.2279 | 2641987.1543 | 1132474.2442
33 | 2641981.5132 | 1132480.997 | 2641981.6488 | 1132485.0686
34 | 2641833.915 | 1132548.7312 | 2641836.6559 | 1132547.3024
35 | 2641971.1868 | 1132591.2684 | 2641967.9436 | 1132605.1885
36 | 2641975.2987 | 1132669.7057 | 2641981.7437 | 1132650.7074 | 2641998.4171 | 1132618.0053
37 | 2641976.5808 | 1132684.6444 | 2641975.2987 | 1132669.7057
38 | 2642004.8992 | 1132597.9079 | 2642001.8109 | 1132611.3488 | 2641998.4171 | 1132618.0053
39 | 2641976.5808 | 1132684.6444 | 2641985.614 | 1132703.1276 | 2641996.6931 | 1132715.2441
40 | 2641976.5808 | 1132684.6444 | 2641963.8256 | 1132708.0893
41 | 2642004.8992 | 1132597.9079 | 2642018.7411 | 1132610.2103
42 | 2642004.8992 | 1132597.9079 | 2642004.4063 | 1132586.3432
43 | 2641996.6931 | 1132715.2441 | 2642002.8599 | 1132720.7786 | 2642012.0855 | 1132722.6436 | 2642026.5613 | 1132727.8802 | 2642033.8086 | 1132734.1226 | 2642074.0902 | 1132763.7622
44 | 2641936.0038 | 1132740.2832 | 2641940.2733 | 1132742.3331 | 2641945.1226 | 1132742.4668 | 2641963.8256 | 1132708.0893
45 | 2642018.7411 | 1132610.2103 | 2642018.7411 | 1132610.2103 | 2642011.6455 | 1132625.6891
46 | 2642074.0902 | 1132763.7622 | 2642014.2299 | 1132886.0085
47 | 2642074.0902 | 1132763.7622 | 2642081.7303 | 1132757.8012 | 2642087.5843 | 1132752.9424
48 | 2641861.0786 | 1133302.3366 | 2641861.0786 | 1133302.3366 | 2641868.0758 | 1133301.2734 | 2641888.2346 | 1133291.6081 | 2641906.148 | 1133276.0576 | 2641913.468 | 1133263.9688 | 2641916.7279 | 1133251.2404 | 2641918.6957 | 1133218.4366
49 | 2641861.0786 | 1133302.3366 | 2641846.3825 | 1133301.3011 | 2641833.8793 | 1133303.7603 | 2641820.5072 | 1133311.6274 | 2641812.1739 | 1133320.0074 | 2641812.1739 | 1133320.0074
50 | 2641918.6957 | 1133218.4366 | 2641918.9736 | 1133213.8036 | 2641923.9521 | 1133201.9098 | 2641955.3745 | 1133169.9558
51 | 2641807.6318 | 1133328.9583 | 2641807.6318 | 1133328.9583 | 2641812.1739 | 1133320.0074
52 | 2641909.1112 | 1133182.9352 | 2641917.9386 | 1133183.2141 | 2641925.8921 | 1133180.8125 | 2641934.5552 | 1133173.769 | 2641943.7379 | 1133161.7487 | 2641948.9264 | 1133159.5391 | 2641953.5843 | 1133160.5831 | 2641956.1453 | 1133163.1577 | 2641956.4356 | 1133166.806 | 2641955.3745 | 1133169.9558 | 2641955.3745 | 1133169.9558
53 | 2641794.8889 | 1133381.6749 | 2641801.6116 | 1133366.8582 | 2641804.9061 | 1133339.0557 | 2641807.6318 | 1133328.9583
54 | 2641909.1112 | 1133182.9352 | 2641908.0255 | 1133182.9009 | 2641892.333 | 1133176.7419
55 | 2641794.8889 | 1133381.6749 | 2641779.0272 | 1133388.9245 | 2641769.9881 | 1133398.089 | 2641763.2156 | 1133410.1039 | 2641754.92 | 1133418.6288
56 | 2641870.6764 | 1133169.7094 | 2641876.2798 | 1133170.4413 | 2641892.333 | 1133176.7419
57 | 2641754.92 | 1133418.6288 | 2641758.5376 | 1133410.3196
58 | 2642071.8591 | 1132913.99 | 2642014.2299 | 1132886.0085
59 | 2642007.4783 | 1132907.0501 | 2642014.2299 | 1132886.0085
60 | 2642007.4783 | 1132907.0501 | 2641983.3864 | 1132897.5224 | 2641978.6057 | 1132897.4442
61 | 2641845.7019 | 1132976.9492 | 2641978.6057 | 1132897.4442
62 | 2641870.6764 | 1133169.7094 | 2641868.0117 | 1133169.3613 | 2641858.5723 | 1133171.7861
63 | 2641842.0904 | 1133191.4761 | 2641848.6093 | 1133178.6762 | 2641858.5723 | 1133171.7861 | 2641858.5723 | 1133171.7861
64 | 2641842.0904 | 1133191.4761 | 2641835.3815 | 1133204.6488
65 | 2641822.854 | 1133229.8695 | 2641824.9079 | 1133225.2138 | 2641835.3815 | 1133204.6488
66 | 2641822.854 | 1133229.8695 | 2641820.9428 | 1133234.202 | 2641819.1024 | 1133235.6527
67 | 2641816.1997 | 1133237.9409 | 2641819.1024 | 1133235.6527
68 | 2641816.1997 | 1133237.9409 | 2641812.7226 | 1133240.6818 | 2641812.7226 | 1133240.6818
69 | 2641812.7226 | 1133240.6818 | 2641801.6499 | 1133244.4183 | 2641793.7563 | 1133245.6311
70 | 2641787.5937 | 1133246.5778 | 2641793.7563 | 1133245.6311
71 | 2641825.9012 | 1133002.8229 | 2641828.1887 | 1132999.8728
72 | 2641825.9012 | 1133002.8229 | 2641819.7401 | 1133010.7687 | 2641819.0237 | 1133011.7268
73 | 2641828.1887 | 1132999.8728 | 2641842.4608 | 1132981.4665 | 2641845.7019 | 1132976.9492
74 | 2641793.8908 | 1133049.4653 | 2641804.4561 | 1133031.2068 | 2641819.0237 | 1133011.7268
75 | 2641793.8908 | 1133049.4653 | 2641802.1119 | 1133050.6894 | 2641810.9395 | 1133054.3746 | 2641818.8042 | 1133058.2275
76 | 2641793.8908 | 1133049.4653 | 2641789.0029 | 1133050.4988 | 2641782.6126 | 1133053.9453 | 2641775.1587 | 1133063.1207 | 2641765.1835 | 1133082.9174 | 2641762.5868 | 1133097.0985
77 | 2641829.7444 | 1133063.587 | 2641818.8042 | 1133058.2275
78 | 2641717.2741 | 1133203.804 | 2641728.4294 | 1133191.4413 | 2641753.7274 | 1133145.4813 | 2641762.5868 | 1133097.0985
79 | 2641820.4947 | 1133041.912 | 2641828.9686 | 1133055.5554 | 2641829.7444 | 1133063.587
80 | 2641706.0931 | 1133193.1214 | 2641712.739 | 1133199.4705 | 2641717.2741 | 1133203.804
81 | 2641702.4646 | 1133224.757 | 2641704.9863 | 1133218.5378 | 2641710.1689 | 1133211.5923 | 2641717.2741 | 1133203.804
82 | 2641702.4646 | 1133224.757 | 2641702.6437 | 1133228.9159 | 2641705.3538 | 1133233.3368 | 2641708.9922 | 1133237.086 | 2641714.4518 | 1133239.0802 | 2641787.5937 | 1133246.5778
83 | 2641739.8131 | 1133393.5117 | 2641744.5781 | 1133391.2879 | 2641751.9347 | 1133387.2144 | 2641756.5777 | 1133387.0463 | 2641759.2435 | 1133390.044 | 2641760.6388 | 1133397.5686 | 2641760.0591 | 1133406.8249 | 2641758.5376 | 1133410.3196

## bus_geodata
| x | y | coords
0 | 2641992.8138 | 1132317.6256
1 | 2641963.7335 | 1132310.5312
2 | 2642005.1179 | 1132366.014
3 | 2641961.7214 | 1132314.8137
4 | 2641992.577 | 1132424.4339
5 | 2642058.0027 | 1132342.8591
6 | 2641958.9451 | 1132320.7228
7 | 2641957.1143 | 1132324.6193
8 | 2641956.5916 | 1132532.6751
9 | 2641962.222 | 1132537.1807
10 | 2641951.2446 | 1132528.3203
11 | 2641964.6071 | 1132541.8441
12 | 2641944.3249 | 1132523.5664
13 | 2641990.6783 | 1132527.1064
14 | 2641962.9879 | 1132558.8415
15 | 2641923.4872 | 1132512.9109
16 | 2641985.1205 | 1132507.6517
17 | 2642000.737 | 1132562.3317
18 | 2641976.4561 | 1132579.5233
19 | 2641914.5931 | 1132528.7017
20 | 2641908.7846 | 1132503.6487
21 | 2641885.8423 | 1132570.1125
22 | 2641868.3656 | 1132533.0912
23 | 2642090.2976 | 1132316.7497
24 | 2641990.7425 | 1132463.4051
25 | 2641825.4895 | 1132297.2257
26 | 2641990.1286 | 1132467.2203
27 | 2641987.4357 | 1132473.5813
28 | 2641987.1543 | 1132474.2442
29 | 2641981.5132 | 1132480.997
30 | 2641981.6488 | 1132485.0686
31 | 2641836.6559 | 1132547.3024
32 | 2641833.915 | 1132548.7312
33 | 2641852.8428 | 1132649.4135
34 | 2641967.9436 | 1132605.1885
35 | 2641971.1868 | 1132591.2684
36 | 2641975.2987 | 1132669.7057
37 | 2641998.4171 | 1132618.0053
38 | 2641976.5808 | 1132684.6444
39 | 2642004.8992 | 1132597.9079
40 | 2641996.6931 | 1132715.2441
41 | 2641963.8256 | 1132708.0893
42 | 2642018.7411 | 1132610.2103
43 | 2642004.4063 | 1132586.3432
44 | 2642074.0902 | 1132763.7622
45 | 2641936.0038 | 1132740.2832
46 | 2642011.6455 | 1132625.6891
47 | 2641861.0786 | 1133302.3366
48 | 2641918.6957 | 1133218.4366
49 | 2641812.1739 | 1133320.0074
50 | 2641955.3745 | 1133169.9558
51 | 2641807.6318 | 1133328.9583
52 | 2641909.1112 | 1133182.9352
53 | 2641794.8889 | 1133381.6749
54 | 2641892.333 | 1133176.7419
55 | 2641754.92 | 1133418.6288
56 | 2642087.5843 | 1132752.9424
57 | 2642014.2299 | 1132886.0085
58 | 2642007.4783 | 1132907.0501
59 | 2641978.6057 | 1132897.4442
60 | 2642071.8591 | 1132913.99
61 | 2641870.6764 | 1133169.7094
62 | 2641858.5723 | 1133171.7861
63 | 2641842.0904 | 1133191.4761
64 | 2641835.3815 | 1133204.6488
65 | 2641822.854 | 1133229.8695
66 | 2641819.1024 | 1133235.6527
67 | 2641816.1997 | 1133237.9409
68 | 2641812.7226 | 1133240.6818
69 | 2641793.7563 | 1133245.6311
70 | 2641825.9012 | 1133002.8229
71 | 2641828.1887 | 1132999.8728
72 | 2641819.0237 | 1133011.7268
73 | 2641845.7019 | 1132976.9492
74 | 2641793.8908 | 1133049.4653
75 | 2641818.8042 | 1133058.2275
76 | 2641762.5868 | 1133097.0985
77 | 2641829.7444 | 1133063.587
78 | 2641717.2741 | 1133203.804
79 | 2641787.5937 | 1133246.5778
80 | 2641702.4646 | 1133224.757
81 | 2641758.5376 | 1133410.3196
82 | 2641739.8131 | 1133393.5117
83 | 2641706.0931 | 1133193.1214
84 | 2641820.4947 | 1133041.912
85 | 2641932.6615 | 1132738.6785

## line_std_types
| c_nf_per_km | r_ohm_per_km | x_ohm_per_km | max_i_ka | type | q_mm2 | alpha | voltage_rating
NAYY 4x50 SE | 210 | 0.642 | 0.083 | 0.142 | cs | 50 | 0.00403 | LV
NAYY 4x120 SE | 264 | 0.225 | 0.08 | 0.242 | cs | 120 | 0.00403 | LV
NAYY 4x150 SE | 261 | 0.208 | 0.08 | 0.27 | cs | 150 | 0.00403 | LV
NA2XS2Y 1x95 RM/25 12/20 kV | 216 | 0.313 | 0.132 | 0.252 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 12/20 kV | 273 | 0.161 | 0.117 | 0.362 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 12/20 kV | 304 | 0.122 | 0.112 | 0.421 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x95 RM/25 6/10 kV | 315 | 0.313 | 0.123 | 0.249 | cs | 95 | 0.00403 | MV
NA2XS2Y 1x185 RM/25 6/10 kV | 406 | 0.161 | 0.11 | 0.358 | cs | 185 | 0.00403 | MV
NA2XS2Y 1x240 RM/25 6/10 kV | 456 | 0.122 | 0.105 | 0.416 | cs | 240 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 12/20 kV | 250 | 0.206 | 0.116 | 0.319 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 12/20 kV | 230 | 0.253 | 0.119 | 0.283 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 12/20 kV | 190 | 0.443 | 0.132 | 0.22 | cs | 70 | 0.00403 | MV
NA2XS2Y 1x150 RM/25 6/10 kV | 360 | 0.206 | 0.11 | 0.315 | cs | 150 | 0.00403 | MV
NA2XS2Y 1x120 RM/25 6/10 kV | 340 | 0.253 | 0.113 | 0.28 | cs | 120 | 0.00403 | MV
NA2XS2Y 1x70 RM/25 6/10 kV | 280 | 0.443 | 0.123 | 0.217 | cs | 70 | 0.00403 | MV
N2XS(FL)2Y 1x120 RM/35 64/110 kV | 112 | 0.153 | 0.166 | 0.366 | cs | 120 | 0.00393 | HV
N2XS(FL)2Y 1x185 RM/35 64/110 kV | 125 | 0.099 | 0.156 | 0.457 | cs | 185 | 0.00393 | HV
N2XS(FL)2Y 1x240 RM/35 64/110 kV | 135 | 0.075 | 0.149 | 0.526 | cs | 240 | 0.00393 | HV
N2XS(FL)2Y 1x300 RM/35 64/110 kV | 144 | 0.06 | 0.144 | 0.588 | cs | 300 | 0.00393 | HV
15-AL1/3-ST1A 0.4 | 11 | 1.8769 | 0.35 | 0.105 | ol | 16 | 0.00403 | LV
24-AL1/4-ST1A 0.4 | 11.25 | 1.2012 | 0.335 | 0.14 | ol | 24 | 0.00403 | LV
48-AL1/8-ST1A 0.4 | 12.2 | 0.5939 | 0.3 | 0.21 | ol | 48 | 0.00403 | LV
94-AL1/15-ST1A 0.4 | 13.2 | 0.306 | 0.29 | 0.35 | ol | 94 | 0.00403 | LV
34-AL1/6-ST1A 10.0 | 9.7 | 0.8342 | 0.36 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 10.0 | 10.1 | 0.5939 | 0.35 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 10.0 | 10.4 | 0.4132 | 0.339 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 10.0 | 10.75 | 0.306 | 0.33 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 10.0 | 11.1 | 0.2376 | 0.323 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 10.0 | 11.25 | 0.194 | 0.315 | 0.47 | ol | 149 | 0.00403 | MV
34-AL1/6-ST1A 20.0 | 9.15 | 0.8342 | 0.382 | 0.17 | ol | 34 | 0.00403 | MV
48-AL1/8-ST1A 20.0 | 9.5 | 0.5939 | 0.372 | 0.21 | ol | 48 | 0.00403 | MV
70-AL1/11-ST1A 20.0 | 9.7 | 0.4132 | 0.36 | 0.29 | ol | 70 | 0.00403 | MV
94-AL1/15-ST1A 20.0 | 10 | 0.306 | 0.35 | 0.35 | ol | 94 | 0.00403 | MV
122-AL1/20-ST1A 20.0 | 10.3 | 0.2376 | 0.344 | 0.41 | ol | 122 | 0.00403 | MV
149-AL1/24-ST1A 20.0 | 10.5 | 0.194 | 0.337 | 0.47 | ol | 149 | 0.00403 | MV
184-AL1/30-ST1A 20.0 | 10.75 | 0.1571 | 0.33 | 0.535 | ol | 184 | 0.00403 | MV
243-AL1/39-ST1A 20.0 | 11 | 0.1188 | 0.32 | 0.645 | ol | 243 | 0.00403 | MV
48-AL1/8-ST1A 110.0 | 8 | 0.5939 | 0.46 | 0.21 | ol | 48 | 0.00403 | HV
70-AL1/11-ST1A 110.0 | 8.4 | 0.4132 | 0.45 | 0.29 | ol | 70 | 0.00403 | HV
94-AL1/15-ST1A 110.0 | 8.65 | 0.306 | 0.44 | 0.35 | ol | 94 | 0.00403 | HV
122-AL1/20-ST1A 110.0 | 8.5 | 0.2376 | 0.43 | 0.41 | ol | 122 | 0.00403 | HV
149-AL1/24-ST1A 110.0 | 8.75 | 0.194 | 0.41 | 0.47 | ol | 149 | 0.00403 | HV
184-AL1/30-ST1A 110.0 | 8.8 | 0.1571 | 0.4 | 0.535 | ol | 184 | 0.00403 | HV
243-AL1/39-ST1A 110.0 | 9 | 0.1188 | 0.39 | 0.645 | ol | 243 | 0.00403 | HV
305-AL1/39-ST1A 110.0 | 9.2 | 0.0949 | 0.38 | 0.74 | ol | 305 | 0.00403 | HV
490-AL1/64-ST1A 110.0 | 9.75 | 0.059 | 0.37 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 110.0 | 9.95 | 0.042 | 0.36 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 220.0 | 10 | 0.059 | 0.285 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 220.0 | 11.7 | 0.042 | 0.275 | 1.15 | ol | 679 | 0.00403 | HV
490-AL1/64-ST1A 380.0 | 11 | 0.059 | 0.253 | 0.96 | ol | 490 | 0.00403 | HV
679-AL1/86-ST1A 380.0 | 14.6 | 0.042 | 0.25 | 1.15 | ol | 679 | 0.00403 | HV

## trafo_std_types
| i0_percent | pfe_kw | vkr_percent | sn_mva | vn_lv_kv | vn_hv_kv | vk_percent | shift_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_degree | tap_step_percent | tap_phase_shifter
160 MVA 380/110 kV | 0.06 | 60 | 0.25 | 160 | 110 | 380 | 12.2 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
100 MVA 220/110 kV | 0.06 | 55 | 0.26 | 100 | 110 | 220 | 12 | 0 | Yy0 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/20 kV | 0.04 | 22 | 0.32 | 63 | 20 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/20 kV | 0.05 | 18 | 0.34 | 40 | 20 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/20 kV | 0.07 | 14 | 0.41 | 25 | 20 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
63 MVA 110/10 kV | 0.04 | 22 | 0.32 | 63 | 10 | 110 | 18 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
40 MVA 110/10 kV | 0.05 | 18 | 0.34 | 40 | 10 | 110 | 16.2 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
25 MVA 110/10 kV | 0.07 | 14 | 0.41 | 25 | 10 | 110 | 12 | 150 | YNd5 | hv | 0 | -9 | 9 | 0 | 1.5 | FALSE
0.25 MVA 20/0.4 kV | 0.32 | 0.8 | 1.44 | 0.25 | 0.4 | 20 | 6 | 150 | Yzn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 20/0.4 kV | 0.3375 | 1.35 | 1.425 | 0.4 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 20/0.4 kV | 0.2619 | 1.65 | 1.206 | 0.63 | 0.4 | 20 | 6 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.25 MVA 10/0.4 kV | 0.24 | 0.6 | 1.2 | 0.25 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.4 MVA 10/0.4 kV | 0.2375 | 0.95 | 1.325 | 0.4 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE
0.63 MVA 10/0.4 kV | 0.1873 | 1.18 | 1.0794 | 0.63 | 0.4 | 10 | 4 | 150 | Dyn5 | hv | 0 | -2 | 2 | 0 | 2.5 | FALSE

## trafo3w_std_types
| sn_hv_mva | sn_mv_mva | sn_lv_mva | vn_hv_kv | vn_mv_kv | vn_lv_kv | vk_hv_percent | vk_mv_percent | vk_lv_percent | vkr_hv_percent | vkr_mv_percent | vkr_lv_percent | pfe_kw | i0_percent | shift_mv_degree | shift_lv_degree | vector_group | tap_side | tap_neutral | tap_min | tap_max | tap_step_percent
63/25/38 MVA 110/20/10 kV | 63 | 25 | 38 | 110 | 20 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2
63/25/38 MVA 110/10/10 kV | 63 | 25 | 38 | 110 | 10 | 10 | 10.4 | 10.4 | 10.4 | 0.28 | 0.32 | 0.35 | 35 | 0.89 | 0 | 0 | YN0yn0yn0 | hv | 0 | -10 | 10 | 1.2

## fuse_std_types
| fuse_type | i_rated_a | t_avg | t_min | t_total | x_avg | x_min | x_total
HV 100A | HV 100A | 100 | 0 | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | 0 | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0] | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0]
HV 10A | HV 10A | 10 | 0 | [10.0, 1675.0, 0.344, 0.156, 0.1, 0.0417, 0.0171, 0.01] | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | 0 | [30.0, 32.0, 35.0, 37.0, 39.0, 50.0, 70.0, 88.0] | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0]
HV 125A | HV 125A | 125 | 0 | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | [10.0, 2.478, 0.426, 0.1, 0.0427, 0.0211, 0.01] | 0 | [375.0, 500.0, 700.0, 925.0, 1200.0, 1500.0, 2341.0] | [750.0, 1000.0, 1500.0, 2200.0, 3000.0, 4000.0, 5765.0]
HV 160A | HV 160A | 160 | 0 | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | [10.0, 2.3, 0.734, 0.274, 0.1, 0.046, 0.0177, 0.01] | 0 | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0] | [960.0, 1300.0, 1700.0, 2200.0, 2996.0, 4000.0, 6000.0, 7946.0]
HV 16A | HV 16A | 16 | 0 | [10.0, 0.352, 0.164, 0.1, 0.0649, 0.0342, 0.01] | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | 0 | [48.0, 60.0, 65.0, 71.0, 80.0, 100.0, 162.0] | [96.0, 110.0, 125.0, 150.0, 168.0, 200.0, 250.0, 398.0]
HV 200A | HV 200A | 200 | 0 | [10.0, 4.267, 1.21, 0.403, 0.1, 0.058, 0.022, 0.01] | [10.0, 3.73, 1.654, 0.328, 0.1, 0.0531, 0.019, 0.01] | 0 | [600.0, 700.0, 900.0, 1150.0, 1665.0, 2000.0, 3000.0, 4313.0] | [1200.0, 1500.0, 1800.0, 2700.0, 3960.0, 5000.0, 7500.0, 10620.0]
HV 20A | HV 20A | 20 | 0 | [10.0, 1.3, 0.3, 0.155, 0.1, 0.0555, 0.023, 0.01] | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | 0 | [60.0, 70.0, 80.0, 87.0, 94.0, 110.0, 150.0, 216.0] | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0]
HV 25A | HV 25A | 25 | 0 | [10.0, 2.512, 0.833, 0.299, 0.1, 0.0372, 0.0223, 0.01] | [10.0, 3.125, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | 0 | [75.0, 82.0, 90.0, 100.0, 124.0, 170.0, 200.0, 289.0] | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0]
HV 31.5A | HV 31.5A | 31.5 | 0 | [10.0, 2.34, 0.722, 0.181, 0.1, 0.055, 0.0296, 0.01] | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | 0 | [95.0, 110.0, 125.0, 150.0, 165.0, 200.0, 250.0, 390.0] | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 960.0]
HV 40A | HV 40A | 40 | 0 | [10.0, 1.3, 0.161, 0.1, 0.0611, 0.0399, 0.0141, 0.01] | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | 0 | [120.0, 150.0, 200.0, 223.0, 260.0, 300.0, 450.0, 532.0] | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0]
HV 50A | HV 50A | 50 | 0 | [10.0, 3.215, 0.597, 0.198, 0.1, 0.0378, 0.022, 0.01] | [10.0, 3.64, 0.854, 0.281, 0.1, 0.0531, 0.022, 0.01] | 0 | [150.0, 170.0, 210.0, 250.0, 294.0, 400.0, 500.0, 711.0] | [300.0, 350.0, 450.0, 550.0, 700.0, 850.0, 1200.0, 1752.0]
HV 6.3A | HV 6.3A | 6.3 | 0 | [10.0, 1.39, 0.344, 0.168, 0.1, 0.056, 0.0263, 0.01] | [10.0, 1.711, 0.516, 0.198, 0.1, 0.0634, 0.0303, 0.01] | 0 | [19.0, 19.5, 20.4, 20.8, 22.0, 25.0, 32.0, 48.0] | [38.0, 40.0, 43.0, 48.0, 53.0, 60.0, 75.0, 118.0]
HV 63A | HV 63A | 63 | 0 | [10.0, 2.84, 0.368, 0.164, 0.1, 0.0621, 0.0378, 0.0195, 0.01] | [10.0, 1.82, 0.344, 0.1, 0.0467, 0.0269, 0.01] | 0 | [189.0, 220.0, 300.0, 350.0, 393.0, 450.0, 530.0, 700.0, 961.0] | [378.0, 500.0, 700.0, 934.0, 1200.0, 1500.0, 2366.0]
HV 80A | HV 80A | 80 | 0 | [10.0, 2.05, 0.369, 0.198, 0.1, 0.051, 0.0298, 0.01] | [10.0, 4.15, 1.03, 0.198, 0.1, 0.051, 0.0172, 0.01] | 0 | [240.0, 300.0, 400.0, 450.0, 530.0, 650.0, 800.0, 1311.0] | [480.0, 550.0, 700.0, 1000.0, 1260.0, 1600.0, 2500.0, 3227.0]
Siemens NH-1-100 | Siemens NH-1-100 | 100 | [5400.0, 2000.0, 400.0, 20.0, 1.0, 0.2, 0.012, 0.004] | 0 | 0 | [150.0, 190.0, 250.0, 430.0, 900.0, 1250.0, 2700.0, 3600.0] | 0 | 0
Siemens NH-1-125 | Siemens NH-1-125 | 125 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [180.0, 400.0, 740.0, 2000.0, 4250.0] | 0 | 0
Siemens NH-1-16 | Siemens NH-1-16 | 16 | [4000.0, 400.0, 2.0, 0.1, 0.04, 0.01] | 0 | 0 | [26.0, 35.0, 75.0, 150.0, 200.0, 300.0] | 0 | 0
Siemens NH-1-160 | Siemens NH-1-160 | 160 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [210.0, 500.0, 900.0, 2300.0, 5000.0] | 0 | 0
Siemens NH-1-25 | Siemens NH-1-25 | 25 | [4000.0, 1000.0, 10.0, 0.2, 0.02, 0.01] | 0 | 0 | [40.0, 50.0, 100.0, 210.0, 400.0, 500.0] | 0 | 0
Siemens NH-1-50 | Siemens NH-1-50 | 50 | [4000.0, 40.0, 4.0, 1.0, 0.02, 0.01] | 0 | 0 | [86.0, 200.0, 300.0, 400.0, 1000.0, 1280.0] | 0 | 0
Siemens NH-1-63 | Siemens NH-1-63 | 63 | [4000.0, 100.0, 10.0, 2.0, 0.04, 0.01] | 0 | 0 | [100.0, 200.0, 300.0, 400.0, 1000.0, 1500.0] | 0 | 0
Siemens NH-1-80 | Siemens NH-1-80 | 80 | [4800.0, 120.0, 7.0, 0.1, 0.01] | 0 | 0 | [150.58, 250.0, 450.0, 1150.0, 2470.0] | 0 | 0
Siemens NH-2-1000 | Siemens NH-2-1000 | 1000 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1900.0, 3500.0, 8400.0, 24000.0, 52000.0] | 0 | 0
Siemens NH-2-200 | Siemens NH-2-200 | 200 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [280.0, 650.0, 1200.0, 3000.0, 7000.0] | 0 | 0
Siemens NH-2-224 | Siemens NH-2-224 | 224 | [4800.0, 120.0, 7.0, 0.2, 0.04, 0.004] | 0 | 0 | [400.0, 750.0, 1453.0, 3025.0, 4315.0, 7600.0] | 0 | 0
Siemens NH-2-250 | Siemens NH-2-250 | 250 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [450.0, 800.0, 1650.0, 4000.0, 8500.0] | 0 | 0
Siemens NH-2-315 | Siemens NH-2-315 | 315 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [550.0, 920.0, 1900.0, 5000.0, 11000.0] | 0 | 0
Siemens NH-2-355 | Siemens NH-2-355 | 355 | [4800.0, 120.0, 6.0, 0.1, 0.004] | 0 | 0 | [650.0, 1116.27, 2350.0, 5840.0, 12790.0] | 0 | 0
Siemens NH-2-400 | Siemens NH-2-400 | 400 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [720.0, 1350.0, 2800.0, 6500.0, 15000.0] | 0 | 0
Siemens NH-2-425 | Siemens NH-2-425 | 425 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [850.0, 1500.0, 3050.0, 7500.0, 16500.0] | 0 | 0
Siemens NH-2-630 | Siemens NH-2-630 | 630 | [4800.0, 120.0, 7.0, 0.1, 0.004] | 0 | 0 | [1200.0, 2000.0, 4800.0, 12000.0, 26000.0] | 0 | 0

## res_bus
| vm_pu | va_degree | p_mw | q_mvar
0 | 0.98611 | -0.26694 | 0.00045274 | 0.00011347
1 | 0.98604 | -0.26837 | 0 | 0
2 | 0.98625 | -0.26417 | 0.00082666 | 0.00020718
3 | 0.98603 | -0.26859 | 0.000514 | 0.00012882
4 | 0.98655 | -0.25838 | 0 | 0
5 | 0.98619 | -0.26549 | 0.00069222 | 0.00017349
6 | 0.98601 | -0.26884 | 0.00047719 | 0.00011959
7 | 0.98601 | -0.26897 | 0.00052033 | 0.00013041
8 | 0.98643 | -0.26069 | 0.0014849 | 0.00037215
9 | 0.98653 | -0.2588 | 0.0014237 | 0.0003568
10 | 0.98635 | -0.26232 | 0.001624 | 0.00040702
11 | 0.9866 | -0.25728 | 0 | 0
12 | 0.98626 | -0.26407 | 0.0017371 | 0.00043537
13 | 0.98726 | -0.24443 | 0 | 0
14 | 0.98649 | -0.25955 | 0.0021328 | 0.00053454
15 | 0.98604 | -0.2682 | 0 | 0
16 | 0.98707 | -0.24827 | 0.0022984 | 0.00057604
17 | 0.98843 | -0.22183 | 0.0021742 | 0.0005449
18 | 0.98636 | -0.26198 | 0.0012852 | 0.0003221
19 | 0.98595 | -0.26998 | 0.0018741 | 0.00046968
20 | 0.98597 | -0.26957 | 0 | 0
21 | 0.98579 | -0.27326 | 0.0020744 | 0.00051988
22 | 0.98576 | -0.27371 | 0.0014628 | 0.00036661
23 | 0.98617 | -0.26588 | 0.00051415 | 0.00012886
24 | 0.98674 | -0.25475 | 0.00050278 | 0.00012601
25 | 0.98587 | -0.2717 | 0.0011308 | 0.0002834
26 | 0.98676 | -0.25436 | 0.00078499 | 0.00019674
27 | 0.9868 | -0.25357 | 0.00053589 | 0.00013431
28 | 0.9868 | -0.25348 | 0.00067214 | 0.00016845
29 | 0.98686 | -0.25226 | 0 | 0
30 | 0.98689 | -0.2517 | 0.00068893 | 0.00017266
31 | 0.98567 | -0.27558 | 0.0012592 | 0.00031559
32 | 0.98566 | -0.27567 | 0.0016294 | 0.00040836
33 | 0.98557 | -0.27738 | 0.0015268 | 0.00038264
34 | 0.98629 | -0.2635 | 0.0023034 | 0.00057729
35 | 0.98632 | -0.26291 | 0.0017023 | 0.00042665
36 | 0.9933 | -0.12753 | 0 | 0
37 | 0.99065 | -0.17877 | 0.0016218 | 0.00040645
38 | 0.994 | -0.11404 | 0 | 0
39 | 0.98968 | -0.19742 | 0 | 0
40 | 0.99285 | -0.13593 | 0 | 0
41 | 0.99608 | -0.074343 | 0.0027058 | 0.00067815
42 | 0.98956 | -0.19983 | 0.0023991 | 0.00060126
43 | 0.98924 | -0.20608 | 0.0056941 | 0.0014271
44 | 0.98997 | -0.19103 | 0 | 0
45 | 1 | 0 | -0.090076 | -0.022639
46 | 0.98948 | -0.20131 | 0.0049001 | 0.0012281
47 | 0.97113 | -0.55847 | 0.0012786 | 0.00032046
48 | 0.97155 | -0.55015 | 0.0010716 | 0.00026858
49 | 0.97099 | -0.56119 | 0.00067004 | 0.00016793
50 | 0.97184 | -0.54435 | 0.0015206 | 0.0003811
51 | 0.97097 | -0.56157 | 0.00073441 | 0.00018406
52 | 0.97224 | -0.53653 | 0.0010606 | 0.00026582
53 | 0.97091 | -0.56287 | 0 | 0
54 | 0.97236 | -0.53401 | 0.0014422 | 0.00036145
55 | 0.97084 | -0.5642 | 0 | 0
56 | 0.98995 | -0.19141 | 0.0012203 | 0.00030583
57 | 0.98589 | -0.26956 | 0 | 0
58 | 0.98533 | -0.28055 | 0.0010973 | 0.00027501
59 | 0.98457 | -0.29523 | 0.0016166 | 0.00040516
60 | 0.98563 | -0.2748 | 0.0045774 | 0.0011472
61 | 0.97256 | -0.53018 | 0.00090382 | 0.00022652
62 | 0.97267 | -0.52789 | 0.00098562 | 0.00024702
63 | 0.97294 | -0.52255 | 0.0015385 | 0.00038559
64 | 0.97311 | -0.51914 | 0.00064127 | 0.00016072
65 | 0.97346 | -0.51233 | 0.00063575 | 0.00015933
66 | 0.97355 | -0.51054 | 0.00080304 | 0.00020126
67 | 0.9736 | -0.50954 | 0.00065722 | 0.00016472
68 | 0.97366 | -0.5083 | 0.00079461 | 0.00019915
69 | 0.97396 | -0.50251 | 0.00070797 | 0.00017743
70 | 0.98025 | -0.3791 | 0.00081376 | 0.00020395
71 | 0.98033 | -0.37755 | 0.00090276 | 0.00022625
72 | 0.98002 | -0.38361 | 0.00064092 | 0.00016063
73 | 0.98097 | -0.36511 | 0.0012139 | 0.00030422
74 | 0.97911 | -0.40129 | 0 | 0
75 | 0.97906 | -0.40224 | 0.00097211 | 0.00024363
76 | 0.97801 | -0.42278 | 0.0011821 | 0.00029627
77 | 0.97905 | -0.40246 | 0 | 0
78 | 0.976 | -0.46226 | 0 | 0
79 | 0.97405 | -0.50059 | 0.00070185 | 0.0001759
80 | 0.97558 | -0.47053 | 0 | 0
81 | 0.97083 | -0.56441 | 0.00069937 | 0.00017528
82 | 0.97081 | -0.56487 | 0.00058108 | 0.00014563
83 | 0.97599 | -0.46249 | 0.00082174 | 0.00020595
84 | 0.97903 | -0.4029 | 0.00099275 | 0.00024881
85 | 0.99998 | 149.9956 | 0 | 0

## res_line
| p_from_mw | q_from_mvar | p_to_mw | q_to_mvar | pl_mw | ql_mvar | i_from_ka | i_to_ka | i_ka | vm_from_pu | va_from_degree | vm_to_pu | va_to_degree | loading_percent
0 | 0.0026427 | 0.00066018 | -0.0026425 | -0.00066045 | 1.7901e-07 | -2.685e-07 | 0.003987 | 0.0039871 | 0.0039871 | 0.98611 | -0.26694 | 0.98604 | -0.26837 | 1.0954
1 | -0.0030954 | -0.00077365 | 0.0030958 | 0.00077327 | 4.0834e-07 | -3.7571e-07 | 0.0046702 | 0.0046699 | 0.0046702 | 0.98611 | -0.26694 | 0.98625 | -0.26417 | 1.283
2 | 0.0026425 | 0.00066045 | -0.0026425 | -0.00066049 | 2.8208e-08 | -4.2301e-08 | 0.0039871 | 0.0039872 | 0.0039872 | 0.98604 | -0.26837 | 0.98603 | -0.26859 | 1.0954
3 | -0.005129 | -0.0012815 | 0.0051304 | 0.0012816 | 1.4102e-06 | 1.0059e-07 | 0.007737 | 0.0077367 | 0.007737 | 0.98625 | -0.26417 | 0.98655 | -0.25838 | 2.1255
4 | 0.0012065 | 0.00030108 | -0.0012064 | -0.00030182 | 7.6091e-08 | -7.3302e-07 | 0.0018198 | 0.0018201 | 0.0018201 | 0.98625 | -0.26417 | 0.98619 | -0.26549 | 0.50002
5 | 0.0021285 | 0.00053167 | -0.0021285 | -0.00053174 | 2.5251e-08 | -6.7115e-08 | 0.0032115 | 0.0032115 | 0.0032115 | 0.98603 | -0.26859 | 0.98601 | -0.26884 | 0.88228
6 | -0.0051304 | -0.0012816 | 0.0051313 | 0.0012817 | 8.8465e-07 | 6.2826e-08 | 0.0077367 | 0.0077365 | 0.0077367 | 0.98655 | -0.25838 | 0.98674 | -0.25475 | 2.1255
7 | 0.00051416 | 0.00012833 | -0.00051415 | -0.00012886 | 9.4602e-09 | -5.2888e-07 | 0.00077561 | 0.0007758 | 0.0007758 | 0.98619 | -0.26549 | 0.98617 | -0.26588 | 0.21313
8 | 0.0016513 | 0.00041214 | -0.0016513 | -0.00041219 | 1.0021e-08 | -4.8498e-08 | 0.0024914 | 0.0024914 | 0.0024914 | 0.98601 | -0.26884 | 0.98601 | -0.26897 | 0.68445
9 | 0.0011309 | 0.00028178 | -0.0011308 | -0.0002834 | 1.4681e-07 | -1.6206e-06 | 0.0017062 | 0.0017068 | 0.0017068 | 0.98601 | -0.26897 | 0.98587 | -0.2717 | 0.46889
10 | -0.014679 | -0.0036769 | 0.014681 | 0.0036776 | 1.3259e-06 | 7.5649e-07 | 0.022143 | 0.022143 | 0.022143 | 0.98643 | -0.26069 | 0.98653 | -0.2588 | 6.0832
11 | 0.013194 | 0.0033047 | -0.013193 | -0.0033042 | 1.0244e-06 | 5.6759e-07 | 0.019903 | 0.019903 | 0.019903 | 0.98643 | -0.26069 | 0.98635 | -0.26232 | 5.4678
12 | -0.016104 | -0.0040344 | 0.016105 | 0.0040351 | 1.1589e-06 | 6.7481e-07 | 0.02429 | 0.02429 | 0.02429 | 0.98653 | -0.2588 | 0.9866 | -0.25728 | 6.6731
13 | 0.011569 | 0.0028971 | -0.011568 | -0.0028966 | 9.6086e-07 | 5.076e-07 | 0.017453 | 0.017453 | 0.017453 | 0.98635 | -0.26232 | 0.98626 | -0.26407 | 4.7947
14 | -0.023531 | -0.0058959 | 0.023545 | 0.0059047 | 1.442e-05 | 8.8389e-06 | 0.035489 | 0.035489 | 0.035489 | 0.9866 | -0.25728 | 0.98726 | -0.24443 | 9.7498
15 | 0.0074254 | 0.0018607 | -0.0074246 | -0.0018604 | 8.0306e-07 | 2.9594e-07 | 0.011199 | 0.011199 | 0.011199 | 0.9866 | -0.25728 | 0.98649 | -0.25955 | 3.0767
16 | 0.0098312 | 0.0024613 | -0.0098293 | -0.0024603 | 1.9335e-06 | 9.3839e-07 | 0.014832 | 0.014832 | 0.014832 | 0.98626 | -0.26407 | 0.98604 | -0.2682 | 4.0747
17 | 0.010619 | 0.0026578 | -0.010617 | -0.0026568 | 1.9432e-06 | 9.8498e-07 | 0.016003 | 0.016004 | 0.016004 | 0.98726 | -0.24443 | 0.98707 | -0.24827 | 4.3966
18 | -0.034164 | -0.0085625 | 0.034201 | 0.0085856 | 3.6821e-05 | 2.3091e-05 | 0.051492 | 0.051492 | 0.051492 | 0.98726 | -0.24443 | 0.98843 | -0.22183 | 14.1463
19 | 0.0052918 | 0.0013259 | -0.0052912 | -0.0013258 | 6.1169e-07 | 6.4662e-08 | 0.007982 | 0.0079821 | 0.0079821 | 0.98649 | -0.25955 | 0.98636 | -0.26198 | 2.1929
20 | 0.0054765 | 0.0013703 | -0.005476 | -0.0013702 | 4.6493e-07 | 6.599e-08 | 0.0082636 | 0.0082637 | 0.0082637 | 0.98604 | -0.2682 | 0.98595 | -0.26998 | 2.2703
21 | 0.0043528 | 0.0010901 | -0.0043525 | -0.0010901 | 2.8305e-07 | -4.1992e-08 | 0.0065684 | 0.0065685 | 0.0065685 | 0.98604 | -0.2682 | 0.98597 | -0.26957 | 1.8045
22 | 0.0083184 | 0.0020808 | -0.008317 | -0.0020802 | 1.3572e-06 | 5.7443e-07 | 0.012539 | 0.012539 | 0.012539 | 0.98707 | -0.24827 | 0.98689 | -0.2517 | 3.4447
23 | -0.036375 | -0.0091305 | 0.036402 | 0.0091477 | 2.7343e-05 | 1.7188e-05 | 0.054765 | 0.054765 | 0.054765 | 0.98843 | -0.22183 | 0.98924 | -0.20608 | 15.0454
24 | 0.004006 | 0.0010037 | -0.0040058 | -0.0010038 | 1.768e-07 | -5.1613e-08 | 0.0060433 | 0.0060434 | 0.0060434 | 0.98636 | -0.26198 | 0.98632 | -0.26291 | 1.6603
25 | 0.003602 | 0.00090052 | -0.0036014 | -0.0009008 | 5.6176e-07 | -2.8701e-07 | 0.0054354 | 0.0054356 | 0.0054356 | 0.98595 | -0.26998 | 0.98579 | -0.27326 | 1.4933
26 | 0.0043525 | 0.0010901 | -0.0043516 | -0.0010902 | 8.5846e-07 | -1.2713e-07 | 0.0065685 | 0.0065687 | 0.0065687 | 0.98597 | -0.26957 | 0.98576 | -0.27371 | 1.8046
27 | 0.0015271 | 0.00038092 | -0.0015268 | -0.00038264 | 2.9891e-07 | -1.7214e-06 | 0.0023044 | 0.0023051 | 0.0023051 | 0.98579 | -0.27326 | 0.98557 | -0.27738 | 0.63327
28 | 0.0028889 | 0.00072362 | -0.0028886 | -0.00072391 | 2.5761e-07 | -2.9564e-07 | 0.0043606 | 0.0043608 | 0.0043608 | 0.98576 | -0.27371 | 0.98567 | -0.27558 | 1.198
29 | -0.005634 | -0.0014077 | 0.0056342 | 0.0014077 | 1.0457e-07 | 1.7562e-08 | 0.0084947 | 0.0084947 | 0.0084947 | 0.98674 | -0.25475 | 0.98676 | -0.25436 | 2.3337
30 | -0.0064191 | -0.0016045 | 0.0064194 | 0.0016045 | 2.4267e-07 | 6.7058e-08 | 0.0096785 | 0.0096784 | 0.0096785 | 0.98676 | -0.25436 | 0.9868 | -0.25357 | 2.6589
31 | -0.0069553 | -0.0017388 | 0.0069553 | 0.0017388 | 2.97e-08 | 9.807e-09 | 0.010487 | 0.010487 | 0.010487 | 0.9868 | -0.25357 | 0.9868 | -0.25348 | 2.8809
32 | -0.0076274 | -0.0019073 | 0.0076279 | 0.0019075 | 4.4241e-07 | 1.6917e-07 | 0.0115 | 0.0115 | 0.0115 | 0.9868 | -0.25348 | 0.98686 | -0.25226 | 3.1594
33 | -0.0076279 | -0.0019075 | 0.0076281 | 0.0019075 | 2.0204e-07 | 7.7251e-08 | 0.0115 | 0.0115 | 0.0115 | 0.98686 | -0.25226 | 0.98689 | -0.2517 | 3.1593
34 | 0.0016294 | 0.00040833 | -0.0016294 | -0.00040836 | 7.0133e-09 | -3.4908e-08 | 0.0024598 | 0.0024598 | 0.0024598 | 0.98567 | -0.27558 | 0.98566 | -0.27567 | 0.67577
35 | -0.0023034 | -0.00057729 | 0.0023035 | 0.00057715 | 6.4728e-08 | -1.4098e-07 | 0.0034752 | 0.0034751 | 0.0034752 | 0.98629 | -0.2635 | 0.98632 | -0.26291 | 0.95472
36 | 0.051205 | 0.012929 | -0.05108 | -0.01285 | 0.00012538 | 7.9507e-05 | 0.076742 | 0.076742 | 0.076742 | 0.9933 | -0.12753 | 0.99065 | -0.17877 | 21.0831
37 | -0.051205 | -0.012929 | 0.051238 | 0.01295 | 3.3121e-05 | 2.1003e-05 | 0.076742 | 0.076742 | 0.076742 | 0.9933 | -0.12753 | 0.994 | -0.11404 | 21.083
38 | 0.049458 | 0.012443 | -0.049414 | -0.012415 | 4.4026e-05 | 2.7903e-05 | 0.074306 | 0.074307 | 0.074307 | 0.99065 | -0.17877 | 0.98968 | -0.19742 | 20.4139
39 | 0.034002 | 0.0087041 | -0.033966 | -0.0086815 | 3.6004e-05 | 2.2564e-05 | 0.050965 | 0.050966 | 0.050966 | 0.994 | -0.11404 | 0.99285 | -0.13593 | 14.0015
40 | -0.08524 | -0.021654 | 0.085403 | 0.021758 | 0.00016323 | 0.00010412 | 0.12771 | 0.12771 | 0.12771 | 0.994 | -0.11404 | 0.99608 | -0.074343 | 35.0844
41 | 0.0073004 | 0.0018297 | -0.0072995 | -0.0018294 | 8.3668e-07 | 2.9754e-07 | 0.010976 | 0.010976 | 0.010976 | 0.98968 | -0.19742 | 0.98956 | -0.19983 | 3.0155
42 | 0.042114 | 0.010586 | -0.042096 | -0.010575 | 1.7409e-05 | 1.0993e-05 | 0.06333 | 0.06333 | 0.06333 | 0.98968 | -0.19742 | 0.98924 | -0.20608 | 17.3984
43 | 0.033966 | 0.0086815 | -0.033876 | -0.008625 | 9.0265e-05 | 5.6575e-05 | 0.050966 | 0.050966 | 0.050966 | 0.99285 | -0.13593 | 0.98997 | -0.19103 | 14.0017
44 | -0.088109 | -0.022437 | 0.088426 | 0.022639 | 0.00031715 | 0.00020234 | 0.13175 | 0.13175 | 0.13175 | 0.99608 | -0.074343 | 1 | 0 | 36.1949
45 | 0.0049005 | 0.0012281 | -0.0049001 | -0.0012281 | 3.4673e-07 | 3.1757e-09 | 0.0073689 | 0.007369 | 0.007369 | 0.98956 | -0.19983 | 0.98948 | -0.20131 | 2.0244
46 | 0.032655 | 0.0083193 | -0.032532 | -0.0082422 | 0.00012322 | 7.7116e-05 | 0.049132 | 0.049133 | 0.049133 | 0.98997 | -0.19103 | 0.98589 | -0.26956 | 13.498
47 | 0.0012203 | 0.00030562 | -0.0012203 | -0.00030583 | 2.1822e-08 | -2.0844e-07 | 0.0018341 | 0.0018342 | 0.0018342 | 0.98997 | -0.19103 | 0.98995 | -0.19141 | 0.5039
48 | -0.0039641 | -0.00099091 | 0.0039657 | 0.00099051 | 1.5668e-06 | -3.9957e-07 | 0.0060731 | 0.0060726 | 0.0060731 | 0.97113 | -0.55847 | 0.97155 | -0.55015 | 1.6684
49 | 0.0026855 | 0.00067045 | -0.0026851 | -0.00067091 | 3.4786e-07 | -4.554e-07 | 0.0041139 | 0.0041141 | 0.0041141 | 0.97113 | -0.55847 | 0.97099 | -0.56119 | 1.1303
50 | -0.0050373 | -0.0012591 | 0.0050387 | 0.0012592 | 1.3913e-06 | 1.1806e-07 | 0.0077139 | 0.0077136 | 0.0077139 | 0.97155 | -0.55015 | 0.97184 | -0.54435 | 2.1192
51 | 0.0020151 | 0.00050298 | -0.0020151 | -0.00050308 | 3.5878e-08 | -1.0119e-07 | 0.0030873 | 0.0030874 | 0.0030874 | 0.97099 | -0.56119 | 0.97097 | -0.56157 | 0.84818
52 | -0.0065593 | -0.0016403 | 0.0065618 | 0.0016411 | 2.4375e-06 | 7.6094e-07 | 0.010042 | 0.010042 | 0.010042 | 0.97184 | -0.54435 | 0.97224 | -0.53653 | 2.7588
53 | 0.0012806 | 0.00031902 | -0.0012806 | -0.00031964 | 7.9e-08 | -6.2629e-07 | 0.0019619 | 0.0019621 | 0.0019621 | 0.97097 | -0.56157 | 0.97091 | -0.56287 | 0.53904
54 | -0.0076224 | -0.0019069 | 0.0076233 | 0.0019072 | 9.1561e-07 | 3.6344e-07 | 0.011665 | 0.011665 | 0.011665 | 0.97224 | -0.53653 | 0.97236 | -0.53401 | 3.2046
55 | 0.0012806 | 0.00031964 | -0.0012805 | -0.00032028 | 8.0745e-08 | -6.3985e-07 | 0.0019621 | 0.0019624 | 0.0019624 | 0.97091 | -0.56287 | 0.97084 | -0.5642 | 0.53911
56 | -0.0090655 | -0.0022687 | 0.0090672 | 0.0022695 | 1.6522e-06 | 7.7334e-07 | 0.013872 | 0.013872 | 0.013872 | 0.97236 | -0.53401 | 0.97256 | -0.53018 | 3.8109
57 | 0.0012805 | 0.00032028 | -0.0012805 | -0.00032039 | 1.3087e-08 | -1.0368e-07 | 0.0019624 | 0.0019624 | 0.0019624 | 0.97084 | -0.5642 | 0.97083 | -0.56441 | 0.53912
58 | 0.0045785 | 0.0011471 | -0.0045774 | -0.0011472 | 1.1445e-06 | -8.2292e-08 | 0.0069102 | 0.0069105 | 0.0069105 | 0.98589 | -0.26956 | 0.98563 | -0.2748 | 1.8985
59 | 0.027954 | 0.0070951 | -0.027939 | -0.0070859 | 1.4773e-05 | 9.1731e-06 | 0.042222 | 0.042222 | 0.042222 | 0.98589 | -0.26956 | 0.98533 | -0.28055 | 11.5996
60 | 0.026841 | 0.0068109 | -0.026823 | -0.0067992 | 1.8938e-05 | 1.1729e-05 | 0.040565 | 0.040566 | 0.040566 | 0.98533 | -0.28055 | 0.98457 | -0.29523 | 11.1444
61 | 0.025206 | 0.0063941 | -0.025122 | -0.006342 | 8.4404e-05 | 5.2056e-05 | 0.038122 | 0.038123 | 0.038123 | 0.98457 | -0.29523 | 0.98097 | -0.36511 | 10.4733
62 | -0.009971 | -0.002496 | 0.0099721 | 0.0024965 | 1.085e-06 | 5.4007e-07 | 0.015255 | 0.015255 | 0.015255 | 0.97256 | -0.53018 | 0.97267 | -0.52789 | 4.1908
63 | -0.010958 | -0.0027436 | 0.01096 | 0.002745 | 2.7898e-06 | 1.4568e-06 | 0.016762 | 0.016762 | 0.016762 | 0.97267 | -0.52789 | 0.97294 | -0.52255 | 4.605
64 | -0.012499 | -0.0031306 | 0.012501 | 0.0031317 | 2.0256e-06 | 1.1127e-06 | 0.019115 | 0.019115 | 0.019115 | 0.97294 | -0.52255 | 0.97311 | -0.51914 | 5.2514
65 | -0.013142 | -0.0032924 | 0.013147 | 0.0032948 | 4.2656e-06 | 2.3799e-06 | 0.020096 | 0.020096 | 0.020096 | 0.97311 | -0.51914 | 0.97346 | -0.51233 | 5.5208
66 | -0.013782 | -0.0034541 | 0.013784 | 0.0034548 | 1.1782e-06 | 6.6602e-07 | 0.021067 | 0.021067 | 0.021067 | 0.97346 | -0.51233 | 0.97355 | -0.51054 | 5.7878
67 | -0.014587 | -0.0036561 | 0.014587 | 0.0036565 | 6.8894e-07 | 3.9496e-07 | 0.022295 | 0.022295 | 0.022295 | 0.97355 | -0.51054 | 0.9736 | -0.50954 | 6.125
68 | -0.015244 | -0.0038212 | 0.015245 | 0.0038217 | 9.0133e-07 | 5.2179e-07 | 0.023299 | 0.023299 | 0.023299 | 0.9736 | -0.50954 | 0.97366 | -0.5083 | 6.4009
69 | -0.01604 | -0.0040209 | 0.016044 | 0.0040234 | 4.433e-06 | 2.5924e-06 | 0.024514 | 0.024514 | 0.024514 | 0.97366 | -0.5083 | 0.97396 | -0.50251 | 6.7345
70 | -0.016752 | -0.0042009 | 0.016754 | 0.0042018 | 1.5317e-06 | 9.027e-07 | 0.025595 | 0.025595 | 0.025595 | 0.97396 | -0.50251 | 0.97405 | -0.50059 | 7.0316
71 | -0.022989 | -0.0058017 | 0.022991 | 0.0058028 | 1.7062e-06 | 1.0449e-06 | 0.034912 | 0.034912 | 0.034912 | 0.98025 | -0.3791 | 0.98033 | -0.37755 | 9.5911
72 | 0.022175 | 0.0055978 | -0.02217 | -0.0055949 | 4.7849e-06 | 2.9205e-06 | 0.033676 | 0.033676 | 0.033676 | 0.98025 | -0.3791 | 0.98002 | -0.38361 | 9.2517
73 | -0.023893 | -0.006029 | 0.023908 | 0.0060378 | 1.4242e-05 | 8.7509e-06 | 0.036282 | 0.036282 | 0.036282 | 0.98033 | -0.37755 | 0.98097 | -0.36511 | 9.9675
74 | 0.021529 | 0.0054342 | -0.021511 | -0.0054231 | 1.8216e-05 | 1.1087e-05 | 0.032703 | 0.032703 | 0.032703 | 0.98002 | -0.38361 | 0.97911 | -0.40129 | 8.9844
75 | 0.001965 | 0.00049173 | -0.0019649 | -0.00049201 | 8.9063e-08 | -2.7798e-07 | 0.002986 | 0.0029862 | 0.0029862 | 0.97911 | -0.40129 | 0.97906 | -0.40224 | 0.82037
76 | 0.019546 | 0.0049314 | -0.019526 | -0.0049193 | 2.009e-05 | 1.2095e-05 | 0.029717 | 0.029718 | 0.029718 | 0.97911 | -0.40129 | 0.97801 | -0.42278 | 8.1642
77 | 0.00099278 | 0.00024837 | -0.00099277 | -0.00024852 | 1.0399e-08 | -1.4655e-07 | 0.0015087 | 0.0015088 | 0.0015088 | 0.97906 | -0.40224 | 0.97905 | -0.40246 | 0.4145
78 | 0.018344 | 0.004623 | -0.018309 | -0.0046024 | 3.458e-05 | 2.065e-05 | 0.027919 | 0.02792 | 0.02792 | 0.97801 | -0.42278 | 0.976 | -0.46226 | 7.6702
79 | 0.00099277 | 0.00024852 | -0.00099275 | -0.00024881 | 2.0592e-08 | -2.9015e-07 | 0.0015088 | 0.0015089 | 0.0015089 | 0.97905 | -0.40246 | 0.97903 | -0.4029 | 0.41452
80 | 0.00082175 | 0.00020576 | -0.00082174 | -0.00020595 | 9.0889e-09 | -1.8716e-07 | 0.0012528 | 0.0012529 | 0.0012529 | 0.976 | -0.46226 | 0.97599 | -0.46249 | 0.34419
81 | 0.017488 | 0.0043966 | -0.017481 | -0.0043925 | 6.9065e-06 | 4.0966e-06 | 0.026667 | 0.026667 | 0.026667 | 0.976 | -0.46226 | 0.97558 | -0.47053 | 7.3261
82 | -0.017456 | -0.0043777 | 0.017481 | 0.0043925 | 2.5044e-05 | 1.4857e-05 | 0.026667 | 0.026667 | 0.026667 | 0.97405 | -0.50059 | 0.97558 | -0.47053 | 7.3262
83 | 0.0005811 | 0.00014511 | -0.00058108 | -0.00014563 | 1.2808e-08 | -5.2428e-07 | 0.00089047 | 0.00089067 | 0.00089067 | 0.97083 | -0.56441 | 0.97081 | -0.56487 | 0.24469

## res_trafo
| p_hv_mw | q_hv_mvar | p_lv_mw | q_lv_mvar | pl_mw | ql_mvar | i_hv_ka | i_lv_ka | vm_hv_pu | va_hv_degree | vm_lv_pu | va_lv_degree | loading_percent
0 | -1.2729e-15 | -1.3162e-15 | 0.00165 | 1.2699e-07 | 0.00165 | 1.2699e-07 | 5.2857e-17 | 0.0023815 | 0.99998 | 149.9956 | 1 | 0 | 0.2619

## res_ext_grid
| p_mw | q_mvar
0 | 0.092478 | 0.023241

## res_load
| p_mw | q_mvar
0 | 0.00045274 | 0.00011347
1 | 0.00082666 | 0.00020718
2 | 0.000514 | 0.00012882
3 | 0.00069222 | 0.00017349
4 | 0.00047719 | 0.00011959
5 | 0.00052033 | 0.00013041
6 | 0.0014849 | 0.00037215
7 | 0.0014237 | 0.0003568
8 | 0.001624 | 0.00040702
9 | 0.0017371 | 0.00043537
10 | 0.0021328 | 0.00053454
11 | 0.0022984 | 0.00057604
12 | 0.0021742 | 0.0005449
13 | 0.0012852 | 0.0003221
14 | 0.0018741 | 0.00046968
15 | 0.0020744 | 0.00051988
16 | 0.0014628 | 0.00036661
17 | 0.00051415 | 0.00012886
18 | 0.00050278 | 0.00012601
19 | 0.0011308 | 0.0002834
20 | 0.00078499 | 0.00019674
21 | 0.00053589 | 0.00013431
22 | 0.00067214 | 0.00016845
23 | 0.00068893 | 0.00017266
24 | 0.0012592 | 0.00031559
25 | 0.0016294 | 0.00040836
26 | 0.0015268 | 0.00038264
27 | 0.0023034 | 0.00057729
28 | 0.0017023 | 0.00042665
29 | 0.0016218 | 0.00040645
30 | 0.0027058 | 0.00067815
31 | 0.0023991 | 0.00060126
32 | 0.0056941 | 0.0014271
33 | 0.0024019 | 0.00060198
34 | 0.0049001 | 0.0012281
35 | 0.0012786 | 0.00032046
36 | 0.0010716 | 0.00026858
37 | 0.00067004 | 0.00016793
38 | 0.0015206 | 0.0003811
39 | 0.00073441 | 0.00018406
40 | 0.0010606 | 0.00026582
41 | 0.0014422 | 0.00036145
42 | 0.0012203 | 0.00030583
43 | 0.0010973 | 0.00027501
44 | 0.0016166 | 0.00040516
45 | 0.0045774 | 0.0011472
46 | 0.00090382 | 0.00022652
47 | 0.00098562 | 0.00024702
48 | 0.0015385 | 0.00038559
49 | 0.00064127 | 0.00016072
50 | 0.00063575 | 0.00015933
51 | 0.00080304 | 0.00020126
52 | 0.00065722 | 0.00016472
53 | 0.00079461 | 0.00019915
54 | 0.00070797 | 0.00017743
55 | 0.00081376 | 0.00020395
56 | 0.00090276 | 0.00022625
57 | 0.00064092 | 0.00016063
58 | 0.0012139 | 0.00030422
59 | 0.00097211 | 0.00024363
60 | 0.0011821 | 0.00029627
61 | 0.00070185 | 0.0001759
62 | 0.00069937 | 0.00017528
63 | 0.00058108 | 0.00014563
64 | 0.00082174 | 0.00020595
65 | 0.00099275 | 0.00024881

## dtypes
| element | column | dtype
0 | bus | name | object
1 | bus | vn_kv | float64
2 | bus | type | object
3 | bus | zone | object
4 | bus | in_service | bool
5 | load | name | object
6 | load | bus | uint32
7 | load | p_mw | float64
8 | load | q_mvar | float64
9 | load | const_z_percent | float64
10 | load | const_i_percent | float64
11 | load | sn_mva | float64
12 | load | scaling | float64
13 | load | in_service | bool
14 | load | type | object
15 | ext_grid | name | object
16 | ext_grid | bus | uint32
17 | ext_grid | vm_pu | float64
18 | ext_grid | va_degree | float64
19 | ext_grid | slack_weight | float64
20 | ext_grid | in_service | bool
21 | line | name | object
22 | line | std_type | object
23 | line | from_bus | uint32
24 | line | to_bus | uint32
25 | line | length_km | float64
26 | line | r_ohm_per_km | float64
27 | line | x_ohm_per_km | float64
28 | line | c_nf_per_km | float64
29 | line | g_us_per_km | float64
30 | line | max_i_ka | float64
31 | line | df | float64
32 | line | parallel | uint32
33 | line | type | object
34 | line | in_service | bool
35 | trafo | name | object
36 | trafo | std_type | object
37 | trafo | hv_bus | uint32
38 | trafo | lv_bus | uint32
39 | trafo | sn_mva | float64
40 | trafo | vn_hv_kv | float64
41 | trafo | vn_lv_kv | float64
42 | trafo | vk_percent | float64
43 | trafo | vkr_percent | float64
44 | trafo | pfe_kw | float64
45 | trafo | i0_percent | float64
46 | trafo | shift_degree | float64
47 | trafo | tap_side | object
48 | trafo | tap_neutral | int32
49 | trafo | tap_min | int32
50 | trafo | tap_max | int32
51 | trafo | tap_step_percent | float64
52 | trafo | tap_step_degree | float64
53 | trafo | tap_pos | int32
54 | trafo | tap_phase_shifter | bool
55 | trafo | parallel | uint32
56 | trafo | df | float64
57 | trafo | in_service | bool
58 | line_geodata | coords | object
59 | bus_geodata | x | float64
60 | bus_geodata | y | float64
61 | bus_geodata | coords | object
62 | res_bus | vm_pu | float64
63 | res_bus | va_degree | float64
64 | res_bus | p_mw | float64
65 | res_bus | q_mvar | float64
66 | res_line | p_from_mw | float64
67 | res_line | q_from_mvar | float64
68 | res_line | p_to_mw | float64
69 | res_line | q_to_mvar | float64
70 | res_line | pl_mw | float64
71 | res_line | ql_mvar | float64
72 | res_line | i_from_ka | float64
73 | res_line | i_to_ka | float64
74 | res_line | i_ka | float64
75 | res_line | vm_from_pu | float64
76 | res_line | va_from_degree | float64
77 | res_line | vm_to_pu | float64
78 | res_line | va_to_degree | float64
79 | res_line | loading_percent | float64
80 | res_trafo | p_hv_mw | float64
81 | res_trafo | q_hv_mvar | float64
82 | res_trafo | p_lv_mw | float64
83 | res_trafo | q_lv_mvar | float64
84 | res_trafo | pl_mw | float64
85 | res_trafo | ql_mvar | float64
86 | res_trafo | i_hv_ka | float64
87 | res_trafo | i_lv_ka | float64
88 | res_trafo | vm_hv_pu | float64
89 | res_trafo | va_hv_degree | float64
90 | res_trafo | vm_lv_pu | float64
91 | res_trafo | va_lv_degree | float64
92 | res_trafo | loading_percent | float64
93 | res_ext_grid | p_mw | float64
94 | res_ext_grid | q_mvar | float64
95 | res_load | p_mw | float64
96 | res_load | q_mvar | float64

## parameters
| version | format_version | converged | OPF_converged | name | f_hz | sn_mva
0 | 2.14.6 | 2.14.0 | TRUE | FALSE |  | 50 | 1